## FO1_2
Commercial/Institutional/Residential Combustors ( ≤ 100 MMBtu/hr)
#1 and #2 Fuel Oil
This calculation is for illustrative purposes only. The emission factors and other data/methodologies used in these calculations are from US EPA's AP-42 Compilation of Air Pollutant Emission Factors. The emission factors, data, methodologies, and assumptions used in these calculations may not be representative/appropriate for a given emission unit/activity. For additional information, please refer to US EPA's AP-42 Compilation of Air Pollutant Emission Factors.
IDEM OAQ does not guarantee the accuracy of these calculations or the emission factors used.
All emission factors and calculations submitted as part of a permit application shall be reviewed by IDEM OAQ Permit Branch for accuracy, completeness, robustness, and appropriateness as part of the permit application review process and a final determination shall be made by the OAQ, Permits Branch.
| Heat Input Capacity | Potential Throughput
| MMBtu/hr | kgals/year |  | S = Weight % Sulfur
| 9.99 | 625.0886 |  | 0.5
Pollutant
|  | PM | PM10 | Direct PM2.5 | SO2 | NOx | VOC | CO
Emission Factor in lb/kgal |  | 2 | 2.38 | 2.13 | 71 | 20 | 0.34 | 5
(142.0S)
Potential Emission in tons/yr |  | 0.62509 | 0.74386 | 0.66572 | 22.1906 | 6.2509 | 0.10627 | 1.5627
Methodology
1 gallon of No. 2 Fuel Oil has a heating value of 140,000 Btu.
Potential Throughput (kgals/year) = Heat Input Capacity (MMBtu/hr) x 8,760 hrs/yr x 1kgal per 1000 gallon x 1 gal per 0.140 MMBtu
Emission Factors are from AP 42, Tables 1.3-1, 1.3-2, 1.3-3, and 1.3-7 (SCC 1-01-005-01, 1-02-005-01/02/03 and 1-03-005-01/02/03) (dated 5/10)
PM emission factor is filterable PM only.
PM10 emission factor is filterable PM10 of 1.08 lb/kgal + condensable PM emission factor of 1.3 lb/kgal.
Direct PM2.5 emission factor is filterable PM2.5 of 0.83 lb/kgal + condensable PM emission factor of 1.3 lb/kgal.
Potential Emission (tons/yr) = Potential Throughput (kgals/year) x Emission Factor (lb/kgal)/2,000 lb/ton
Hazardous Air Pollutants (HAPs)
HAPs
|  | Arsenic | Beryllium | Cadmium | Chromium | Lead | Mercury
Emission Factor in lb/MMBtu |  | 4e-06 | 3e-06 | 3e-06 | 3e-06 | 9e-06 | 3e-06
Potential Emission in tons/yr |  | 0.00017502 | 0.00013127 | 0.00013127 | 0.00013127 | 0.00039381 | 0.00013127
HAPs (continued)
|  | Manganese | Nickel | Selenium | Formaldehyde | POM
Emission Factor in lb/MMBtu |  | 6e-06 | 3e-06 | 1.5e-05 | 0.00043571 | 2.3571e-05
Potential Emission in tons/yr |  | 0.00026254 | 0.00013127 | 0.00065634 | 0.019065 | 0.0010314
[5 empty] | Potential Emission of Combined HAPs (tons/yr) | 0.022241
[5 empty] | Potential Emission of Highest Single HAP (tons/yr) | 0.019065 | Formaldehyde
Methodology
Emission Factors are from AP 42, Tables 1.3-8 and 1.3-10 (SCC 1-01-005-01, 1-02-005-01, and 1-03-005-01) (dated 5/10)
POM = Polycyclic Organic Matter
Potential Emission (tons/year) = Potential Throughput (MMBtu/hr) x Emission Factor (lb/MMBtu) x 8,760 hrs/yr / 2,000 lb/ton
Greenhouse Gases (GHGs)
Greenhouse Gas
|  | CO2 | CH4 | N2O
Emission Factor in lb/kgal |  | 21500 | 0.216 | 0.26
Potential Emission in tons/yr |  | 6719.7021 | 0.06751 | 0.081262
Summed Potential Emissions in tons/yr |  |  | 6719.8509
CO2e Total in tons/yr |  |  | 6745.6058
Methodology
The CO2 Emission Factor for #1 Fuel Oil is 21500. The CO2 Emission Factor for #2 Fuel Oil is 22300.
Emission Factors are from AP 42, Tables 1.3-3, 1.3-8, and 1.3-12 (SCC (1-01-005-01, 1-02-005-01/02/03, 1-03-005-01) (dated 5/10)
Global Warming Potentials (GWP) from Table A-1 of 40 CFR Part 98 Subpart A.
Potential Emission (tons/yr) = Potential Throughput (kgals/year) x Emission Factor (lb/kgal)/2,000 lb/ton
CO2e (tons/yr) = CO2 Potential Emission ton/yr x CO2 GWP (1) + CH4 Potential Emission ton/yr x CH4 GWP (25) + N2O Potential Emission ton/yr x N2O GWP (298).