## Diesel - hp
Reciprocating Internal Combustion Engines - Diesel Fuel
Output Rating (<=600 HP)
Maximum Input Rate (<=4.2 MMBtu/hr)
This calculation is for illustrative purposes only. The emission factors and other data/methodologies used in these calculations are from US EPA's AP-42 Compilation of Air Pollutant Emission Factors. The emission factors, data, methodologies, and assumptions used in these calculations may not be representative/appropriate for a given emission unit/activity. For additional information, please refer to US EPA's AP-42 Compilation of Air Pollutant Emission Factors.
IDEM OAQ does not guarantee the accuracy of these calculations or the emission factors used.
All emission factors and calculations submitted as part of a permit application shall be reviewed by IDEM OAQ Permit Branch for accuracy, completeness, robustness, and appropriateness as part of the permit application review process and a final determination shall be made by the OAQ, Permits Branch.
Use a conversion factor of 7,000 Btu/hp-hr to convert from horsepower to Btu/hr, unless the manufacturer provides a specific brake specific fuel consumption (BSFC)
Emissions calculated based on output rating (hp)
| Output Horsepower Rating (hp) | 600
| Maximum Hours Operated per Year | 8760
| Potential Throughput (hp-hr/yr) | 5256000
Pollutant
| PM* | PM10* | direct PM2.5* | SO2 | NOx | VOC | CO
Emission Factor in lb/hp-hr | 0.0022 | 0.0022 | 0.0022 | 0.00205 | 0.031 | 0.0025141 | 0.00668
Potential Emission in tons/yr | 5.7816 | 5.7816 | 5.7816 | 5.3874 | 81.468 | 6.6071 | 17.555
*PM and PM2.5 emission factors are assumed to be equivalent to PM10 emission factors. No information was given regarding which method was used to determine the factor or the fraction of PM10 which is condensable.
Hazardous Air Pollutants (HAPs)
Pollutant
Total PAH
| Benzene | Toluene | Xylene | 1,3-Butadiene | Formaldehyde | Acetaldehyde | Acrolein | HAPs***
Emission Factor in lb/hp-hr**** | 6.531e-06 | 2.863e-06 | 1.995e-06 | 2.737e-07 | 8.26e-06 | 5.369e-06 | 6.475e-07 | 1.176e-06
Potential Emission in tons/yr | 0.017163 | 0.007524 | 0.0052429 | 0.00071928 | 0.021707 | 0.01411 | 0.0017016 | 0.0030905
***PAH = Polyaromatic Hydrocarbon (PAHs are considered HAPs, since they are considered Polycyclic Organic Matter)
****Emission factors in lb/hp-hr were calculated using emission factors in lb/MMBtu and a brake specific fuel consumption of 7,000 Btu / hp-hr (AP-42 Table 3.3-1).
[7 empty] | Potential Emission of Total HAPs (tons/yr) | 0.071259
Methodology
Emission Factors are from AP 42 (Supplement B 10/96) Tables 3.3-1 and 3.3-2.
Potential Throughput (hp-hr/yr) = [Output Horsepower Rating (hp)] * [Maximum Hours Operated per Year]
Potential Emission (tons/yr) = [Potential Throughput (hp-hr/yr)] * [Emission Factor (lb/hp-hr)] / [2,000 lb/ton]
Green House Gas Emissions (GHG)
Pollutant
| CO2 | CH4 | N2O
Emission Factor in lb/hp-hr | 1.15 | 4.6297e-05 | 9.2594e-06
Potential Emission in tons/yr | 3022.2 | 0.12167 | 0.024334
[7 empty] | Summed Potential Emissions in tons/yr | 3022.346
[7 empty] | CO2e Total in tons/yr | 3032.4932
Methodology
CO2 Emission Factor is from AP42 (Supplement B 10/96), Tables 3.3-1.
CH4 and N2O Emission Factors are from 40 CFR 98 Subpart C Table C-2.
Global Warming Potentials (GWP) from Table A-1 of 40 CFR Part 98 Subpart A.
Potential Emission (tons/yr) = [Potential Throughput (hp-hr/yr)] * [Emission Factor (lb/hp-hr)] / [2,000 lb/ton]
CO2e (tons/yr) = CO2 Potential Emission ton/yr x CO2 GWP (1) + CH4 Potential Emission ton/yr x CH4 GWP (25) + N2O Potential Emission ton/yr x N2O GWP (298).

## Diesel - MMBtu
Reciprocating Internal Combustion Engines - Diesel Fuel
Output Rating (<=600 HP)
Maximum Input Rate (<=4.2 MMBtu/hr)
This calculation is for illustrative purposes only. The emission factors and other data/methodologies used in these calculations are from US EPA's AP-42 Compilation of Air Pollutant Emission Factors. The emission factors, data, methodologies, and assumptions used in these calculations may not be representative/appropriate for a given emission unit/activity. For additional information, please refer to US EPA's AP-42 Compilation of Air Pollutant Emission Factors.
IDEM OAQ does not guarantee the accuracy of these calculations or the emission factors used.
All emission factors and calculations submitted as part of a permit application shall be reviewed by IDEM OAQ Permit Branch for accuracy, completeness, robustness, and appropriateness as part of the permit application review process and a final determination shall be made by the OAQ, Permits Branch.
Use a conversion factor of 7,000 Btu/hp-hr to convert from horsepower to Btu/hr, unless the manufacturer provides a specific brake specific fuel consumption (BSFC)
Emissions calculated based on heat input capacity (MMBtu/hr)
| Heat Input Capacity (MMBtu/hr) | 4.2
| Maximum Hours Operated per Year | 8760
| Potential Throughput (MMBtu/yr) | 36792
Pollutant
| PM* | PM10* | direct PM2.5* | SO2 | NOx | VOC | CO
Emission Factor in lb/MMBtu | 0.31 | 0.31 | 0.31 | 0.29 | 4.41 | 0.36 | 0.95
Potential Emission in tons/yr | 5.7028 | 5.7028 | 5.7028 | 5.3348 | 81.1264 | 6.6226 | 17.4762
*PM and PM2.5 emission factors are assumed to be equivalent to PM10 emission factors. No information was given regarding which method was used to determine the factor or the fraction of PM10 which is condensable.
Hazardous Air Pollutants (HAPs)
Pollutant
Total PAH
| Benzene | Toluene | Xylene | 1,3-Butadiene | Formaldehyde | Acetaldehyde | Acrolein | HAPs***
Emission Factor in lb/MMBtu | 0.000933 | 0.000409 | 0.000285 | 3.91e-05 | 0.00118 | 0.000767 | 9.25e-05 | 0.000168
Potential Emission in tons/yr | 0.017163 | 0.007524 | 0.0052429 | 0.00071928 | 0.021707 | 0.01411 | 0.0017016 | 0.0030905
***PAH = Polyaromatic Hydrocarbon (PAHs are considered HAPs, since they are considered Polycyclic Organic Matter)
[7 empty] | Potential Emission of Total HAPs (tons/yr) | 0.071259
Methodology
Emission Factors are from AP 42 (Supplement B 10/96) Tables 3.3-1 and 3.3-2.
Potential Throughput (MMBtu/yr) = [Heat Input Capacity (MMBtu/hr)] * [Maximum Hours Operated per Year]
Potential Emission (tons/yr) = [Potential Throughput (MMBtu/yr)] * [Emission Factor (lb/MMBtu)] / [2,000 lb/ton]
Greenhouse Gas Emissions (GHG)
Pollutant
| CO2 | CH4 | N2O
Emission Factor in lb/MMBtu | 164 | 0.0066139 | 0.0013228
Potential Emission in tons/yr | 3016.944 | 0.12167 | 0.024334
[7 empty] | Summed Potential Emissions in tons/yr | 3017.09
[7 empty] | CO2e Total in tons/yr | 3027.2372
Methodology
CO2 Emission Factor is from AP42 (Supplement B 10/96), Tables 3.3-1.
CH4 and N2O Emission Factors are from 40 CFR 98 Subpart C Table C-2.
Global Warming Potentials (GWP) from Table A-1 of 40 CFR Part 98 Subpart A.
Potential Emission (tons/yr) = [Potential Throughput (MMBtu/yr)] * [Emission Factor (lb/MMBtu)] / [2,000 lb/ton]
CO2e (tons/yr) = CO2 Potential Emission ton/yr x CO2 GWP (1) + CH4 Potential Emission ton/yr x CH4 GWP (25) + N2O Potential Emission ton/yr x N2O GWP (298).