## A
Natural Gas Combustion ( > 100 MMBtu/hr)
Large Industrial and Utility Boilers
This calculation is for illustrative purposes only. The emission factors and other data/methodologies used in these calculations are from US EPA's AP-42 Compilation of Air Pollutant Emission Factors. The emission factors, data, methodologies, and assumptions used in these calculations may not be representative/appropriate for a given emission unit/activity. For additional information, please refer to US EPA's AP-42 Compilation of Air Pollutant Emission Factors.
IDEM OAQ does not guarantee the accuracy of these calculations or the emission factors used.
All emission factors and calculations submitted as part of a permit application shall be reviewed by IDEM OAQ Permit Branch for accuracy, completeness, robustness, and appropriateness as part of the permit application review process and a final determination shall be made by the OAQ, Permits Branch.
HHV
| Heat Input Capacity | mmBtu |  | Potential Throughput
| MMBtu/hr | mmscf |  | MMCF/yr
| 100.1 | 1020 |  | 859.6824
Pollutant
|  | PM* | PM10* | direct PM2.5* | SO2 | NOx | VOC | CO
Emission Factor in lb/MMCF |  | 1.9 | 7.6 | 7.6 | 0.6 | 0 | 5.5 | 84
**see below
Potential Emission in tons/yr |  | 0.8167 | 3.2668 | 3.2668 | 0.2579 | 0 | 2.3641 | 36.1067
*PM emission factor is filterable PM only. PM10 emission factor is condensable and filterable PM10 combined.
PM2.5 emission factor is condensable and filterable PM2.5 combined.
**Emission Factors for NOx: Uncontrolled = 280 (pre-NSPS) or 190 (post-NSPS), Low NOx Burner = 140, Flue gas recirculation = 100 (See Table 1.4-1)
Methodology
All emission factors are based on normal firing.
MMBtu = 1,000,000 Btu; MMCF = 1,000,000 Cubic Feet of Gas
Emission Factors from AP 42, Chapter 1.4, Tables 1.4-1, 1.4-2, and 1.4-3, SCC #1-01-006-01, 1-01-006-04 (AP-42 Supplement D 3/98)
Potential Throughput (MMCF/yr) = Heat Input Capacity (MMBtu/hr) x 8,760 hrs/yr x 1 MMCF/1,020 MMBtu
Potential Emission (tons/yr) = Potential Throughput (MMCF/yr) x Emission Factor (lb/MMCF)/2,000 lb/ton
Hazardous Air Pollutants (HAPs)
HAPs - Organics
|  | Benzene | Dichlorobenzene | Formaldehyde | Hexane | Toluene
Emission Factor in lb/MMcf |  | 0.0021 | 0.0012 | 0.075 | 1.8 | 0.0034
Potential Emission in tons/yr |  | 0.00090267 | 0.00051581 | 0.032238 | 0.77371 | 0.0014615
HAPs - Metals
|  | Lead | Cadmium | Chromium | Manganese | Nickel
Emission Factor in lb/MMcf |  | 0.0005 | 0.0011 | 0.0014 | 0.00038 | 0.0021
Potential Emission in tons/yr |  | 0.00021492 | 0.00047283 | 0.00060178 | 0.00016334 | 0.00090267
[5 empty] | Potential Emission of Combined HAPs (tons/yr) | 0.81119
Methodology |  |  |  |  | Potential Emission of Highest Single HAP (tons/yr) | 0.77371 | Hexane
Methodology is the same above.
The five highest organic and metal HAPs emission factors are provided above.
Additional HAPs emission factors are available in AP-42, Chapter 1.4.
Greenhouse Gases (GHGs)
Greenhouse Gas
|  | CO2 | CH4 | N2O
Emission Factor in lb/MMcf |  | 120000 | 2.3 | 2.2
Potential Emission in tons/yr |  | 51580.9412 | 0.98863 | 0.94565
Summed Potential Emissions in tons/yr |  |  | 51582.8755
CO2e Total in tons/yr |  |  | 51887.4609
Methodology
The N2O Emission Factor for uncontrolled is 2.2. The N2O Emission Factor for low Nox burner is 0.64.
Emission Factors are from AP 42, Table 1.4-2 SCC #1-02-006-02, 1-01-006-02, 1-03-006-02, and 1-03-006-03.
Global Warming Potentials (GWP) from Table A-1 of 40 CFR Part 98 Subpart A.
Potential Emission (tons/yr) = Potential Throughput (MMCF/yr) x Emission Factor (lb/MMCF)/2,000 lb/ton
CO2e (tons/yr) = CO2 Potential Emission ton/yr x CO2 GWP (1) + CH4 Potential Emission ton/yr x CH4 GWP (25) + N2O Potential Emission ton/yr x N2O GWP (298).