## A
LPG-Propane - Industrial Boilers
(Heat input capacity: > 10 MMBtu/hr and < 100 MMBtu/hr)
This calculation is for illustrative purposes only. The emission factors and other data/methodologies used in these calculations are from US EPA's AP-42 Compilation of Air Pollutant Emission Factors. The emission factors, data, methodologies, and assumptions used in these calculations may not be representative/appropriate for a given emission unit/activity. For additional information, please refer to US EPA's AP-42 Compilation of Air Pollutant Emission Factors.
IDEM OAQ does not guarantee the accuracy of these calculations or the emission factors used.
All emission factors and calculations submitted as part of a permit application shall be reviewed by IDEM OAQ Permit Branch for accuracy, completeness, robustness, and appropriateness as part of the permit application review process and a final determination shall be made by the OAQ, Permits Branch.
| Heat Input Capacity | Potential Throughput
| MMBtu/hr | kgals/year |  | SO2 Emission factor = 0.10 x S
| 9.99 | 956.4197 |  | S = Sulfur Content = |  | 0 | grains/100ft^3
Pollutant
|  | PM* | PM10* | direct PM2.5** | SO2 | NOx | VOC | CO
Emission Factor in lb/kgal |  | 0.2 | 0.7 | 0.7 | 0 | 13 | 1 | 7.5
[5 empty] | (0.10S) |  | **TOC value
Potential Emission in tons/yr |  | 0.095642 | 0.33475 | 0.33475 | 0 | 6.2167 | 0.47821 | 3.5866
*PM emission factor is filterable PM only. PM emissions are stated to be all less than 10 microns in aerodynamic equivalent diameter, footnote in Table 1.5-1, therefore PM10 is based on the filterable and condensable PM emission factors.
** No direct PM2.5 emission factor was given. Direct PM2.5 is a subset of PM10. If one assumes all PM10 to be all direct PM2.5,
then a worst case assumption of direct PM2.5 can be made.
**The VOC value given is TOC. The methane emission factor is 0.2 lb/kgal.
Methodology
1 gallon of LPG has a heating value of 94,000 Btu
1 gallon of propane has a heating value of 91,500 Btu (use this to convert emission factors to an energy basis for propane)
(Source - AP-42 (Supplement B 10/96) page 1.5-1)
Potential Throughput (kgals/year) = Heat Input Capacity (MMBtu/hr) x 8,760 hrs/yr x 1kgal per 1000 gallon x 1 gal per 0.0915 MMBtu
Emission Factors are from AP42 (7/08), Table 1.5-1 (SCC #1-02-010-02)
Propane Emission Factors shown. Please see AP-42 for butane.
Emission (tons/yr) = Throughput (kgals/yr) x Emission Factor (lb/kgal) / 2,000 lb/ton
Greenhouse Gases (GHGs)
Greenhouse Gas
|  | CO2 | CH4 | N2O
Emission Factor in lb/kgal |  | 12500 | 0.2 | 0.9
Potential Emission in tons/yr |  | 5977.623 | 0.095642 | 0.43039
Summed Potential Emissions in tons/yr |  |  | 5978.149
CO2e Total in tons/yr |  |  | 6108.2699
Methodology
The CO2 Emission Factor for Propane is 12500. The CO2 Emission Factor for Butane is 14300.
Emission Factors are from AP 42 (7/08), Table 1.5-1 (SCC #1-02-010-02)
Global Warming Potentials (GWP) from Table A-1 of 40 CFR Part 98 Subpart A.
Emission (tons/yr) = Throughput (kgals/ yr) x Emission Factor (lb/kgal)/2,000 lb/ton
CO2e (tons/yr) = CO2 Potential Emission ton/yr x CO2 GWP (1) + CH4 Potential Emission ton/yr x CH4 GWP (25) + N2O Potential Emission ton/yr x N2O GWP (298).