## Sheet1
Current Code | Model Code | Summary of Change | Rationale for Change | Fiscal Analysis
| 200.4(B) | Requires grouping of grounded conductor with ungrounded conductor | Installer safety and reduced fire risk due to overloading | $0 per unit
200.9 | 200.9 | Adds the color silver to permissible identification of grounded conductor terminal | Installer safety and reduced fire risk due to miswiring | $0 per unit
210.8(A) | 210.8(A) | GFCI protection for 125 Volt 15A/20A receptacles required in all basement areas (finished and unfinished) | Even finished basements are subject to moisture intrusion. Finished floor surfaces have varying degrees of conductivity (tile, carpet, laminate, stained concrete) | $15 per unit
| 210.8 | GFCI protective device must be installed in a readily accessible location | Removes need to move appliances to reset tripped GFCI | $0 per unit
210.8(B) | 210.8(B) | GFCI protection required in buffet areas, locker rooms, garages | These areas contain moisture and normally non-current carrying metallic surfaces | $15 per circuit
| 210.8(D) | GFCI protection required for specific appliances operating 150 volts to ground and 60 amps or less | The CPSC found that an average of 9 people died from appliance electrocution each year between 2018 and 2020 | $195 per unit
| 210.8(F) | GFCI protection required for outdoor outlets operating 150 volts to ground and 50 amps or less | Outdoor appliances such as AC condensers can present electrocution hazards. | $100 per unit
210.52(G) | 210.11(C)(4) | Minimum of one 120V 20A branch circuit required for a garage in a dwelling unit | Removes the need to run extension cord and prevents overloading of adjacent circuits. This circuit removes the burden of installing an individual circuit in each bay of a multi-bay garage. | $25 per unit savings
| 210.12(A) | Expanded list of AFCI protection options for installers to choose from | As new products enter the market, installers can choose based on performance and value | $0 per unit
210.12(B) | 210.12(B) | AFCI protection for dwellings expanded to include kitchens and laundry areas | Cord connected appliances are a major source of arc fault cased fires. Both kitchens and laundry areas frequently contain cord connected appliances. By using AFCI/GFCI combination receptacles, this requirement adds no cost to an installation. | $0 per unit
| 210.18 | Branch circuits ratings expanded to include 10A (See 210.23(A)) | Permits the use of 10 amp lighting circuits in dwellings due to the wide use of LED luminaires. This lower ampacity rating reduces the calculated size for conductors and lowers installations costs. | $120 per unit savings
210.52(C) | 210.52(C) | Peninsula and island receptacles no longer permitted to be installed below the countertop surface | The CPSC reported 9,700 burns and 10 deaths (mainly children) who pulled the cord of an appliance. The ability to omit the receptacle and provide provisions for future results in a fiscal savings. | $464 per unit savings
| 210.65 | Meeting rooms require floor receptacle to minimize extension cord use | Reduce tripping and fire hazard due to extension cord use | $100 per meeting room
| 215.15 | Isolating barriers are required to protect personnel from inadvertent contact with busbars or terminals | Provides installer/maintenance safety from energized supply side of equipment. These barriers are included in all newly manufactured equipment. | $0 per panelboard
| 215.18 | Surge protection device required for feeders supplying dwelling and dormitory units, guest rooms, and patient sleeping rooms | Primary goal is to protect life safety devices in occupancy such as AFCI, GFCI, smoke alarms, and fire alarm systems. Additional benefit is the protection for consumer electronics | $50 per unit
220.12 | 220.5(C) | Lighting load calculated floor space must include garage floor area | Garages are frequently used for extended occupations that require illumination. After applying demand factors, this number is negligible. | $0 per unit
Table 220.12 | Table 220.42(A) | Unit load VA/ft² for lighting drastically reduced for numerous occupancies | Widespread use of LED lighting. Estimated to be a 63% savings in banks and office building electrical system demands. Fiscal impact difficult to calculate, but undoubtedly major savings for non-dwelling occupancies statewide. | $10,000,000+ savings statewide
| 220.42(B) | Designers can follow adopted energy codes for lighting that reduce/eliminate the need to follow 220.42 | Provides savings for electrical designers who use modern design practices to reduce the calculated lighting load demand | Difficult to quantify
| 220.57 | EVSE load calculation information added | Provides installers a data point to prevent oversizing systems for EVSE compatibility. Provides a design target when building EV-ready homes. | $0 per unit
| 225.41 | Emergency disconnect is required for dwellings fed from an outside branch circuit or feeder | Provides first responders with a safe means to remove electrical hazards from a dwelling | $0 per unit
| 230.62(C) | Isolating barriers are required to protect personnel from inadvertent contact with busbars or terminals | Provides installer/maintenance safety from energized supply side of equipment. These barriers are included in all newly manufactured equipment. | $0 per panelboard
| 230.67 | Surge protection device required for services supplying dwelling and dormitory units, guest rooms, and patient sleeping rooms | Primary goal is to protect life safety devices in occupancy such as AFCI, GFCI, smoke alarms, and fire alarm systems. Additional benefit is the protection for consumer electronics | $50 per unit
| 230.85 | Emergency disconnect is required for one and two-family dwellings | Provides first responders with a safe means to remove electrical hazards from a dwelling | $265 per dwelling unit