## Changes
Article (2023) | Article (2009 IEC) | 2023 NEC | Cost impact
Article 235 Branch Circuits, Feeders, and Services Over 1000 Volts ac, 1500 Volts dc, Nominal
235 |  | New article in 2023, requirements from other articles consolidated in 235, no technical changes | None
Article 240 Overcurrent Protection
240.2 | 240.2 | Prohibits reconditioning of certain electrical equipment, permits reconditioning of LV power circuit breakers and electromechanical protective relays and current tranformers | None
240.4 D (3) & (5) | 240.4 D (3) & (5) | Adds requirements for Copper-Clad Aluminum | None
240.4 (H) | 240.4 (H) | Specifies dwelling unit feeder & service conductor protection values | None
Table 240.6 (A) | Table 240.6 (A) | Adds 10A as a standard rating for fuses & circuit breakers | None
240.7 | 240.7 | Requires listing of Branch-circuit overcurrent protective devices, relays & circuit breakers providing ground fault protection of equipment, & Ground Fault circuit interrupter devices. | None
240.11 | 240.11 | Requires selective coordination of all feeder and service overcurrent devices where one of the feeder devices are required to be coordinated by other parts of the code.
240.15 (B) (1) | 240.15 (B) (1) | Requires Handle Ties For circuit breakers protecting Multiwire branch ciruits | $10.00 / Multiwire Circuit
240.15 (B) (4) | 240.15 (B) (4) | Specifies requirements for 3-wire DC circuit protection | None
240.16 | 240.16 | Requires branch-circuit overcurrent protective devices to be rated 5000 AIC minimum | None
240.23 | 240.23 | Deleted section, requirement duplicated in 220.61 | None
240.24 [E] | 240.24 [E] | Adds showering facilities, or locker rooms with showering facilities as prohibited places to install Overcurrent protective devices | None
240.4 | 240.4 | Adds and 425.22(C) for fixed resistance and electrode industrial process heating equipment, or where specifically permitted elsewhere in this Code | None
240.60 [E] | 240.60 [E] | Adds requirement for fuse reducers to be listed | None
240.67 | 240.67 | Requires Arc Energy Reduction where fuses are rated 1200 Amps or higher | $7,500 / per set of fuses
240.67 (A) | 240.67 (A) | Requires documentation for Arc Energy Reduction
240.67 (B) | 240.67 (B) | Specifies methods to reduce clearing time of fuses to .07 seconds or less
240.67 [C] | 240.67 [C] | Requires performance testing of the arc energy reduction system
240.87 | 240.87 | Requires Arc Energy Reduction where circuit breakers are rated 1200 Amps or higher | $7,500 / per breaker
240.87 (A) | 240.87 (A) | Requires documentation for Arc Energy Reduction
240.87 (B) | 240.87 (B) | Specifies methods to operate circuit breakers at less than the available arcing current
240.87 [C] | 240.87 [C] | Requires performance testing of the arc energy reduction system
240.89 | 240.89 | Requires replacement trip units to be listed for use with the circuit breaker type in which it is installed | None
240.91 | 240.91 | Added new requirement for supervised industrial applications permitting "rounding up" applications in circuits protected by overcurrent protective devices rated more than 800 amperes | None
Article 242 Overvoltage Protection (Created to consolidate the requirements of articles 280 & 285)
242.1 | 280.1 & 285.1 | Scope of article | None
242.2 |  | New requirement - SPDs and surge arresters shall not be reconditioned. | None
242.3 |  | Equipment shall be protected against overvoltage in accordance with the article in this Code that covers the type of equipment or location specified in Table 242.3 | None
242.6 | 285.5 | Requires listed device | None
242.8 | 285.6 | Requires Short-circuit current rating | None
242.9 |  | New Requirement - An SPD shall provide indication that it is functioning properly. | None
242.12 | 285.3 | Uses Not Permitted | None
242.13 | 285.23 | Type 1 SPD requirements | None
242.14 | 285.24 | Type 2 SPD requirements | None
242.16 | 285.25 | Type 3 SPD requirements | None
242.18 |  | Type 4 SPD requirements | None
242.20 | 285.4 | Number of devices required | None
242.22 | 285.11 | location requirements | None
242.24 | 285.12 | Routing of conductors | None
242.28 | 285.26 | Conductor size Requirements | None
242.30 | 285.27 | Requirements for Connection Between Conductors | None
242.32 | 285.28 | Requirements for Grounding Electrode Conductor Connections and Enclosures | None
242.4 | 280.2 | Uses Not Permitted | None
242.42 | 280.4 | Specifies requirements for rating of surge arrester over 1000 Volts | None
242.44 | 280.3 | Specifies number of surge arresters required | None
242.46 | 280.11 | Specifies location requirements | None
242.48 | 280.12 | Specifies requirements for routing of equipment grounding conductors | None
242.50 | 280.21 | Specifies connection requirements | None
242.52 | 280.23 | The conductor between the surge arrester and the line, and the surge arrester and the grounding connection, shall not be smaller than 6 AWG copper or aluminum | None
242.54 | 280.24 | Requirements for a surge arrester protecting a transformer that supplies a secondary distribution system | None
242.56 | 280.25 | Requirements for Grounding Electrode Conductor Connections and Enclosures | None
Article 245 Overcurrent Protection for Systems Rated Over 1000 Volts ac, 1500 Volts dc (New Article to consolidate requirements from other articles)
245.1 | 245.1 | Scope
245.2 | 245.2 | Specifies requirements for reconditioned equipment over 1000 volts ac, 1500 volts dc, nominal.
245.21 | 245.21 | Specifies requirements for Circuit-Interrupting Devices over 1000 volts ac, 1500 volts dc, nominal.
245.26 | 240.100 | Feeder & Branch circuit protection requirements relocated to new article for systems rated over 1000 volts AC, 1500 volts DC | None
245.27 | 240.101 | Feeder protection requirements relocated to new article for systems rated over 1000 volts AC, 1500 volts DC | None
Article 250 Grounding and Bonding
Art. 100 | 250.2 | Definitions moved to Article 100
250.21 [C] |  | New requirement to mark ungrounded systems | None
250.28 (D) (1) | 250.28 (D) (1) | Refers to new table 250.102[C](1) for Main & System Bonding Jumpers. (No Change to requirements) | None
| 250.52 (B)(3) | Prohibits using structures and structural rebar of swimming pools as a grounding electrode | None
| 250.64 (G) | Prohibits installing grounding electrode conductors through ventilation openings of enclusures | None
| 250.118 (B) | Prohibits the use of grounding electrode conductors, and the structural metal fame of a building as an equipment grounding conductor. | None
| 250.122 (F)(2)[C] | Permits a suplementary EGC sized by 250.122 in combination with smaller EGC of multiconductor cables. | Could be a cost savings vs. custom cable configurations
| 250.167 | Requires Ground-Fault detection for Ungrounded DC systems and permits Ground-Fault detection for grounded DC systems | None