## 2006_bypasses
PERMIT | FACILITY NAME | COUNTY | BYPASS DATE | DURATION | GALLONS | LOCATION | REASON | ACTIONS
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-04-14 | 10:30P - 1:30A (4/15) | 1000 | MANHOLE IN GAYE DRIVE | RAIN 3" | LONG TERM CONTROL PLAN APPROVED
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-04-14 | 10:30P - 1:30A (4/15) | 2000 | MANHOLE AT LEHMAN ST & VAN BUREN | RAIN 3" | SOUTH TRUNK LINE PROJECT SCHEDULED TO BEGIN THIS SUMMER
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-04-14 | 10:30P - 1:30A (4/15) | 4000 | MANHOLE 1425 HENDRICKS ST | RAIN 3" | LINES TO BE JETTED MAY / JUNE - PROJECT TO RELIEVE PROBLEM
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-04-14 | 10:30P - 1:30A (4/15) | 8000 | MANHOLE AT FRANKLIN ST & HENDRICKS ST | RAIN 3" | SOUTH TRUNK LINE PROJECT TO BEGIN THIS SUMMER
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-04-14 | 10:30P - 1:30A (4/15) | 2000 | MANHOLE AT WELTY ST | RAIN 3" | LINES TO BE JETTED MAY / JUNE
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-04-14 |  |  | BERNR ST & ELLENBERGER TILE | RAIN 3" | AREA INSPECTED BY BERNE, NO VISABLE EVIDENCE OF OVERFLOW
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-04-14 | 10:30P - 1:30A (4/15) | 8000 | MANHOLE AT LINN GROVE & VAN BUREN | RAIN 3" | SOUTH TRUNK LINE PROJECT TO BEGIN THIS SUMMER
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-05-18 | 4:00P - 4:30P | 300 | MANHOLE SOUTH HENDRICKS ST | S HENDRICKS ST LIFT STATION LOSS 3 PHASE POWER
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-08-26 | 12:00P - 3:00P | 50000 | CSO # 6 | 8" WATER MAIN LEAK GOING DIRECTLY TO 8" TILE | FIXED WATER MAIN LEAK
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2006-12-31 | 6:00P - 7:30P | 1000 | MANHOLE LINN GROVE AVE & VAN BUREN ST | RAIN 1.5" | LONG TERM CONTROL PLAN
IN0039357 | GENEVA MUNICIPAL STP | ADAMS | 2006-11-16 | 11/16 - 11/22 |  | MANHOLE - FORD ST & 116 | POSSIBLE OVERFLOW BUT NOT OBSERVED - RAIN | RAISING MANHOLE, WORKING ON I&I REMOVAL
IN0048119 | ARCOLE COLLECTION SYSTEM | ALLEN | 2006-07-26 | 11:41P - 6:00A | 15000 | MAIN LIFT STATION & MANHOLE ON ARCOLE RD | RAIN 6", STREETS UNDER WATER | ENSURE LIFT STATION OPERATION - WORKING TO PREVENT FUTURE OVERFLOWS
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-01-01 | 10:30A - 10:20A (1/2) |  | SSO T34-028 | RAIN & MELTING SNOW OVERLOADED SYSTEM | WORKING ON SEWER SYSTEM IMPROVEMENTS IN THE AREA
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-01-13 | 1/13 - 1/14 |  | MANHOLES T34 024 - T34 028 | RAIN CAUSING SYSTEM TO OVERLOAD | CITY MAKING SEWER IMPROVEMENTS IN AREA
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-01-13 | 1/13 - 1/14 |  | MANHOLE # M18 231 - VESSEY PARK | RAIN 0.75" CAUSED THE SYSTEM TO OVERFLOW | CITY IS MAKING SEWER IMPROVEMENTS IN THE AREA
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-01-23 | 9:47A - 10:00A (1/24) |  | PERMIT # 5 | DEBRIS BLOCKAGE IN REGULATOR GATE | CITY IS MAKING SEWER SYSTEM IMPROVEMENTS IN THE AREA
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-04-28 | 1:30P - 1:00A (4/29) | 69000 | MANHOLE # 134-001 | STICKS OF WOOD & CONCRETE BLOCKING FLOW IN SEWER | RAISED MANHOLE & BOLTED LID TO PREVENT VANDALISM
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-05-26 | 2:15P - 3:00P | 100 | MANHOLE # S30-023 | MANHOLE / SEWER LINE PLUGGED WITH ROOTS & GREASE | BI-WEEKLY MAINTENANCE TO BE CONDUCTED ON SEWER LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-05-27 | 3:40P - 5:40P | 400 | MANHOLE # N23-1255 | MANHOLE / SEWER LINE PLUGGED | WEEKLY MAINTENANCE TO BE CONDUCTED ON SEWER LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-06-08 | 12:30P - 1:10P | 100 | MANHOLE K42 050 | BLOCKAGE, GREASE & GRAVEL | SEWER TO BE PUT ON 30 DAY CLEANING SCHEDULE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-06-16 | 10:30A - 11:30A | 50 | MANHOLE D39 015 | MALFUNCTIONING AIR RELEASE VALVE ON FORCE MAIN | WILL PUT INSPECTION OF AIR RELEASE VALVE ON PM PROGRAM
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-07-27 | 7/27 |  | MANHOLE # F30 031 - UP STREAM OF GOLFVIEW LIFT STATION | RAIN 1.4" | CHECKING OPERATION OF LIFT STATION WEEKLY
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-09-13 | ? - 6:15P | 200 | MANHOLES # L39 022 | ROOTS CAUSING SEWER BLOCKAGE | ADDING SEWER TO THREE MONTH CLEANING SCHEDULE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-09-14 | ? - 11:40A | 500 | MANHOLES # O19 O41 | SEWER PLUGGED WITH GREASE | ADDING SEWER TO CLEANING SCHEDULE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-09-19 | / - 8:00A |  | MANHOLE # K06 154 | RAIN / CONSTRUCTION RELATED TO ABANDONED LINE | BULKHEAD TO BE REBUILT - MANHOLE TO BE FILLED WITH CONCRETE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-10-09 | ? - 10:15A (10/10) |  | PERMIT # 21 | EQUIPMENT FAILURE, FLOAT PARTIALLY STUCK CLOSED | SITE IS VISUALLY CHECKED DAILY
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-10-16 | 9:00A - 3:00P |  | BASEMENT MAIN WWTP BUILDING | VALVE FAILURE DURING DEOMOLITION OF OLD RAW PUMPS | FLOW PUMPED TO POND 1
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-10-17 | ? - 12:24P |  | N23 121 & N23 122 | RAIN 2.06" - SYSTEM OVERLOADED | CHECKING TO ENSURE NO BLOCKAGE IN SEWER
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-10-17 | ? - 2:13P |  | T34 028 | RAIN 2.06" - SYSTEM OVERLOADED | CHECKING TO ENSURE NO BLOCKAGE IN SEWER
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-10-17 | ? - 6:30P |  | V10 001 | RAIN 2.06" - SYSTEM OVERLOADED | CHECKING TO ENSURE NO BLOCKAGE IN SEWER
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-12-01 | 9:00A - 1:30P |  | N23 121, N23 122, T34 024, T34 028, V06 001 | RAIN 2.3", SYSTEM OVERLOADED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2006-12-31 | 12/31 - 1/1 |  | N23 121, T34 028, V10 001 | RAIN 1.25", SYSTEM OVERLOADED
IN0044369 | GRABILL COLLECTION SYSTEM | ALLEN | 2006-12-01 | 7:00A - 10:45A | 1500 | MANHOLE 2-4 | RAIN 2.75"
| HOAGLAND | ALLEN | 2006-09-01 | 9/1 - 9/5 | 600 | AIR RELIEF VALVE MANHOLE ON HOAGLAND ROAD | AIR RELIEF VALVE ON FORCE MAIN HAD A HOLE IN THE PIPE | PIT PUMPED DOWN, REPAIRS MADE & AREA CLEANED
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-10-17 | 5:30A - 1:00P | 6000 | DUPONT LIFT STATION | RAIN 1.8", CITY OF FT WAYNE BACKUP
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-10-17 | 5:30A - 8:00A | 2000 | REDWOOD LIFT STATION | RAIN 1.8", CITY OF FT WAYNE BACKUP
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-07-27 | 1:00A - 8:30A | 25000 | DUPONT LIFT STATION | RAIN 6", CITY OF FT WAYNE BACKUP
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-07-27 | 1:00A - 6:15A | 8000 | REDWOOD LIFT STATION | RAIN 6", CITY OF FT WAYNE BACKUP
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-12-01 | 5:15A - 9:15A | 3000 | REDWOOD LIFT STATION WET WELL | RAIN 1.4"
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-12-01 | 5:00 - 10:55A | 8000 | DUPONT LIFT STATION | RAIN 1.5"
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-12-01 | 7:00A - |  | MANHOLE SYCAMORE LIFT STATION WET WELL | RAIN 1.4"
| UTILITY CENTER / CITY OF FT WAYNE | ALLEN | 2006-12-01 | 5:00 - 11:15A | 7000 | MANHOLE WASHINGTON, GRAHAM, KLUG DR | RAIN 1.5"
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2006-01-31 | ? - 4:00P | 100 | REAR LOT 40 LIBERTY HILLS | ROOTS AND RAGS IN SEWER LINE, JETTED LINE
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2006-07-27 | 1:00A - 10:00A | 25000 | SEVERAL COLLECTION SYSTEM MANHOLES | RAIN 6", CITY OF FT WAYNE BACKUP | MONITORING OPERATION OF LIFT STATIONS
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2006-07-27 | 10:00A - 2:22P | 85000 | SYCAMORE LIFT STATION | RAIN 8.2" | MONITORING LIFT STATIONS FOR FULL OPERATIONS
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2006-10-17 | 6:15A - 4:00A (10/18) | 19000 | SYCAMORE LIFT STATION | RAIN 1.8"
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2006-12-01 | 12/1 - 12/2 | 100000 | MANHOLE W OF SYCAMORE HILLS LIFT STATION | RAIN
IN0042391 | UTILITY CENTER, MIDWEST | ALLEN | 2006-07-27 | 2:00A - 8:00A | 7800 | MANHOLE F27-2 | RAIN 6"
| UTILITY CENTER/CITY OF FT WAYNE | ALLEN | 2006-07-12 | 2:00P - 8:22P | 15000 | MANHOLE WEST OF DUPONT LIFT STATION | RAIN 1.9" - CITY OF FT WAYNE MANHOLES WERE BACKED UP | ENSURE PROPER OPERATION OF LIFT STATION
IN0021407 | WOODBURN MUNICIPAL STP | ALLEN | 2006-07-27 | 12:00 - 5:00A | 15000 | MANHOLE 611 | RAIN 4.5", FLOODING | WORKING ON I & I REDUCTION
IN0021407 | WOODBURN MUNICIPAL STP | ALLEN | 2006-07-27 | 12:00 - 4:05A | 5000 | HAVENWOOD LIFT STATION | RAIN 4.5", LIFT STATION POWER FAILURE | CONTACT AEP TO RESTORE POWER
IN0032573 | COLUMBUS MUNICIPAL STP | BARTHOLOMEW | 2006-07-19 | 12:30A - 9:00A | 10000 | LIFT STATION 150W & DEAVER RD - WALESBORO FORCE MAIN | FORCE MAIN FAILURE
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2006-03-08 | 3/8 - 3/9 | 80000 | LIFT STATION | RAIN 2.5" | LOOKING FOR INFLOW SOURCES
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2006-03-12 | 3/12 | 100000 | LIFT STATION | RAIN 6.8" | LOOKING FOR MANHOLES UNDER WATER
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2006-05-10 | 5/10 - 5/11 | 50000 | LIFT STATION | RAIN 3" | SMOKE TEST
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2006-08-28 | AM - 11:00 | 5000 | MANHOLE & LIFT STATION | RAIN 2.2", EVIDENCE LIFT STATION HAD OVERFLOWED | INSPECTION OF MANHOLES FOR SUSPECTED I&I
IN0021075 | HARTSVILLE MUNICIPAL STP | BARTHOLOMEW | 2006-03-12 | 3/12 | 100000 | OVERFLOW AT THE AERATION TANK & CLARIFIER | RAIN 6.8" | GETTING GRANT FOR IMPROVEMENTS
IN0021075 | HARTSVILLE MUNICIPAL STP | BARTHOLOMEW | 2006-04-16 | 4/16 - 4/17 | 200000 | OUTFALL AT CREEK & OVERFLOW OF MLSS TANK | RAIN 4.1" | DIVERT RUNOFF TO STREAM & NOT INTO WWTP
IN0021075 | HARTSVILLE MUNICIPAL STP | BARTHOLOMEW | 2006-05-10 | 5/10 - 5/11 | 50000 | OVERFLOW AT MIXING TANKS | RAIN 3", RUNOFF FROM SURROUNDING AREA | CONSIDERING DIVERTING RUNOFF
IN0021075 | HARTSVILLE MUNICIPAL STP | BARTHOLOMEW | 2006-05-30 | ? - 16:00 | 20000 | OUTFALL | BLOWER MOTOR TRIPPED OUT - STORM OR HOT WEATHER | INSTALLING TWO BLOWER MOTORS
IN0021075 | HARTSVILLE MUNICIPAL STP | BARTHOLOMEW | 2006-08-28 | 8/28 | 10000 | BLOWERS DOWN UPON ARRIVAL AT PLANT, TRIPPED OUT (STORM) | RAIN 2", BLOWERS DOWN | LOOK INTO GETTING SURGE PROTECTOR
IN0021075 | HARTSVILLE MUNICIPAL STP | BARTHOLOMEW | 2006-09-12 | 11:00A | 1000 | MLSS TANK OVERFLOW | RAIN 2.5", RUNOFF ENTERING THROUGH RUSTED AREAS IN MLSS TANK | NEW PLANT CONSTRUCTION TO BEGIN LATE 2006
IN0021253 | HOPE HARDWOODS, INC. | BARTHOLOMEW | 2006-10-22 | 9:30A - 3:30P |  | LIFT STATION MANHOLE | BUILD UP OF GREASE ON FLOATS WOULD NOT LET PUMPS KICK ON | KEEP A CLOSE EYE ON WET WELL - ENSURE OPERATION OF FLOATS
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2006-03-12 | 3/12 |  | MANHOLES & LIFT STATION | RAIN | WORKING ON I & I REDUCTION
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2006-04-15 | 4/15 - |  | MANHOLE AT LIFT STATION | HOLE IN SUMP PIT ALLOWING SURFACE WATER INTO PIT | PLAN TO PLUG HOLE UNTIL REPAIR CAN BE MADE
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2006-08-10 | 2:30P - 8:30P |  | LIFT STATION - MILLERS MERRY MANOR | RAIN 1.6", POWER FAILURE
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2006-08-10 | 2:30P - 12:00P (8/11) |  | LIFT STATION | RAIN 1.6", POWER FAILURE
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2006-08-29 | 7:00A - 9:00A |  | LIFT STATION MORAVIAN CEMETARY | LIFT STATION PUMPS AIR LOCKED | TO CHECK LIFT STATION TWICE DAILY
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2006-12-22 | 6:00A - 8:00A |  | LIFT STATION - MORAVAN | RAIN 1" | MAKE SURE PUMPS ARE RUNNING
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2006-12-31 | 5:00P - 7:00P |  | MORAVIAN LIFT STATION | RAIN 0.7" - BOTH PUMPS WERE NOT ON DURING WEEKEND | PUMPS WERE BOTH ON AFTER COMPLAINT
IN0042366 | PRINCES LAKE MUNICIPAL STP | BARTHOLOMEW | 2006-03-10 | 3/10 - 3/13 |  | SIX MANHOLES | RAIN 4"
IN0043681 | SECOND TAMERIX ADDITION | BARTHOLOMEW | 2006-09-12 | 9/12 | 5000 | OUTFALL (PARTIALLY TREATED RELEASE) | RAIN >2", SHUT DOWN BLOWERS TO RETAIN SOLIDS | PLANNING NEW PLANT
IN0043681 | TAMERIX LAKE WWTP | BARTHOLOMEW | 2006-03-08 | 3/8 | 30000 | PLANT | RAIN 2" | NEW PLANT
IN0021628 | HARTFORD CITY MUNICIPAL STP | BLACKFORD | 2006-01-16 | 10:30A - 12:00 | 10000 | 007, 006, 005 | REPAIR OF SEWER FORCE MAIN (OLD PLANT LIFT STATION) | INTERMITENT BYPASS
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2006-08-18 | 7:30 - 7:40 | 15 | LIFT STATION | SEWAGE LEAKING OUT OF ARV VALVE | CLOSED VALVE AND CLEANED UP SEWAGE
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-04-14 | 4/14 | 450000 | PLANT | RAIN 1.57", SEWER LINE INFILTRATION | RELINEING SEWERS
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-04-15 | 4/15 | 407000 | PLANT | RAIN 0.04" | RELINEING SEWERS
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-06-28 | 9:30A - 10:20A |  | MANHOLE - CONST RELATED - PLUG BLEW OUT OF STRUCTURE | CONSTRUCTION RELATED | PUMP REMOVED & PLUG FIXED
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-08-11 | 8/11 | 589000 | PLANT | SEWER LINES INFILTRATION | RELINEING SEWERS
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-09-14 | 9/14 | 1550000 | PLANT | RAIN 1.58" | NEW PLANT HEADWORKS UNDER CONST, RELINING SEWERS
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-10-28 | 10/28 | 734000 | PLANT | RAIN 1.08", SEWER LINE INFILTRATION | CONSTRUCTION PROJECT FOR NEW HEADWORKS UNDERWAY
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-11-16 | 11/16 - 11/17 | 2976000 | PLANT | RAIN 1.85" | RELINEING SEWER LINES
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-12-01 | 12/1 - 12/2 | 2515000 | PLANT | RAIN 1.86" | RELINEING SEWER LINES
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2006-12-23 | 12/23 | 101000 | PLANT | RAIN 1.2" | RELINING SEWERS
IN0036951 | ZIONSVILLE MUNICIPAL STP | BOONE | 2006-12-13 | 2:25A - 4:15A | 40000 | MAIN LIFT STATION (4TH ST) | TEMPORARY PUMP AROUND FOR PUMP REPLACEMENT FAILED | ADDITIONAL THRUST BLOCKING INSTALLED
IN0030325 | BROWN COUNTY STATE PARK | BROWN | 2006-01-13 | 1/13 - 1/14 |  | NORTH LIFT STATION | RAIN 1.5", INFILTRATION | REPAIRS PLANNED FOR SEWAGE LINES
IN0030325 | BROWN COUNTY STATE PARK | BROWN | 2006-04-18 | 4:30 - 5:45 |  | EQ BASIN | VALVE OFF AFTER UV LIGHT INSTALLATION, FILTER OVERFLOW | PAY MORE ATTENTION TO VALVE POSITION
IN0030325 | BROWN COUNTY STATE PARK | BROWN | 2006-05-29 | 11:30A | 1200 | EQ OVERLOADED SAND FILTERS | POWER FAILURE WHEN PUMPS RESTORED EQ OVER LOADED FILTERS
IN0030325 | BROWN COUNTY STATE PARK | BROWN | 2006-08-31 | ? - 11:30A |  | LIFT STATION | GRINDER PUMPS CLOGGED | CLEANED PUMPS & LIFT STATION
IN0058416 | HELMSBURG REGIONAL SEWER DIST. | BROWN | 2006-07-17 | 10:30A - 8:00P | 3000 | FORCE MAIN | BROKEN PLASTIC CLEANOUT, REPLACED
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-01-13 | 9:30A - 7:00A (1/14) | 737000 | OUTFALL 101 (EQUALIZATION) | RAIN 1.16"
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-01-20 | 10:30A - 10:33A |  | DIGESTER OVERFLOW TO GROUND | OPERATOR DISTRACTED, SLUDGE COLLECTED & DISPOSED OF | RESIST DESTRACTIONS DURING WASTING
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-01-25 | 2:30P - 4:30P | 100 | RAS PIPE | LEAK IN RAS PIPE REQUIRED EQ BASIN OPENING TO REPAIR
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-01-26 | 10:00A - 6:30A (1/27) | 100000 | OUTFALL 101 (EQUILIZATION) | LEAK IN RAS PIPE REQUIRED EQ BASIN OPENING TO REPAIR
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-03-01 | 1:00P - 3:30P | 500 | MANHOLE # 53B | SEWER MAIN STOPPED UP AT LIFT STATION
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-03-09 | 3/9 - 3/13 | 1900000 | MANHOLES 47, 51 | RAIN 3.4", PARTIAL SEWER BLOCKAGE | PLANNING I&I REPAIRS THIS SUMMER
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-03-31 | 6:44P - 7:15P | 3100 | JAIL MANHOLE # 1 | POWER FAILURE, EQUIPMENT FAILURE | REPAIR STATION
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-04-04 | 2:45P - 3:15P | 3000 | JAIL MANHOLE # 1 | RAIN SHORTED ALARM & ELECTRICAL | CHECKING AND MAKING REPAIRS
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-04-07 | 1:45P - 2:00P | 1500 | LIFT STATION | OVERFLOW WHILE MAKING LIFT STATION REPAIRS
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2006-07-20 | 8:00P - 2:30P | 800 | FORCE MAIN | BROKEN FORCE MAIN | REPAIRED, LIME SPREAD AND SEPTIC HAULER CLEANED AREA
IN0049883 | SPRUNICA ELEMENTARY SCHOOL | BROWN | 2006-01-18 | 9:00A - 12:00P (1/23) |  | BYPASS SAND FILTERS | SANDFILTER SPRAY NOZZLE FAILURE | REPLACING SPRAY NOZZLE, SAND & MEDIA
IN0039799 | BURLINGTON MUNICIPAL STP | CARROLL | 2006-12-15 | 6:45A - 9:00A | 300 | HAUN DRIVE | ONE OF TWO PUMPS FAILED TRIPPING OVERLOAD | REPAIRED PUMP
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-04-15 | 12:00P - 7:00A (4/16) |  | EQ TANK OVERFLOWING INTO TWO DAY POND | RAIN 2.467"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-04-16 | 7:00A - 7:00A (4/17) |  | EQ TANK OVERFLOWING INTO TWO DAY POND | RAIN 3.7", PLANT & COLLECTION SYSTEM FLOODED
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-04-17 | 4/17 - 4/18 |  | EQ TANK OVERFLOWING INTO TWO DAY PONDS | RAIN 3.7"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-04-18 | 4/18 - 4/19 |  | EQ TANK OVERFLOWING INTO TWO DAY PONDS | RAIN 3.7"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-04-19 | 7:00A - 1:00A (4/20) | 90000 | EQ TANK OVERFLOWING INTO TWO DAY PONDS | RAIN 3.7"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-05-12 | 6:00A - 6:006 (5/13) | 930000 | EQ TANK OVERFLOW | RAIN 2.98"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-05-13 | 5/13 - 5/14 | 888000 | EQ TANK OVERFLOW | RAIN .34"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-05-14 | 6:00A - 6:006 (5/15) | 840000 | EQ TANK OVERFLOW | RAIN .32"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-05-15 | 5/15 - 5/16 |  | EQ TANK OVERFLOWING INTO TWO DAY PONDS | RAIN 0.13"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-05-16 | 5/16 - 5/17 |  | EQ TANK OVERFLOWING INTO TWO DAY PONDS | RAIN 0.07"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-05-17 | 5/17 - 5/18 | 108000 | EQ TANK OVERFLOWING INTO TWO DAY PONDS | RAIN 0.32"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-05-18 | 6:00A - 6:00A (5/19) | 54000 | EQ TANK OVERFLOW TO TWO DAY PONDS | PLANT CATCHING UP AFTER 4.24" OF RAIN
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-11-17 | 12:15A - 7:00A | 81750 | EQ TANK OVERFLOW TO TWO DAY POND | RAIN 1.7"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-11-30 | 11/30 | 555000 | EQ TANK OVERFLOW | RAIN 2.09"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2006-12-02 | 7:00A - 11:00P | 243000 | EQ TANK OVERFLOW | RAIN 2.09"
IN0020354 | WALTON MUNICIPAL STP | CASS | 2006-05-10 | 6:00P - 2:30A (5/11) | 258000 | LIFT STATION | RAIN 2.24"
IN0020354 | WALTON MUNICIPAL STP | CASS | 2006-05-25 | 9:00A - 11:45A |  | LIFT STATION | PUMP FAILURE
IN0020354 | WALTON MUNICIPAL STP | CASS | 2006-11-30 | 2:30A - 1:30P (12/1) | 36000 | COLLECTION LIFT STATION | RAIN 1.42"
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-01-10 | 1/10 |  | MANHOLE 3-82A | RAIN 1.5" | AGREED ORDER WITH IDEM TO PERFORM SEWER SYS EVALUATION
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-01-17 | 11:30 |  | MANHOLE 3-82A | RAIN 0.8" | AO WITH IDEM, SSES TO REDUCE I&I
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-03-11 | 3/11 |  | MANHOLES 3-82A * 3-171 | RAIN 3.5" | UNDER IDEM AGREED ORDER
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-03-12 | 3/12 |  | MANHOLE 3-149A, 3-82, 3-52 | RAIN 4.2" | OPERATING UNDER AN IDEM AGREED ORDER
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-03-30 | ? - 3:30P |  | MANHOLE 3-159 | ROOTS IN SEWER - ROOTS WERE CUT TO OPEN STOPPAGE | OPERATING UNDER AN IDEM AGREED ORDER
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-04-21 | 4/21 |  | MANHOLE 3-171 & 3-82A | RAIN 0.9" | OPERATING UNDER AN IDEM AGREED ORDER
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-06-10 | 6/10 - 6/11 |  | 3-82-B IN PARK | RAIN 1.4"
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-06-20 | 04:00 - 09:00 |  | MANHOLE 3-82A | RAIN 1.5" | WORKING ON SEWER SYSTEM EVALUATION
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-07-14 | 7:30P - 10:15P |  | MANHOLE 3-82A | RAIN 2.5" | OPERATING UNDER AN IDEM AGREED ORDER, WORKING ON SSES
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-07-30 | 9:00P - 9:15P |  | SADDLEBACK # 1 STATION | EQUIPMENT FAILURE, CONTROL BREAKER TRIPPED | OPERATING UNDER AN IDEM AGREED ORDER TO ADDRESS OVERFLOWS
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-09-12 | 9/12 - 9/13 |  | MANHOLES 30171 3-82A & 3-151 | RAIN 4.3" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-09-22 | 9/22 - 9/24 |  | MANHOLE 3-82A, 3-171, 3-151, 3-272 & SPRING ST RETENTION BASIN | RAIN 5.4" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-10-17 | ? - 09:00 |  | MAPLE DR LIFT STATION | EQUIPMENT FAILURE, RELAY BURNT OUT | OPERATING UNDER AN IDEM AGREED ORDER, SMOKE TESTING SEWERS
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-10-17 | 10/17 |  | MANHOLES 3-82A, 3-171, 3-151, 3-151A | RAIN 2.5" | OPERATING UNDER AN IDEM AGREED ORDER - SMOKE TESTING
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-10-27 | 10/27 |  | MANHOLE 3-82A | RAIN 1.3" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-11-15 | 4:45P - 11:00P |  | MANHOLE 3-82A | RAIN 0.9" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-12-01 | 01:00 |  | MANHOLE 3-82A | RAIN 1.2" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2006-12-26 | 12:00 |  | MANHOLE 3-82A | RAIN 1.5" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-01-23 | 1:00P - 1:15P | 300 | STATION 21 / POTTERS LANE | LOST A BREAKER THAT KNOCKED OUT THE CONTROL CABINET | INSPECTION OF PUMPS & ELECTRICAL SCHEDULED
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-02-05 | 2/5 - 2/6 | 500 | MANHOLE AT PLANT | GRIT SYSTEM SEWER STOPPED UP CAUSING OVERFLOW | PREVENTIVE MAINTENANCE CLEANING
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-04-02 | 10:30P - 11:30P | 1000 | MANHOLE AT LIFT STATION # 1 6420 ST RD 60 | POWER FAILURE, STORMS, CINERGY
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-04-19 | 4:00A - 6:30A |  | MANHOLE AT STA 31 6400 ST RD 60 | LOST POWER FROM CINERGY (STORM) BACKUP PUMP FAILURE | CORRECTING PUMP PROBLEM
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-04-21 | 3:00P - 5:30P (4/22) | 2000 | MH ON N CLARK | RAIN 2"
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-05-19 | 11:00A - 12:00P (5/19) | 200 | HARRISON AVE & PHELPS | MAIN LINE WAS BLOCKED
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-06-15 | 1:00P - 9:00P | 45000 | FORCE MAIN AT STA # 24 - BEFORE CROSSING SILVER CK | BREAK IN FORCE MAIN
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-06-27 | 9:00A - 10:00A | 100 | STA 23 - MANHOLE ON WALNUT GROVE | BLOCKAGE IN MAIN SEWER LINE
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-07-14 | 8:00P - 11:00P | 750 | MANHOLE ON 600 N CLARK | RAIN 1.6"
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-09-23 | 1:00A - 3:00A (9/24) | 5000 | MANHOLES N CLARK, WASHINGTON & LINCOLN | RAIN 7.8"
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-09-24 | 2:00A - 4:00A |  | PRIMARY CLARIFIER # 1 | RAIN 7.8", FLOOD CONDITIONS
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-10-07 | 2:00P - 3:30P (10/9) | 500 | STORM LINE AT ARLINGTON & DEPAW | STORM DRAIN CONNECTED TO MAIN SEWER LINE | GOING TO PLUG STORM DRAIN TO PREVENT FURTHER OVERFLOWS
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-11-02 | 11:00A - 12:00P | 250 | MANHOLE (AIR RELIEF VALVE) ON HALLMARK DR | AIR RELIEF VALVE MALFUNCTION | VALVE WAS CLOSED
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2006-12-30 | 11:00A - 12:30P | 500 | AIR RELIEF VALVE I265 1 MILE W OF I65 | AIR RELIEF VALVE FAILURE | REPAIR VALVE
IN0030147 | DEAM LAKE STATE RECREATION ARE | CLARK | 2006-09-25 | 9:30A - 9:40A |  | 6" FORCE MAIN / CAUSEWAY | BROKEN FORCE MAIN - LIFT STATION SHUT DOWN IMMEDIATELY | REQUEST IN PLACE TO REPLACE FORCE MAIN
IN0030147 | DEAM LAKE STATE RECREATION ARE | CLARK | 2006-12-04 | 12/4 |  | FORCE MAIN RUPTURED | BROKEN FORCE MAIN | MONEY REQUESTED TO REPLACE FORCE MAIN
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2006-03-09 | 3/9 - 3/10 | 12000 | MANHOLE AT 305 RR ST, # 1 LIFT STATION | RAIN | PLAN TO JET CLEAN & TV LINES
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2006-03-11 | 09:30 - 14:45 | 10000 | TWO MANHOLES S FERGUSON, RAILROAD ST | RAIN 8" | CHECKING LINES FOR I&I
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2006-03-11 | 09:22 - 24:00 | 100000 | HENRYVILLE 1 LIFT STATION | RAIN 8" | CHECKING LINES FOR I&I
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2006-03-12 | 3/12 - 3/13 | 162000 | HENRYVILLE LIFT STATION | RAIN | LOOKING FOR INFLOW SOURCES
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2006-03-13 | 3/13 | 8000 | HENRYVILLE LIFT STATION | RAIN 1.5" | LOOKING FOR INFLOW SOURCES
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2006-05-29 | 07:30 - 08:20 | 5000 | HENRYVILLE 1 LIFT, NORTH PENN ST | LOST ONE OF THREE PHASE SERVICE FOR 30 MIN
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2006-07-14 | 18:30 - 22:00 |  | HENRYVILLE LIFT STATION & MANHOLE AT 305 RAILROAD ST | RAIN, POWER FAILURE (STORM)
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2006-03-13 | 3/13 - 3/17 | 35000 | MANHOLE ON PORT ROAD | RAIN 2.75" - LIFT STATION COULD NOT HANDLE FLOW | TO EVALUATE STATION
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2006-07-20 | 7/20 | 3000 | SILVER CREEK LIFT STATION | CHECK VALVE FAILED ON PUMP | PULLED PUMP AND REPAIRED
IN0043621 | NEW PROVIDENCE (BORDEN)_STP | CLARK | 2006-09-05 | ? - 7:15A |  | FORCE MAIN NEAR CREEK CROSSING | HOLE IN FORCE MAIN | REPAIRED, AREA CLEANED - REVIEW WITH ENGINEER
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2006-01-14 | 10:00A - 10:50A | 50 | BASEMENT DRAIN AT 3613 PENNSYLVANYA DR | BLOCKAGE IN SEWER | SEWER CLEANED WITH JET, TO BE ADDED TO WEEKLY MAINT.
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2006-08-17 | 10:35A - 11:10A | 10 | SEEPAGE FROM MANHOLE - 928 ASSEMBLY RD | BLOCKAGE IN MAIN SEWER LINE | TO FOLLOW UP WITH SEWER INSPECTION & TV
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2006-09-23 | 11:00A - 4:00P | 150 | 1202 W WALFORD DR BASEMENT DRAIN | RAIN 6.7", RESIDENCE HAS AN OPEN CLEANOUT (CAP MISSING) | REPLACED CLEANOUT CAP - CHECKING AREA FOR OPEN CLEANOUTS
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2006-09-23 | 10:00A - 4:00P | 100 | 2908 W WALFORD DR BASEMENT DRAIN | RAIN 6.7", RESIDENCE HAS A BROKEN CLEANOUT CAP | REPLACED CLEANOUT CAP - CHECKING AREA FOR OPEN CLEANOUTS
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2006-11-07 | 10:00A - 10:45A | 50 | 1003 PENNSYLVANIA DR BASEMENT DRAIN | RAIN 0.04", BASEMENT DRAIN NEAR ELEVATION OF MAIN LINE | HOME OWNER NOTIFIED TO INSTALL BACK FLOW PREVENTER
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-03-11 | 3/11 |  | SSO'S 6, 7, 8, 9, 10, 5 & 4 | RAIN 2" | PROJECT UNDERWAY, ENDING AT THE END OF 2006
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-03-12 | 3/12 |  | SSO # 16 | RAIN 3"
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-06-11 | 6/11 |  | #8 & #9 MANHOLES | RAIN 2" | CLEAN AREA - PROJECT IN THE WORKS TO BE DONE AT END OF YEAR
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-07-14 | 7:00P - 12:00P (7/15) |  | MANHOLES IN COLLECTION SYSTEM OVERFLOWING | RAIN 5" | TOWN HAS CONSTRUCTION PROJECT UNDERWAY, COMPLETE IN 2006
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-09-12 | 3:00 - 10:00 | 1000 | MANHOLES 834 & 624 S INDIANA AVE | RAIN 2" | WORKING ON IMPROVEMENTS IN THE AREA
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-09-22 | 9/22 |  | SSO # 8, 10A, 10B, 9 | RAIN 5.6" IN 3 HRS | UPGRADE PROJECTS IN THE WORKS
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-09-23 | 9/23 | 250 | OUTFALL # 16 TWO MANHOLES AT KOCH PLACE | RAIN 7.5", FLOODING | CLEANED ATREA WITH VAC TRUCK, LOOKING TO UPGRADE LIFT STATION
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2006-10-17 | 10/17 |  | MANHOLE # 8 & 9 | RAIN 3" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0109533 | WASHINGTON TOWNSHIP RSD | CLARK | 2006-08-18 | 8/18 | 1000 | OHIO STREET LIFT STATION | BOTH PUMPS TRIPPED OUT - ELECTRICIAN COULD NOT LOCATE PROBLEM | MORE FREQUENT STATION CHECKS
IN0021211 | BRAZIL MUNICIPAL STP | CLAY | 2006-03-09 | 3/9, 3/10, 3/11-3/12 |  | MANHOLE LIFT STATION 003 | RAIN 4" | PLANS TO ELIMINATE PROBLEM
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-01-17 | 7:00A - 6:00A (1/18) | 50000 | MANHOLE AT PLANT BEFORE WET WELL | RAIN
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-03-08 | 3/8 - 3/9 | 600000 | MANHOLE AT PLANT | RAIN 5"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-03-09 | 3/9 - 3/10 | 8000 | TWO LIFT STATION MANHOLES | RAIN 5"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-03-12 | 3/12 | 60000 | MANHOLE @ 1ST ST, E 7TH ST & PLANT WET WELL | RAIN 2"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-03-22 | 3/22 - 3/23 |  | LIFT STATION MANHOLE AT EAST 7TH ST | REPLACING PUMP & VALVE DID NOT HOLD, FLOODED STATION | VAC TRUCK PUMPED STATION
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-04-06 | 4/6 - 4/7 |  | E 7TH LIFT STATION, W 1ST LIFT STATION, W 7TH MANHOLE | RAIN
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-05-11 | 7:00A - 7:00P |  | MANHOLE BEFORE WET WELL AT PLANT | RAIN 2.1"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-05-25 | 6"30A - 1:00P |  | MANHOLE BEFORE WET WELL AT PLANT | RAIN 1.6"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-06-02 | 8:00A - 3:00A (6/3) |  | MANHOLE AT PLANT | RAIN 2.5"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-09-12 | 6:00A - 7:00P (9/13) |  | PLANT, 1ST & 7TH STREET LIFT STATIONS | RAIN 6" TOTAL
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-09-18 | 5:30A - 6:30A |  | 1ST STREET & 7TH STREET LIFT STATIONS | RAIN 1.8"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-10-17 | 6:30A - 2:00P |  | LIFT STATION MANHOLES - E 7TH ST, 1ST ST, AT WWTP | RAIN 2.6"
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-10-27 | 8:00A - 11:00 (10/29) |  | MANHOLE LIFT STATION ON 1ST ST & MANHOLE AT PLANT | RAIN
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-11-16 | 6:00A - 8:30P |  | THREE MANHOLES - 1ST ST LS, 7TH ST LS, PLANT | RAIN
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-11-30 | 12:00P - 8:00P |  | LIFT STATION MANHOLE 1ST ST, 7TH ST, AT WWTP | RAIN
IN0039861 | CLAY CITY MUNICIPAL STP | CLAY | 2006-12-22 | 12/22 |  | LIFT STATION MANHOLES - 1ST ST, 7TH ST, PLANT | RAIN
IN0025224 | STAUNTON MUNICIPAL STP | CLAY | 2006-03-10 | 3/10 |  | POLISHING POND | RAIN 3" | NEW SEWER LINE CONSTRUCTION
IN0020443 | COLFAX MUNICIPAL STP | CLINTON | 2006-05-10 | 8:00P - 11:00A (5/11) | 100000 | MANHOLE MERIDIAN ST | PUMP FAILURE - RAIN 2.8"
IN0022934 | FRANKFORT MUNICIPAL STP | CLINTON | 2006-05-11 | 2:00P - 6:00P | 5000 | MANHOLE 751A | RAIN 3.22", PLANT AT 170% CAPACITY, GREASE PLUGGING SEWER | WILL MAKE MONTHLY INSPECTION OF AREA SEWER
IN0031976 | MULBERRY MUNICIPAL STP | CLINTON | 2006-04-16 | 10:00P - 2:00P (4/17) | 25000 | MANHOLE # 131 | RAIN 3.4" | SPREAD LIME AROUND AREA
IN0039985 | ELNORA MUNICIPAL STP | DAVIESS | 2006-03-12 | 3/12 - 3/14 | 75000 | WET WELL 101 | RAIN 7.5" | DOING I & I STUDY
IN0034932 | MONTGOMERY MUNICIPAL STP | DAVIESS | 2006-03-09 | 06:00 - 18:00 | 100000 | MAIN LIFT STATION | RAIN 4.5" | WORKING ON I & I REDUCTION
IN0034932 | MONTGOMERY MUNICIPAL STP | DAVIESS | 2006-04-19 | 06:00 - 15:00 | 11000 | MAIN LIFT STATION | RAIN 4.1" | SEWER REHABILIATATION IS PROGRESS
IN0020214 | ODON MUNICIPAL STP | DAVIESS | 2006-03-09 | 3/9 - 3/10 | 250000 | SSO # 003 | RAIN +5" | UPGRADE PLANT
IN0020214 | ODON MUNICIPAL STP | DAVIESS | 2006-06-22 | 6/23 | 100000 | SSO 003 | RAIN 2" | PLAN TO UPGRADE PLANT
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-02-16 | 10:00P - 7:15A (2/17) | 13000 | OUTFALL 002 | RAIN 0.74"
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-03-13 | 7:30A - 11:00P | 750000 | WWTP PUMPING AT CAPACITY | RAIN | TRY TO LOCATE SOURCES OF INFLOW
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-05-30 | 7:20P - 10:40P | 202000 | OUTFALL 002 | RAIN 1.7" | OPERATED PLANT TO MINIMIZE BYPASS, OVERFLOWS & FLOODING
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-05-31 | 5:00P - 8:00P | 31000 | OUTFALL 002 | RAIN | OPERATED PLANT TO MINIMIZE BYPASS, OVERFLOWS & FLOODING
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-08-28 | 7:00P - 9:00P | 104000 | OUTFALL 002 | RAIN 2.06" | MAXIMIZING FLOW THROUGH WASTEWATER PLANT
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-10-02 | 1:00P - 3:00P | 8000 | OUTFALL 002 | RAIN 1.79" | RUNNING WWTP IN WET WEATHER MODE, MAXIMUM PUMPING CAP
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-10-17 | 3:00A - NOON | 449000 | WWTP | RAIN 1.95" | MAXIMUM PUMPING AT WWTP
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-12-01 | 5:00A - 2:00P | 976000 | OUTFALL 002 | RAIN 1.73" | MAXIMIZING FLOW THROUGH WASTEWATER PLANT
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2006-12-31 | 7:00P - 9:00P | 6000 | OUTFALL 002 | RAIN 0.81" | WWTP RUNNING IN WET WEATHER MODE
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-01-13 | 1/13 - 1/18 | 902000 | OUTFALL # 101 - OVERFLOWING FROM EQ BASIN TO POLISHING POND | RAIN 1.96" OVER SEVERAL DAYS
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-01-29 | 1/29 | 530000 | OUTFALL 101, PROCESS BYPASS | RAIN 0.86", BLENDED WITH FINAL EFFLUENT & SAMPLED
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-02-09 | 2/9 |  | LIFT STATION # 4 US 6 | BROKEN SEWER LINE FILLED LIFT STATION WITH SAND, PLUGGED PUMPS | IN THE PROCESS OF INSTALLING NEW LIFT STATION
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-02-17 | 10:00 |  | OUTFALL 101 | RAIN 1.23"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-03-13 | 3/13 |  | OUTFALL 101 | RAIN 1.2"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-05-12 | 5/12 |  | OUTFALL # 101 | RAIN 1.95" | ABLE TO MEET FINAL LIMITS AT THIS TIME
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-10-17 | 18:00 - 15:00 (10/19) | 462000 | OUTFALL 101 | RAIN 1.86"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-10-17 | 10/17 | 368000 | OUTFALL 101 | RAIN 1.86"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-11-16 | 17:00 - 02:00 (11/18) | 542000 | OUTFALL 101 | RAIN 1.08" | MAXIMIZING FLOW TO WWTP
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-01 | 7:30A - 1:28A (12/2) | 270000 | MANHOLE NEAR WALNUT & BEST STS | RAIN 1.83"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-01 | 7:30A - 1:28A (12/2) | 108000 | MANHOLE @ WWTP | RAIN 1.83"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-01 | 7:30A - 6:00A (12/5) | 1400000 | OUTFALL # 101 | RAIN 1.83"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-13 | 08:30 - 01:00 (12/15) | 236000 | OUTFALL # 101 | RAIN 0.88" | WORKING ON I & I REDUCTION
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-21 | 3:315A - 1:00A (12/29) | 1307000 | OUTFALL # 101 | RAIN 1.57" | WORKING ON I & I REDUCTION
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-31 | 12/31 - 1/1 | 137000 | MANHOLE NEAR WALNUT & BEST STS | RAIN 1.03"
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-31 | 12/31 - 1/4 | 941000 | OUTFALL #101 | RAIN 1.1" | WORKING ON I & I REDUCTION
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2006-12-31 | 12/31 - 1/1 | 137000 | MANHOLE AT WWTP | RAIN 1.03"
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-01-08 | 1/8 - 1/9 |  | SSO # 004 W 4TH | PLUG AT MANHOLE, GOING OUT OVERFLOW, FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-01-10 | 1/10 | 1000 | CSO 002 IMPORTING | PLUG AT MANHOLE BRFORE LIFT STATION, FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-01-10 | 1/10 | 1000 | SSO # 003 COCHRAN | RAIN 0.25", ONE PUMP DOWN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-01-17 | 1/17 | 2000 | SSO 003 COCHRAN LIFT STATION | RAIN 0.375
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-01-23 | 7:30A - 3:00P | 500 | SSO # 4 | MAIN BLOCKAGE | ATEMPTING TO CLEAR BLOCKAGE
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-01-23 | 1/23 | 1000 | SSO # 3 COCHRAN | RAIN 0.25"
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-01-24 | 1/24 - 1/25 | 5000 | CSO # 006 & 002 | HIGH LEVEL OF OHIO RIVER BACK FLOWING INTO LIFT STATIONS
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-02-06 | AM - 3:00P | 5000 | SSO # 3 | PLUG BETWEEN LIFT STATION & MANHOLE - FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-02-09 | PM - 9:00A (2/10) | 100 | # 11-31 RANDALL AVE | SEWER MAIN PLUGGED | FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-02-10 | AM - 2:00P | 500 | SSO # 3, COCHREN LIFT | SEWER MAIN PARTIALLY PLUGGED | FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-02-16 | 2/16 | 200 | SSO # 3 | SEWER MAIN PARTIALLY PLUGGED | FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-02-23 | 2/23 | 500 | SSO # 4 WYTH | MAIN PLUGGED GOING INTO LIFT STATION | FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-03-08 | 3/8 | 100 | DIERKING LIFT STATION | BOTH PUMPS FAILED IN GRINDER STATION SERVING RETIREMENT HOME | PUMPS & ALARM BULB TO BE REPLACED
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-03-08 | 3/8 | 3000 | SSO # 3, 4, 5 | RAIN 1"
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-03-12 | 3/12 | 16000 | SSO'S, CSO'S & LIFT STATION & MANHOLES | RAIN 3"
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-03-14 | 3/14 | 5000 | BURGER KING LIFT STATION | PUMP FAILURE
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-03-20 | 1:00P - 4:30P | 5000 | SSO # 3 COCHRAN | PUMP / EQUIPMENT FAILURE
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-03-22 | 3/22 | 10000 | SSO # 1,3, 4, 5 | 3" OF MELTING SNOW
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-03-29 | 3/29 | 20000 | SSO # 3 | EQUIPMENT FAILURE, PUMP NOT PUMPING
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-04-03 | 7:30A | 20000 | SSO # 3 | RAIN 3" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-04-05 | 4/5 | 10000 | SSO # 003, BESSLER'S LIFT STATION | CHECK VALVE AIR LOCKED
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-04-15 | 1:00A - 6:00P (4/16) | 25000 | SSO 1, 3, 4 & 5 | RAIN 2.5" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-04-19 | 4/19 | 8000 | MANHOLE 9-28 | RAIN | FLUSH LINE WITH JETTER, LTCP
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-04-21 | 4/21 | 1000 | SSO # 003 | RAIN 0.25" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-05-01 | 7:30A - 10:00A | 50 | MARKERS LIFT STATION | BOTH LIFT STATION PUMPS QUIT | SERVICE PUMPS, WASH DOWN AREA
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-05-05 | 1:00P | 100 | MARKERS LIFT STATION | PUMP FAILURE ON GRINDER STATION
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-05-15 | 3:00P | 500 | CHEAK LIFT STATION | BOTH PUMPS FAILED | REPLACING PUMPS, WASH DOWN AREA
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-05-18 | 5/18 | 5000 | SSO # 003 COCKRAN | RAIN 1" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-05-25 | 3:00P - 4:00P | 5000 | MANHOLE 14-26 | MAIN LINE BLOCKAGE
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-05-26 | 5/26 | 5000 | SSO # 003 COCHRAN | RAIN 0.25"
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-06-01 | 6/1 | 5000 | SSO # 003 | RAIN 0.5"
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-06-05 | 8:00A - 8:50A |  | BUENA VISTA LIFT STATION | EQUIPMENT FAILURE AT LIFT STATION | REGULARY SCHEDULED CHECKS
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-06-07 | 6/7 | 5000 | SSO # 003 COCHREN | RAIN 0.5" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-06-18 | 12:00P - 7:30A (6/19) | 500 | BURGER KING LIFT STATION | HEAVY FLOW INTO LIFT STATION CAUSING TROUBLE WITH FLOATS | READJUST & MOVE FLOATS
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-06-27 | 8:00A - 2:00P | 500 | MORITZ LIFT STATION | EQUIPMENT FAILURE - BOTH PUMPS CLOGGED WITH DEBRIS | CHANGED RING & CUTTERS
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-06-30 | 8:00A - 10:00A | 5000 | SSO # 004 W 4TH | MAIN PLUGGED BETWEEN MANHOLE & LIFT STATION | FLUSHED WITH JETTER, REBUILD PIT AS PART OF LTCP
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-07-10 | 7/10 | 10000 | SSO # 003 - COCHRAN | MAIN GOING TO LIFT STATION PLUGGED - TO EXCAVATE
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-07-18 | 8:00A - 12:00P | 500 | AUROA CASKET WEST | POWER LOSS (POWER SUPPLIER) | WASH DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-08-11 | 8/11 | 50 | 10439 MILLSTONE DR | LEAKING SEWER MAIN | TO BE REPAIRED
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-08-14 | 8/14 | 1000 | 2" FORCEMAIN BLAIR RD | CUT WITH BACKHOE | LOCATE LINES BEFORE DIGGING
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-08-20 | 1:00P - 5:00P | 10000 | SSO # 003 COCHRAN | POWER FAILURE - TRANSFORMER WENT BAD AT POLE | WASH DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-08-28 | 7:30A - 9:15A | 1000 | SSO # 004 W 4TH STREET | MAIN PLUGGED GOING TO PIT | RE-DESIGN PIT WHEN THIS ONE IS DEMOLISHED
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-09-12 | 9/12 | 5000 | SSO # 003 COCHRAN LIFT | RAIN 1", PUMPS NOT KEEPING UP | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-10-16 | 10:00P - 12:00P (10/17) |  | SSO # 003 COCHRAN | RAIN 2" | LTCP
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-10-19 | 11:00P - 8:00A (10/20) |  | SSO # 003 COCHRAN | RAIN 1.5" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-10-27 | 10/27 |  | SSO # 003 COCHRAN | RAIN 1" | LTCP
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-10-29 | 1:00P - 4:00P | 5000 | LIFT STATION AT BURGER KING | 8" FORCE MAIN ON HWY 50 BROKE, SHUT DOWN TO REPAIR | WASH DOWN SOLIDS, LTCP
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-10-30 | 8:00A - 11:00A | 200 | MANHOLE # 26A | SEWER MAIN BLOCKAGE | FLUSHED WITH JETTER
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-10-30 | 10/30 | 10500 | SSO # 001, 004, 005 | OHIO RIVER RUNNING BACK INTO LIFT STATIONS
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-10-31 | 10/31 |  | SSO # 003 COCHRAN | RAIN 0.5" | LTCP
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-11-15 | 11/15 | 20000 | SSO # 003 COCHRAN | RAIN 0.5" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-11-16 | 8:00P - | 5000 | SSO # 004, 003 | RAIN 0.5" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-11-18 | 11/18 | 10000 | SSO # 1 & # 5 | RIVER FLOWING BACK INTO LIFT STATION | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-11-28 | 11:00P - 8:45 (11/29) | 10000 | SSO # 003 | RAIN 0.75" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-12-01 | 12/1 | 15000 | SSO # 003 COCHRAN | RAIN 2" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-12-01 | 12/1 | 1000 | SSO # 005 W SIDE | RAIN 2" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-12-01 | 12/1 | 1000 | SSO # 001 DECATUR | RAIN 2" | LONG TERM CONTROL PLAN
IN0050903 | AURORA, CITY OF | DEARBORN | 2006-12-01 | 6:00A | 5000 | SSO # 004 | RAIN 2" | LONG TERM CONTROL PLAN
IN0022781 | DILLSBORO MUNICIPAL STP | DEARBORN | 2006-11-22 | ? - 11/22 |  | SMALL LEAK IN FORCE MAIN | LEAKING FORCE MAIN | REPAIR FORCE MAIN, CLEAN AREA WITH VAC TRUCK
| GREENDALE MUNICIPAL STP | DEARBORN | 2006-03-12 | 3/12 - 3/13 |  | MANHOLE BEHIND SPEEDWAY | RAIN 3.5" | LOOKING FOR INFLOW SOURCES
| GREENDALE MUNICIPAL STP | DEARBORN | 2006-08-18 | 5:15P - 7:45P | 5000 | SANITARY SEWER THAT RUNS ALONG RAIL ROAD TRACKS | PLASTIC DEBRIS IN SANITARY SEWER CAUSING OBSTRUCTION | CONTACTING INDUSTRIAL USERS
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-03-08 | 2:49P - 9:02P | 83000 | WWTP | RAIN 2"
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-03-09 | 3:16P - 4:32P | 17000 | WWTP | RAIN 1.5" | PREVENTING SOLIDS WASHOUT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-03-11 | 7:06P - 12:01P | 64000 | WWTP | RAIN 1.3"
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-03-12 | 3/12 | 92000 | WWTP, MAIN LIFT STATION | RAIN 1.7"
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-04-02 | 11:20 - 6:10A (4/3) | 57000 | WWTP | RAIN 1" | MANAGING PLANT TO MINIMIZE IMPACT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-04-21 | 5:00P - 6:30P | 4000 | MAIN LIFT STATION | RAIN 2.2"
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-04-21 | 5:15P - 8:27 | 25000 | WASTEWATER PLANT | RAIN 2.2" | MANAGED PLANT TO MAINTAIN SOLIDS
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-09-12 | 1:28P - 3:47P |  | WWTP | RAIN 2.8" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-09-22 | 11:05 - 11:58 | 10000 | WWTP | RAIN 1.3" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-10-17 | 7:22A - 9:00A | 30000 | WWTP | RAIN 1.7" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-10-28 | 5:34A - 6:37A | 18000 | WWTP | RAIN 1.3" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2006-12-01 | 4:00A - 9:37A | 71000 | WWTP | RAIN 2.3", POWER FAILURE
IN0058408 | ST. LEON WWTP | DEARBORN | 2006-07-20 | 7/20 - 7/21 |  | FORCE MAIN - PIPE FAILURE / SLOPE SLIPPAGE | BROKEN 2" FORCE MAIN - FROM THE IDEM SPILL LINE
IN0058408 | ST. LEON WWTP | DEARBORN | 2006-07-24 | 11:30A - 2:30P | 350 | FORCE MAIN VALVE | COUNTY TRUCK RAN OVER VALVE
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-03-08 | 5:00P - 6:30 | 6000 | 006 & MANHOLE 5014 | EQUIPMENT FAILURE, LIFT STATION
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-03-10 | 3/10 - 3/11 |  | 002 | RAIN 2" | TO TV SEWER LINES
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-03-12 | 3/12 - 3/14 | 126000 | 002 | RAIN 3.75" | LOOKING FOR INFLOW SOURCES
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-03-12 | 3/12 |  | 005, 006 | RAIN 3.75" | LOOKING FOR INFLOW SOURCES
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-03-13 | 3/13 |  | 006 | RAIN 3.75" | LOOKING FOR INFLOW SOURCES
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-04-22 | 2:30P - 9:30A (4/23) |  | 002 | RAIN 2" | WORKING ON I & I REDUCTION
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-06-05 | 6/5 | 2000 | LIFT STATION 2 | EQUIPMENT FAILURE | REPLACED FLOATS & RESET PUMPS
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-09-06 | 6:00P - 7:00P |  | LIFT 2 | PUMP PLUGGED WITH RAG
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-10-11 | 8:30A - 9:00A | 2000 | SMALL HOLE IN EQUALIZATION TANK | SMALL HOLE IN EQUALIZATION TANK | PATCHED HOLE
INU043168 | VALLEY RURAL UTILITY | DEARBORN | 2006-10-29 | 10:30A - 11:15A | 5000 | LIFT STATION # 6 | EQUIPMENT FAILURE | RESET PUMP
IN0060704 | LAKE SANTEE REGIONAL WASTE | DECATUR | 2006-05-31 | 9:00A - 7:30A (6/1) | 26000 | ARV STRUCTURE AT 391 W SANTEE DR | PIPE / FITTING FAILURE | LINE EXCAVATED & REPAIRED
IN0020842 | SAINT PAUL MUNICIPAL STP | DECATUR | 2006-03-12 | 3/12 - 3/13 |  | RIVERBEND LIFT STATION | RAIN 5.5" | WORKING ON I & I REDUCTION
IN0020842 | SAINT PAUL MUNICIPAL STP | DECATUR | 2006-07-27 | 10:00 - 14:00 |  | RIVERBEND LIFT STATION | RAIN 6.5"
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-01-13 | 1/13 - 1/14 |  | LIFT STATION ON S WEST ST | RAIN 0.9" | LOOKING FOR INFLOW SOURCES
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-01-17 | 2:00P |  | LIFT STATION ON SW STREET | RAIN 0.9" | LOOKING FOR INFLOW SOURCES
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-03-08 | 3/8 - 3/10 |  | LIFT STATION SW STREET | RAIN 3.3" | WORKING ON I & I REDUCTION
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-03-08 | 3/8 - 3/13 |  | LIFT STATION ON SW STREET | RAIN 6.45" | LOOKING FOR INFLOW SOURCES
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-03-08 | 3/8 |  | LIFT STATION ON SW STREET | RAIN 1.9" | WORKING ON I & I REDUCTION
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-03-31 | 10:00P - 6:00P (4/1) |  | LIFT STATION ON S WEST STREET | RAIN 1" | LOOKING FOR INFLOW SOURCES
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-04-02 | 4/2 - 4/3 |  | LIFT STATION SOUTH WEST STREET | RAIN 0.75", POWER FAILURE | LOOKING FOR INFLOW SOURCES
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-04-07 | 7:30P - 12 NOON (4/8) |  | LIFT STATION SOUTH WEST ST | RAIN 1.8" | ONGOING EFFORT TO LOCATE I & I
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-04-14 | 10:45 - 10:00A (4/15) |  | LIFT STATION ON S WEST STREET | RAIN 1.55" | CONTINUNING EFFORTS TO LOCATE INFLOW
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-06-11 | 6/11 |  | LIFT STATION ON S WEST STREET | RAIN 1.4" | ONGOING EFFORT TO LOCATE I & I
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-08-10 | 2:45P - 6:30P |  | LIFT STATION ON SOUTH WEST ST | RAIN 8.88", POWER FAILURE
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-08-14 | 7:30P - AM (8/15) |  | LIFT STATIONS AND MANHOLES ALONG SANDI LANE & MAIN ST | RAIN 3"
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-08-28 | 8:30A - PM |  | LIFT STATION ON SW STREET | RAIN 10" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-10-16 | 10/16 - 10/18 |  | LIFT STATION ON S WEST ST | RAIN 2.35" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-10-27 | 10/27 - 10/28 |  | LIFT STATION ON S WEST ST | RAIN 1.7" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-11-16 | 11/16 - 11/17 |  | LIFT STATION ON S WEST STREET | RAIN 1.5" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-11-30 | 11/10 |  | LIFT STATION ON S WEST ST, MANHOLE # 78 | RAIN 2.3" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-12-01 | 12/1 - 12/2 |  | LIFT STATION ON S WEST ST | RAIN | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-12-12 | 12/12 |  | LIFT STATION S WEST ST | RAIN 0.85" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-12-22 | 12/22 |  | LIFT STATION ON WEST ST | RAIN 1.25" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-12-26 | 12/26 |  | LIFT STATION SOUTH WEST ST | RAIN 0.75" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2006-12-31 | 12/31 - 1/1 |  | MANHOLE # 96 & 97 | RAIN 1.6" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-01-17 | 1:46P - 9:28A (1/18) | 400000 | HEADWORKS | RAIN 0.3"
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-01-29 | 1/29 - 1/31 | 200000 | HEADWORKS | RAIN 0.9"
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-02-03 | 2/3 - 2/6 | 200000 | HEADWORKS | RAIN 0.8" | SEWER PROJECT TO START 2/18/06
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-02-16 | 11:18A - 2:45P (2/19) | 500000 | HEADWORKS | RAIN & CLOGGED PUMP
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-03-10 | 3/10 - 3/13 | 400000 | HEADWORKS | RAIN
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-03-13 | 3/13 - 3/15 | 150000 | LIFT STATION 002 | RAIN
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-03-14 | 3/14 - 3/16 |  | HEADWORKS | RAIN | HAVE STARTED SEWER PROJECT
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-04-14 | 4/14 - 4/19 | 500000 | HEADWORKS | RAIN
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-05-02 | 8:00A - 9:30A (5/3) | 200000 | HEADWORKS | RAIN 0.6"
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-05-11 | 5/11 |  | HEADWORKS | RAIN 1.4"
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-05-11 | 5/11 - 5/22 | 950000 | HEADWORKS | RAIN 3.5" IN SIX DAYS
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-06-21 | 6/21 - 6/22 |  | HEADWORKS | RAIN 0.9"
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-06-22 | 6/22 | 300000 | HEADWORKS | RAIN 0.8"
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-06-22 | 6/22 |  | HEADWORKS & LIFT STATION | RAIN
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-10-17 | 10/17 |  | WASTE WATER TREATMENT PLANT | RAIN 2.5" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-10-17 | 8:30 - 3:46 (10/19) | 700000 | WWTP | RAIN 2.5"
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-11-07 | 11/7 - 11/9 | 800000 | HEADWORKS | RAIN 0.3" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-11-17 | 9:04A - 1:00P | 1000000 | HEADWORKS | RAIN 1.3" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-12-01 | 12/1 - 12/4 | 536000 | WWTP | RAIN 2.4" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-12-22 | 12/22 - 12/24 | 1000000 | HEADWORKS | RAIN 0.7" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0022136 | ALBANY MUNICIPAL STP | DELAWARE | 2006-12-26 | 8:30A - 8:00A (12/28) | 1200000 | HEADWORKS | RAIN 0.8" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-01-02 | 5:00P - 6:30P | 500 | 606 N MANHATTAN | ROOTS IN SEWER, AREA CLEANED | CONTINUE TO MONITOR
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-01-23 | 1:40P - 2:20P | 100 | MANHOLE 3910 FRANKLIN ST | ROOTS IN SEWER LINE | MONITORING SEWER LINE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-01-28 | 10:55A - 11:55A |  | 1603 COWING DR | ROOTS IN SEWER LINE | CHECK LINE ON REGULAR BASIS
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-02-02 | 11:45A - 12:40P | 50 | SEWER BACKUP 600 BLOCK ELM | DEBRIS IN SEWER LINE, CLEANED | MONITOR LINE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-02-07 | 11:30A - 1:00P | 100 | 2500 BROADWAY (RICHARDS RESTAURANT) | GREASE BUILD-UP IN SEWER LINE | JET RODDED SEWER LINE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-02-27 | 2:00P - 3:00P | 300 | 250 S GRANDVILLE | GREASE & ROOTS IN SEWER LINE, LINE CLEANED | GOING TO TV LINE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-03-09 | 5:30P - 7:30P | 100 | 2104 E GRACE CT | RAIN 1", SEWER BLOCKAGE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-03-10 | 4:30P - 6:00P | 100 | 3556 JOHNSON CIR | CLOGGED SEWER | RODDED LINE, MONITORING
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-03-12 | 9:26A - 2:00P | 300 | OAKWOOD | SEWER PLUGGED | MAINT TO RUN PREVENT CHECKS
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-03-12 | 9:26A - 2:00P | 300 | OAKWOOD & COWING | RAIN 1.25", SEWER PLUGGED
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-03-13 | 5:30P - 7:30P | 100 | 2104 E GRACE CT | SEWER PLUGGED | MAINT TO RUN PREVENT CHECKS
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-05-13 | 5/13 |  | MANHOLE #1, #2, #3 ON WHITERIVER BLVD | RAIN 3.24"
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-05-30 | 3:12P - 7:00P | 30000 | LYNCH AVE CSO | OBSTRUCTION IN PIPE | SEWER REHABILIATATION IS PROGRESS
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-05-30 | 12:00P |  | LYNCH AVE | OBSTRUCTION IN PIPE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-08-16 | 5:00P - 6:00P |  | CSO 18 | BAR SCREEN MALFUNCTION CAUSING BACKUP IN LINE | MONITOR BAR SCREEN
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-08-25 | 3:00P - 3:20P | 1000 | 1809 E FULKNER / BUNCH BLVD | SEWER LINE PLUGGED
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-08-29 | 10:15A - 10:45A | 100 | 1809 FAULKNER & BUNCH BLVD | SANITARY LINE RESTRICTED | LINE CONDITION TO BE EVALUATED FOR REPAIRS
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-10-25 | 6:30P - 7:45P | 500 | 3710 BROOKS DR | ROOTS IN SEWER LINE | DEROOT THE LINE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-11-08 | 10:20A - 1:00P | 300 | 3400 N CHADAM LN | GREASE IN SEWER | PUT ON DEGREASING SCHEDULE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2006-12-01 | 2:50A - 4:00P | 800000 | MANHOLE BENSON RESIDENCE - MOORE RD | RAIN 2" & CONST AT WWTP REDUCED FLOW THROUGHPUT | MONITOR SITUATION
INU043168 | VALLEY RURAL UTILITY | DELAWARE | 2006-04-17 | 2:15P - 12:30 (4/18) | 13200 | 002 | RAIN 2.25" | LOOKING FOR INFLOW SOURCES
IN0020150 | YORKTOWN MUNICIPAL STP | DELAWARE | 2006-03-12 | 3/12 |  | FINAL CLARIFIERS | RAIN | I&I INFLOW STUDY
IN0020150 | YORKTOWN MUNICIPAL STP | DELAWARE | 2006-12-01 | 9:30A |  | MANHOLE | RAIN 2.64" | WORKING ON I & I REDUCTION
IN0039748 | BIRDSEYE MUNICIPAL STP | DUBOIS | 2006-05-12 | 5/12 | 5000 | LIFT STATION | PUMP FAILURE CAUSING LIFT STATION TO FLOOD | MADE REPAIRS TO PUMP & ELECTRICAL
IN0020648 | FERDINAND MUNICIPAL STP | DUBOIS | 2006-07-14 | 11:30A - 11:50A | 15000 | HEADWORKS | RAIN 5.2", PLANT FLOODED, HEADWORKS PUMP DOWN DURING STORM
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-01-02 | 3:30P - 6:00P |  | KENTUCKY ST LIFT STATION | RAIN 0.7"
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-03-09 | 3/9 |  | KY ST LIFT STATION | RAIN 2.7" | TOWN BOARD WORKING ON PROBLEM
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-03-11 | 3/11 - 3/12 |  | KY ST LIFT STATION | RAIN 4.1"
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-04-16 | 4/16 |  | KY ST LIFT STATION | RAIN 1.7"
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-04-21 | 07:30 - 11:30 |  | KY LIFT STA | RAIN 2.5"
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-09-12 | 10:30 - 3:00 |  | LIFT STA KY ST | RAIN 5.1" | PLANS TO BUILD HOLDING RESERVOIR
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-09-23 | 9/23 - 9/24 |  | LIFT STA KY ST | RAIN 8"
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-10-17 | 10/17 |  | LIFT STATION ON KY ST | RAIN 3.3"
IN0023108 | HOLLAND MUNICIPAL STP | DUBOIS | 2006-11-15 | 11/15 - 11/16 |  | LIFT STATION KENTUCKY AVE | RAIN 2.6" | PLANS ARE BEING LOOKED INTO
IN0023124 | HUNTINGBURG MUNICIPAL STP | DUBOIS | 2006-03-11 | 3/11 | 100000 | MH 187, 441 | RAIN 4" | LOOKING FOR INFLOW SOURCES
IN0023124 | HUNTINGBURG MUNICIPAL STP | DUBOIS | 2006-06-21 | 6/21 - 6/22 | 3000 | MANHOLE # 523 & FORCE MAIN | FORCE MAIN BREAK & LIFT STATION POWER FAILURE | ON GOING MAINTENANCE
IN0023124 | HUNTINGBURG MUNICIPAL STP | DUBOIS | 2006-08-14 | 8:00A - 10:30A | 2000 | VAN BUREN ST LIFT STATION | EQUIPMENT FAILURE, ELECTRICAL OVERLOAD
IN0023124 | HUNTINGBURG MUNICIPAL STP | DUBOIS | 2006-08-29 | 3:00A - 11:10A | 5000 | LIFT STATION | BROKEN FORCE MAIN | REPAIRED
IN0023124 | HUNTINGTON MUNICIPAL STP | DUBOIS | 2006-01-06 | 6:00A - 11:00A | 5000 | 19TH STREET LIFT STATION | POWER MONITOR FAILURE
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2006-03-09 | 3/9 - 3/10 | 110000 | MANHOLE KNIES LIFT STATION | RAIN 3.5" | LOOKING FOR INFLOW SOURCES
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2006-03-11 | 3/11 - 3/13 | 425000 | MANHOLE NEAR KANES LIFT STATION | RAIN 5" | WORKING ON I & I REDUCTION
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2006-03-12 | 3/12 | 100000 | MANHOLE 400 WEST LIFT STATION | RAIN 5" | LOCATED MAJOR INFLOW SOURCE
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2006-07-12 | 11:00A - 4:00P | 72000 | KNIES & HOEHGESANG LIFT STATIONS | RAIN 4" | WORKING ON I & I REDUCTION
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2006-09-12 | 9:00A - 2:30P | 48000 | MANHOLE U/S OF KNIES LS & HOCHPESANG LIFT STATION | RAIN 4.3" | WORKING ON I & I REDUCTION
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2006-01-06 | 9:45A - 12:30P |  | FORCE MAIN INLINE VALVE | MECHANICAL JOINT FAILURE
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2006-02-16 | 8:00P - 9:00A (2/17) |  | LIFT STATION 900E DUBOIS | POWER FAILURE, ELECTRIC CO TRANSFORMER | ELECT CO TO NOTIFY RWD WHEN THEY HAVE PROBLEMS
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2006-07-12 | 12:00AM - 2:00P |  | LIFT STATION | RAIN 4"
IN0036846 | BRISTOL MUNICIPAL STP | ELKHART | 2006-02-03 | PM - 7:45P (2/4) | 140000 | STOP FLOW TO RIVER, REDIRECTED TO DIGESTER | SLUG OF LOW PH | SOURCE STILL UNDER INVESTIGATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2006-05-03 | 9:48P - 11:08P | 300 | CSO 23, 8TH & FRANKLIN | AEP RE-ROUTING POWER CAUSED POWER LOSS AT LIFT STATION | UTILITY PLACED ON NOTIFICATION LIST BY AEP
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2006-10-16 | 22:45 - 23:35 | 4770 | CSO 23, 8TH & FRANKLIN | POWER FAILURE AT THE 8TH & FRANKLIN LIFT STATION | AEP RESTORED POWER
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2006-01-30 | 9:45A - 11:00A | 2000 | CSO 002 | PARTIAL SEWER BLOCKAGE, SEWER CREW & VACTOR DISPATCHED
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2006-01-30 | 9:45A - 11:00A | 2000 | CSO 002 | PARTIAL SEWER BLOCKAGE | SEWER CREW & VACTOR DISPATCHED
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2006-07-16 | 6:00P - 9:00A (7/17) | 500 | BROKEN SEWER PIPE NEAR ROCK RUN CREEK | RAIN 6.75" (FOR THE WEEK) HIGH FLOW IN CREEK CAUSING DAMAGE | REPAIRED
IN0023761 | MIDDLEBURY MUNICIPAL STP | ELKHART | 2006-05-02 | MIDNIGHT - 3:30A | 10000 | AEROBIC DIGESTER OVERFLOW | VALVE FOR WASTING LEFT OPEN | STOPPED OVERFLOW UPON ARRIVAL AT PLANT
IN0040363 | MILLERSBURG MUNICIPAL STP | ELKHART | 2006-07-11 | 7/11 - 7/12 | 40000 | 198 E WABASH / OVERFLOW OF LIFT STATION | RAIN 8" | WWTP UNDER CONSTRUCTION
IN0040363 | MILLERSBURG MUNICIPAL STP | ELKHART | 2006-08-30 | 6:00A - 9:00A | 12000 | 198 E WABASH - LIFT STATION OVERFLOW | POWER FAILURE - LIGHTING STRUCK A POWER LINE | PLANT GENERATOR STARTED & LIFT STATION BROUGHT ON LINE
IN0032336 | CONNERSVILLE MUNICIPAL STP | FAYETTE | 2006-07-21 | 7/21 - 7/25 |  | CSO 004 | WATER STREET LIFT STATION & DIALER FAILURE - POWER SURGE | INVESTIGATE POWER SURGE, MONITOR STATIONS AFTER ALL STORMS
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-01-02 | 12:00 - 4:00 | 85000 | INLET | RAIN 2" & SATURATED SOIL
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-01-13 | 10:00 - 3:00 (1/14) | 75000 | INLET | RAIN, SATURATED SOIL
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-02-03 | 8:00 - 1:00 (2/4) | 75000 | INLET | BYPASS DUE TO RAINFALL AND SATURATED SOILS
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-03-06 | 3/6 - 3/8 | 85000 | INLET | RAIN 1.5"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-03-10 | 3/10 - 3/15 | 210000 | INLET | RAIN 3+"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-05-02 | 9:00 - 11:30 | 50000 | INLET | RAIN 1.5"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-05-11 | 5/11 - 5/16 | 55000 | INLET | RAIN & SATURATED SOILS
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-05-18 | 1:30 - 2:00 (5/19) | 45000 | INLET | RAIN 1.5"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-06-02 | 12:30 - 5:00 (6/4) | 75000 | INLET | RAIN 1.5"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-07-26 | 12:00 - 3:00 (7/28) | 50000 | INLET | RAIN 3.5"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-10-17 | 12:00 - 4:30 (10/18) | 50000 | INLET | RAIN 2.5"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-12-01 | 12/1 - 12/3 | 70000 | INLET | RAIN 2"
IN0044776 | PLEASANTVIEW SUBDIVISION | FAYETTE | 2006-12-25 | 4:30P - 12:00 (12/27) | 75000 | INLET | RAIN 2" | BYPASSED MINIMUM TIME POSSIBLE
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-01-27 | 1/27 | 100 | LEAKING SEPTIC TANK | CRACK DOWN SIDE OF TANK, TANK REPLACED
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-03-09 | 3/9 |  | AIR RELIEF STATION | GREASE BUILD UP INSIDE OF SEWER
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-03-11 | 3/11 | 100 | MANHOLE | RAIN 6" | SPREAD LIME
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-06-28 | 6/28 - 6/29 | 150 | CRACKED SEPTIC TANK - 9000 WALNUT ST | CRACK IN SEPTIC TANK 0 POOR INSTALLATION | REMOVED DIRT TO LANDFILL
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-09-23 | 9/23 | 300 | 6605 ST RD 64 LIFT STATION (WET WELL) | RAIN 7.5" CAUSING EQUIPMENT FAILURE | REPLACING DAMAGED COMPONENTS
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-09-24 | 9/24 | 2000 | 6605 ST RD 64 LIFT STATION (WET WELL) | RAIN WASHING MATERIAL INTO PUMPS CAUSING PUMPS TO FAIL | REPLACING DAMAGED COMPONENTS
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-11-16 | 11/16 | 850 | WET WELL | SOUTH PUMP FAILURE (DEBRIS IN PUMP) | SENT PUMP FOR REPAIR
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2006-12-18 | 12/18 | 100 | SEPTIC TANK REPLACEMENT 7133 PEACHTREE | SEPTIC TANK FAILURE - NOT INSTALLED CORRECTLY | REPLACED TANK REMOVED ALL DIRT IN AREA
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-01-17 | 12:29P - 4:29P | 4800 | SSO # 026 MH 30-57 | RAIN, WET WEATHER CAPACITY | ROBERT E LEE LIFT STATION SCHEDULED FOR UPGRADE, LATE 06
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-03-11 | 3/11 | 73840 | SSO 009, 007, 023, 026, 016, 021 (11 MANHOLES) | RAIN 1.44" | BAR SCREEN AT 10TH ST LIFT STATION BEING UPGRADED
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-03-12 | 10:45A - 6:30P | 91500 | SSO 009, 007, 010, 023, 026, 016, 021 (13 MANHOLES) | RAIN 1.12", 10TH ST LS BAR SCREEN PLUGGED | BAR SCREEN AT 10TH ST LIFT STATION BEING UPGRADED
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-03-30 | 9:00A |  | MANHOLE 35-24E | BOWLING BALL DROPPED INTO MANHOLE, PLUGGED 8" SEWER | REPLACED MANHOLE LID & TACK WELDED LID
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-04-01 | 12:11A - 2:11A | 480 | SSO # 009 | RAIN 1.03" | BAR SCREEN PROJECT SHOULD RESOLVE PROBLEM
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-04-02 | 7:55P - 10:55P | 3600 | SSO # 021, MH 35-18 | RAIN 1.21" | LINE TO BE CLEANED
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-04-02 | 6:45P - 8:45P | 720 | SSO # 016, MH 9-47 & 9-48 | RAIN 1.21" | INSPECTING SIPHON FOR CLEANING & FLUSHING LINE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-04-21 | 2:30P - 6:15P | 900 | SSO 011, 021, 016 & 026 | RAIN 0.81" | MAIN INTERCEPTOR TO ROBERT E LEE LIFT STATION TO BE REPLACED
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-07-14 | 7:30P - 3:46A (7/15) | 57480 | TWELVE (12) COLLECTION SYSTEM MANHOLES | RAIN 2.38"
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-07-31 | 7/31 |  | SSO # 006 | STILL UNDER INVESTIGATION - TO FOLLOW UP
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-09-23 | 9:51A - 7:32P | 32520 | 19 COLLECTION SYSTEM MANHOLES | RAIN 6.23" | OPERATING UNDER AN EPA ENFORCEMENT ACTION
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-09-27 | ? - 2:30P |  | MANHOLE 34-21 | 8" MAIN PLUGGED WITH GREASE | PLUGGED CLEARED, AREA WITHIN SEVERAL BLOCKS INSPECTED
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2006-10-08 | ? - 4:00P |  | MINI BASIN # 14, MH # 14-R125C | 8" MAIN STOPPED UP WITH ROOTS | BASIN # 14 TO BE CLEANED & TELEVISED IN 2008 - NOT CHRONIC
IN0043923 | WYMBERLY WOODS UTLS. | FLOYD | 2006-08-09 | 7:15A - 7:30A | 500 | DIGESTER TANK AT THE WWTP | OPERATOR ARRIVED AT PLANT - CONTROL PANEL OPEN & PUMPS OFF | CONTROL PANEL LOCKED, ALARM DIRECTED TO PLANT'S DIALER
IN0043923 | WYMBERLY WOODS UTLS. | FLOYD | 2006-10-11 | 9:30P - 9:00A (10/12) | 3000 | FORREST SPRINGS LIFT STATION | ELECTRICAL PROBLEM AT CONTROL PANEL - BOTH PUMPS FAILED | STORING SPARE REPLACEMENT PARTS
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-02-03 | 2/3 |  | OUTFALL | RAIN 0.8", SOLIDS GATHERED IN CLARIFIER MIXED WITH EFF & DISCHARGED | TO BE DISCUSSED AT BOARD MEETING
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-02-04 | ? - 07:00 | 5000 | OUTFALL | RETURNS CLOGED FLOW IS HIGH, SOLIDS OVER WEIRS | CLEANED RETURN, HOSED AREA - TALKED TO TOWN ENGINEER RE: MODIFICATIONS
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-03-08 | 3/8 - 3/9 | 100000 | PARTIALLY TREATED RELEASE, OUTFALL 001 | RAIN 2" | TO USE DIGESTERS FOR WET WEATHER STORAGE
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-03-11 | 3/11 | 100000 | AIR SHUT OFF TO RETAIN SOLIDS | RAIN >4" | IMPROVEMENTS BEING PLANNED
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-04-14 | 4/14 - 4/15 | 10000 | LIFT STATION BYPASS | RAIN | TALK TO TOWN ENGINEER
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-08-28 | ? - 08:00 | 2000 | LIFT STATION OVERFLOW | RAIN 4.8" (TWO DAYS), # 2 RAW PUMP TRIPPED OUT | CLEANED BAR SCREEN TO REDUCE HEAD ON LIFT STATION
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-09-12 | 11:00A | 5000 | OUTFALL (PARTIALLT TREATED RELEASE) | RAIN >3" (TWO DAYS) | CHECKING SUSPECTED I&I SPOTS
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-10-17 | 10/17 | 50000 | OUTFALL | RAIN 2.6", PLANT HYDRAULICALLY OVERLOADED | UTILITY BOARD MEETING ABOUT I/I
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-11-27 | 06:00 - 06:30 | 6700 | LIFT STATION | # 1 PUMP FLOAT FAILED | REPLACED FLOAT, OBSERVE
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2006-11-30 | 11/30 - 12/1 | 500000 | PLANT OVERLOADED BYPASSING PARTIALLY TREATED EFFLUENT | RAIN 3.1" | WORKING ON I & I REDUCTION
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-01-10 | 1/10 | 243000 | INPLANT BYPASS PUMP | RAIN 1.1"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-01-13 | 1/13 - 1/14 | 1227000 | INPLANT BYPASS PUMP | RAIN 1"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-01-22 | 1/22 - 1/23 | 430000 | INPLANT BYPASS PUMP | RAIN
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-02-02 | 2/2 | 758000 | IN PLANT BYPASS PUMP | RAIN 1.2"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-02-16 | 2/16 | 97000 | INPLANT BYPASS PUMP | RAIN 0.7"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-03-09 | 3/9 - 3/13 | 13025000 | IN PLANT BYPASS PUMP | RAIN 9.3"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-04-02 | 4/2 | 138000 | INPLANT BYPASS PUMP | RAIN
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-05-01 | 5/1 | 388000 | INPLANT BYPASS PUMP | RAIN 1.5"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-05-10 | 5/10 | 131000 | INPLANT BYPASS PUMP | RAIN 1.6"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-05-25 | 5/25 | 465000 | INPLANT BYPASS PUMP | RAIN 1.8"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-06-01 | 6/1 - 6/2 | 454000 | INPLANT BYPASS PUMP | RAIN 1.6"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-06-22 | 6/22 | 79000 | INPLANT BYPASS PUMP | RAIN 2.1" | OPERATING UNDER IDEM AGREED ORDER FOR PLANT EXPANSION
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-07-11 | 7/11 | 83000 | INPLANT BYPASS PUMP | RAIN 1.9"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-07-12 | 7/12 | 72000 | INPLANT BYPASS PUMP | RAIN 0.8"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-08-09 | 8/9 | 302000 | INPLANT BYPASS PUMP | RAIN 2.5" | PLANT EXPANSION PROJECT
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-08-10 | 8/10 | 339000 | INPLANT BYPASS PUMP | RAIN 1" | PLANT EXPANSION PROJECT
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-08-15 | 8/15 | 79000 | INPLANT BYPASS PUMP | RAIN 1.3"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-09-12 | 9/12 - 9/13 | 1985000 | INPLANT BYPASS PUMP | RAIN 4.5"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-09-17 | 9/17 | 66000 | INPLANT BYPASS PUMP | RAIN 0.8"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-09-18 | 9/18 | 123000 | INPLANT BYPASS PUMP | RAIN 1.3"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-09-22 | 9/22 - 9/24 | 4433000 | INPLANT BYPASS PUMP | RAIN 3.1"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-10-16 | 10/16 - 10/17 | 595000 | INPLANT BYPASS PUMP | RAIN 2.3"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-10-19 | 10/19 | 15000 | INPLANT BYPASS PUMP | RAIN 0.6"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-10-27 | 10/27 | 128000 | INPLANT BYPASS PUMP | RAIN 3.1"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-11-10 | 11/10 - 11/11 | 122000 | INPLANT BYPASS PUMP | RAIN 0.7"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-11-15 | 11/15 - 11/16 |  | INPLANT BYPASS PUMP | RAIN 2.6"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-11-30 | 11/30 - 12/1 | 1933000 | INPLANT BYPASS PUMP | RAIN 1.6"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-12-12 | 12/12 | 855000 | INPLANT BYPASS PUMP | RAIN 1.5" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-12-21 | 12/21 - 12/23 | 1610000 | IN PLANT BYPASS PUMP | RAIN 1.6"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-12-25 | 12/25 - 12/26 | 944000 | INPLANT BYPASS PUMP | RAIN 0.9"
IN0022896 | FORT BRANCH MUNICIPAL STP | GIBSON | 2006-12-31 | AM - PM | 343000 | IN PLANT BYPASS PUMP | RAIN 0.7"
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2006-03-09 | 7:00A - 11:30P | 1000000 | PLANT | RAIN | PLAN TO INSTALL NEW PUMP, SLIPLINING PROBLEM AREAS
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2006-03-11 | 3/11 - 3/12 | 1000000 | PLANT | RAIN | SLIP LINNING & GROUTING MANHOLES
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2006-12-12 | 8:15A - 1:30P | 250000 | WASTEWATER PLANT | RAIN 1.8", HEADWORKS PUMP OUT | REPLACING PUMP
IN0038288 | OWENSVILLE MUNICIPAL STP | GIBSON | 2006-03-09 | 3/9 | 100000 | MANHOLES 1ST & WARRICK, HWY 65 S | RAIN 4" | UNDER AGREED ORDER
IN0038288 | OWENSVILLE MUNICIPAL STP | GIBSON | 2006-03-11 | 3/11 - 3/12 | 250000 | MANHOLES WARRICKST, HWY 65, S HILLCREST LS | RAIN 7" | WORKING ON I & I REDUCTION
IN0062286 | FOWLERTON WWTP | GRANT | 2006-02-17 | 2/17 - 2/20 |  | ROTOR BRUSH FAILURE, NO TREATMENT IN OXIDATION DITCH | LOSS OF ROTOR BRUSH IN OXIDATION DITCH
IN0022985 | GAS CITY MUNICIPAL STP | GRANT | 2006-11-17 | 9:00 - 6:00A (11/19) | 1083432 | PLANT | RAIN 1.4", RIVER 8' ABOVE NORMAL | WORKING ON I & I REDUCTION
IN0022985 | GAS CITY MUNICIPAL STP | GRANT | 2006-12-01 | 12:00P |  | PLANT | RAIN 2.4" | WORKING ON I & I REDUCTION
IN0022985 | GAS CITY MUNICIPAL STP | GRANT | 2006-12-01 | 12:00P - 1:00P (12/3) | 2447569 | PLANT | RAIN 2.4" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
| JONESBORO, CITY OF | GRANT | 2006-12-01 | 9:30A - 2:30P |  | MANHOLE C-1, I-11 & I-18 | RAIN 2.4" | CLEAN MANHOLES
IN0025585 | MARION MUNICIPAL STP | GRANT | 2006-04-17 | 2:00A - 9:00A | 10000 | MERDONA BROOKS & STONECREST LIFT STATIONS | POWER FAILURE - LIGHTNING STRIKE
IN0025585 | MARION MUNICIPAL STP | GRANT | 2006-06-23 | 1:54P - 3:25P | 500 | MANHOLE BEHIND 2008 MAPLEWOOD DR | POWER FAILURE TO LIFT STATION & GENERATOR BREAK DOWN | GOT GENERATOR WORKING & PUMPED DOWN WET WELL
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-02-16 | 7:25A - 7:55P | 60 | NORTH LIFT STATION | RAIN 1" | PLAN TO MAKE CORRECTIONS THIS SUMMER
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-02-16 | 10:00P - 11:00P |  | NORTH LIFT STATION | RAIN 0.8" | SUMMER UPDATING OF PLANT
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-04-16 | 11:30P - 2:00A (4/17) | 300 | NORTH LIFT STATION | RAIN 1.8" | WWTP UPDATES FOR SUMMER 06
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-04-17 | 6:30A - 10:00A | 420 | NORTH LIFT STATION | RAIN 2.8" | WWTP UPDATES FOR SUMMER 06
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-04-17 | 6:30A - 12:30P | 720 | WWTP | RAIN 2.8" | WWTP UPDATES FOR SUMMER 06
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-07-12 | 7/12 - 7/13 | 660 | NORTH LIFT STATION | RAIN 3.6" | WWTP UPDATES FOR SUMMER OF 2006
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-08-28 | 8:00A - 8:30A | 60 | WEST LIFT STATION | RAIN 2.3" | UPDATES TO WWTP
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-08-28 | 7:00A - 11:30A | 900 | NORTH LIFT STATION & WWTP | RAIN 2.3" | WWTP UPDATES WILL BE STARTING
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-09-12 | 10:00A - 11:00A | 120 | NORTH LIFT STATION | RAIN 1.3" | WWTP UPDATES STARTING THIS FALL
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-10-05 | 12:00A - 1:30A | 180 | NORTH LIFT STATION | LIGHTNING CAUSED PUMP FAILURE
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-10-17 | 2:30A - 12:30P | 1980 | NORTH LIFT STATION, WWTP | RAIN 2.3" | WWTP UPDATES TO START IN THE FALL
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-11-16 | 6:00A - 2:30P | 1620 | WWTP & NORTH LIFT STATION | RAIN 1.6" | WWTP WPDATES TO START WINTER OF 07
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-12-01 | 12/1 | 2820 | MANHOLE AT PLANT, W LIFT STATION, N LIFT STATION | RAIN 2.8" | UPGRADES TO PLANT PLANNED EARLY 2007
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2006-12-31 | 5:00P - 1:00A (1/1) | 1920 | WWTP & NORTH LIFT STATION | RAIN 1.4" | UPGRADE PLANT
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-01-14 | 4:00P - 7:00P (1/15) | 261000 | PUMP ST | EQUIPMENT FAILURE (PUMP), RAIN 1.2" | AGREED ORDER WITH IDEM
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-01-17 | 09:00 - 11:45 (1/18) | 186000 | PUMP ST | RAIN, 1.2", EQUIPMENT FAILURE (PUMP) | AGREED ORDER WITH IDEM
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-02-16 | 9:00P - 3:15A (2/17) | 25000 | PUMP ST 001 | RAIN 1.3" | IDEM AGREED ORDER I/I REMOVAL
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-04-17 | MIDNIGHT - 9:45A | 74000 | PUMP ST 001 | RAIN 1.2" | OPERATING UNDER IDEM AGREED ORDER - I&I REMOVAL
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-05-17 | 11:15P - 12:15A (5/18) | 5000 | PUMP ST 001 | RAIN 1.2" | AGREED ORDER 2001-10444-W, I/I REMOVAL
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-06-18 | 9:00P - 1:00A | 65000 | PUMP ST 001 | RAIN 2.1" | AGREED ORDER, I&I REMOVAL
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-07-12 | 3:00P - 11:AM (7/13) | 390000 | PUMP ST 001 | RAIN 3.7" | OPERATING UNDER IDEM AGREED ORDER
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-08-26 | 11:00P - 1:15A (8/27) | 43000 | PUMP STATION | RAIN 1.7" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-09-11 | 6:15P - 8:15P | 8000 | LIFT STATION | RAIN 1" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-10-17 | 01:00A - 5:00P | 249000 | LIFT STATION | RAIN 2.7" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-10-27 | 10:30P - 1:00A (10/28) | 74000 | LIFT STATION | RAIN 1.4" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-11-15 | 07:15 - 11:45P | 152000 | LIFT STATION | RAIN 1" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-12-01 | 4:00P - 12:00A (12/2) | 527000 | LIFT STATION | RAIN 2.4" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-12-12 | 8:00P - 11:15P | 8000 | LIFT STATION | RAIN 1.4" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020559 | VAN BUREN MUNICIPAL STP | GRANT | 2006-12-31 | 11:45P - 1:30A (1/1) | 71000 | LIFT STATION | RAIN 1.4" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0020575 | LINTON MUNICIPAL STP | GREENE | 2006-03-13 | 3/13 |  | MANHOLES AT PLANT, 8TH ST | RAIN 4"
IN0020575 | LIZTON MUNICIPAL STP | GREENE | 2006-03-08 | 3/8 - 3/9 |  | MANHOLE AT PLANT | RAIN 4"
IN0030228 | SHAKAMAK STATE PARK | GREENE | 2006-03-08 | 10:30A - 12:30P | 4000 | # 1 LIFT STATION | POWER FAILURE REPORTED TO CINERGY | PROJECT UNDERWAY TO REPLACE MAJORITY OF SEWERS
IN0030228 | SHAKAMAK STATE PARK | GREENE | 2006-03-09 | 3/9 - 3/12 |  | PLANT OVER CAPACITY | RAIN | PROJECT TO REPLACE SEWER LINES TO BE COMPLETE 2006
IN0030228 | SHAKAMAK STATE PARK | GREENE | 2006-03-31 | 09:30 - 11:25 | 5000 | # 1 LIFT STATION | FAILED TO RESTORE POWER AFTER REPAIR TO LIFT STATION | DOUBLE CHECK OPERATION OF EQUIPMENT
IN0030228 | SHAKAMAK STATE PARK | GREENE | 2006-04-03 | 17:00 - 9:50 (4/4) | 4000 | LIFT STATION # 1 | POWER FAILURE, RAIN 0.28" | HAULED SEVERAL LOADS TO MH, OBTAIN GENERATORS
IN0030228 | SHAKAMAK STATE PARK | GREENE | 2006-04-06 | 4/6 | 125000 | HIGH FLOW TO PLANT | RAIN I&I | PROJECT TO REPLACE SEWERS UNDERWAY
IN0022497 | CARMEL MUNICIPAL STP | HAMILTON | 2006-03-12 | 6:00A - 2:00P | 1440 | MANHOLES 136TH & OAK RIDGE | RAIN 1+", LIFT STATION AT CAPACITY | NEW GRAVITY SEWER BEING INSTALLED
IN0022497 | CARMEL MUNICIPAL STP | HAMILTON | 2006-03-22 | 11:45A - 3:30P | 10000 | 96TH ST RANDAL RD LIFT STATION | PRESSURE ON DISCHARGE SIDE OF STATION COULD NOT BE STOPPED | VAC TRUCK PUMPED STATION & DITCH DUMPED AT PLANT
IN0022497 | CARMEL MUNICIPAL STP | HAMILTON | 2006-05-30 | 6:30P - 6:38P | 800 | FORCE MAIN ON 136TH (CORNER OF OAKRIDGE) | CONTRACTOR DIGGING AROUND FORCE MAIN - GROUND COLLAPESED | REPAIRED FORCE MAIN
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2006-04-02 | 4/2 - 4/3 |  | MANHOLE 3-96 | SEWER MAIN BLOCKAGE, CLEANED | TELEVISE LINE
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2006-04-15 | 8:00A - 6:00P |  | MANHOLE MAIN ST LIFT STATION | MAIN BLOCKAGE | PERFORMING MAJOR CLEANING
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2006-12-01 | 7:00A - 10:45P | 1020600 | MANHOLES & LIFT STA - MAIN ST, S PERU, PLANT INFLUENT | RAIN 3.16" | SEWER REHAB & CLEANING
IN0055760 | CLAY TOWNSHIP RWD | HAMILTON | 2006-04-17 | 10:05A - 12:00P |  | FORD DEALERSHIP SI 7 | RAIN 3.4", ONE PUMP FAILURE | LIFT STATION #2 UPGRADE COMPLETE IN 30 DAYS, FLOW TO BE DIVERTED
IN0055760 | CLAY TOWNSHIP RWD | HAMILTON | 2006-06-05 | 6/5 | 100 | MANHOLE # SC-8 | GREASE BLOCKAGE IN MAIN LINE | CLEAN LINE THREE TIMES / YEAR
IN0055760 | CLAY TOWNSHIP RWD | HAMILTON | 2006-06-06 | 12:00 - 10:15A (6/7) | 10 | AIR RELEASE VALVE - 106TH & TOWNE | AIR RELEASE VALVE FAILURE | USED VACTOR TO CLEAN AREA
IN0055760 | CLAY TOWNSHIP RWD | HAMILTON | 2006-08-30 | 2:30P - 3:15P | 150 | CLEAN OUT | GREASE BLOCKAGE IN MAIN LINE | CLEAN & INSPECT MAIN LINE MORE FREQUENTLY
IN0055760 | CLAY TOWNSHIP RWD | HAMILTON | 2006-12-11 | 12/11 | 400 | MANHOLE | BLOCKAGE IN MAIN LINE SEWER | CLEAN LINES WITH VACTOR TRUCK & TELEVISE
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-01-09 | 1:00A - 1:30A | 21000 | MANHOLE WINDING CREEK | POWER FAILURE, BLOWN FUSE | AREA CLEANED, DEBRIS REMOVED
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-03-05 | 2:30P - 3:30P | 72000 | WINDING CREEK LIFT STATION | LIFT STATION POWER FAILURE - BREAKER TRIPPING | STUDY FOR LIFT STATION UPGRADE IS IN PROGRESS
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-03-11 | 12:00P - 12:30P | 30000 | WINDING CREEK LIFT STATION | RAIN, POWER FAILURE | DESIGNING IMPROVEMENTS TO LIFT STATION
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-03-12 | 3:00A - 12:00P |  | WINDING & SMOCK CREEK LIFT STATIONS | RAIN 1.7" | ENGINEERING STUDY FOR LIFT STATION UPGRADE
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-03-15 | 8:00A - 8:30A | 15000 | WINDING CREEK LIFT STATION | SEAL FAILURE ON # 1 PUMP, SPARE PUMP INSTALLED | LIFT STATION UPGRADE
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-07-13 | 6:30A - 8:00A | 7500 | RIVER GLEN LIFT STATION | ELECTRICAL FAILURE AT LIFT STATION | LIFT STATION UNDER EVALUATION
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-09-19 | 9:00A - 9:15A | 30000 | SMOCK LIFT STATION | LIFT STATION OVERFLOW DURING REPAIR OF VACUUM RELEASE VALVE | NEW ISOLATION VALVE REPLACEMENT
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-11-02 | 6:10A - 6:12A | 2000 | MANHOLE U/S OF THE WINDING CREEK LIFT STATION | WASTE WATER SURGE AFTER REMOVING SEWER PLUG FOR TIE IN | TIE IN REDUCED POSSIBLE OVERFLOW AT WINDING CK LIFT STATION
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-12-01 | 7:30A - 11:30A | 12000 | SMOCK LIFT STATION | RAIN | IMPROVEMENTS TO SMOCK CK LS IN DESIGN
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2006-12-31 | 8:05P - 8:10P | 1000 | SMOCK CREEK LIFT STATION | DEBRIS PLUGGING ONE OF THE THREE LIFT STATION PUMPS | LIFT STATION IMPROVEMENTS CURRENTLY BEING DESIGNED
| HAMILTON SOUTHEASTERN UTILITIES | HAMILTON | 2006-06-06 | 4:30P - 9:30P | 17958 | FORCE MAIN AT 104TH & CYNTHEANNE RD | FORCE MAIN DAMAGED BY DIRT MOVING CREW | AREA VACUUMED & FORCE MAIN MARKED
| HAMILTON SOUTHEASTERN UTILITIES | HAMILTON | 2006-07-22 | 10:00A - 12:30P | 8500 | FORCE MAIN - 116TH STREET | VALVE FAILURE | REPLACED VALVE
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-06-27 | 13:15 - 14:45 |  | CSO MANHOLE 220 CHESTNUT | MILLER PIPELINE SET UP BYPASS TO WORK ON SEWER | EXPLAINED PROCEDURES TO MILLER PIPELINE
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-10-17 | 1:45A - 12:15P | 4760000 | BYPASS OVERFLOW 009 (WWTP) | RAIN 2.47" | PLANT EXPANSION UNDERWAY
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-10-27 | 4:00P - 11:46P | 2271000 | BYPASS OVERFLOW 009 (WWTP) | RAIN 1.76" - PARTIALLY TREATED RELEASE | PLANT EXPANSION UNDERWAY
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-11-16 | 07:10 - 13:30 |  | BYPASS OVERFLOW 009 (WWTP) | RAIN 1.35" | PLANT EXPANSION UNDERWAY
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-12-01 | 6:00A - 10:15A |  | LIFT STATION 005, 406 WESTCHESTER BLVD | RAIN 2.28", LIFT STATION PUMPING AT CAPACITY
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-12-01 | 1:20A - 3:50P | 5321000 | BYPASS OVERFLOW 009 (WWTP) | RAIN 2.28" | PLANT EXPANION UNDERWAY
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-12-02 | 12/2 - 12/4 | 18990000 | BYPASS OVERFLOW 009 (WWTP) | RAIN 2.28", FLOODING, RIVER FLOWING INTO COLLECTION SYSTEM | PLANT EXPANION UNDERWAY TO INCREASE CAPACITY
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2006-12-31 | 9:35A - 11:00P | 5756000 | BYPASS OVERFLOW 009 (WWTP) | RAIN 0.75" | PLANT EXPANSION UNDERWAY
IN0059544 | WESTFIELD MUNICIPAL STP | HAMILTON | 2006-05-31 | 3:00P - 6:30P | 180 | FORCE MAIN AIR RELIEF | AIR RELIEF STRUCTURE FAILURE | TO INSTALL NEW VALVE
IN0059544 | WESTFIELD MUNICIPAL STP | HAMILTON | 2006-07-07 | 7/7 - 7/7 | 24809 | PRIVATE SANITARY MANHOLE | POWER SURGE DAMAGE TO FLOAT SYSTEM - SCADA DID NOT NOTIFY | EVALUATE LIFT STATION - CHECK SCADA SYSTEM
IN0059544 | WESTFIELD MUNICIPAL STP | HAMILTON | 2006-10-17 | 00:30 - 13:30 | 41400 | OAK RP LIFT STATION - MANHOLE SURCHARGE NEAR COOL CREEK | RAIN 2.11"
IN0059544 | WESTFIELD MUNICIPAL STP | HAMILTON | 2006-12-01 | 2:00A - 1:40P | 20000 | MANHOLE | RAIN 2.18" | WORKING ON I & I REDUCTION
IN0002925 | ELI LILLY AND CO., GREENFIELD | HANCOCK | 2006-10-17 | 3:00A - 7:00P (10/19) | 58000 | LEAKING SANITARY SEWER LINE TO STORMWATER BASIN | RAIN CAUSED SUPPORT TO WASH AWAY CAUSING PIPE TO PULL APART | PIPE BREACH REPAIRED
IN0060542 | MCCORDSVILLE WWTP | HANCOCK | 2006-03-23 | 3/23 - 3/27 | 1500 | AIR RELEASE VALVE - MANHOLE # 33+90 FORCE MAIN | AIR RELEASE VALVE FAILURE, REPLACED
IN0060542 | MCCORDSVILLE WWTP | HANCOCK | 2006-04-15 | 3:00A - 10:00A | 30000 | WWTP | RAIN 1.6", PLUG BLEW OUT ON LINE UNDER CONSTRUCTION | CONTRACTOR REPAIRED AND REPLACED PLUG
IN0059013 | WESTERN HANCOCK UTILITIES | HANCOCK | 2006-08-07 | 8/7 - 8/09 |  | WWTP | WWTP LOST TERATMENT ABILITY - POSSIBLE POWER FAILURE | STILL WORKING TO RESTORE TREATMENT
IN0020893 | CORYDON MUNICIPAL STP | HARRISON | 2006-07-06 | 2 TO 3 MINUTES | 300 | DIGESTED SLUDGE SPILLED TO ASPHALT PARKING LOT | 4" LINE FEEDING SLUDGE PRESS RUPTURED | AREA CLEANED, SPILLED SLUDGE RETURNED TO DIGESTER
IN0040215 | LANESVILLE MUNICIPAL STP | HARRISON | 2006-09-23 | 5:00A - 10:00A |  | MANHOLE @ LIFT STATION | RAIN 9", PUMPS CAN'T KEEP UP
IN0020460 | MILLTOWN MUNICIPAL STP | HARRISON | 2006-02-06 | ? - 9:00A | 30000 | LIFT STATION # 1 | START FLOAT FELL OFF, REPAIRED | MADE FLOAT STRONGER SO IT WILL STAY ON
IN0020460 | MILLTOWN MUNICIPAL STP | HARRISON | 2006-03-20 | ? - 3/20 | 30000 | LS # 1 | BREAKER KICKED OFF, AREA CLEANED
IN0020460 | MILLTOWN MUNICIPAL STP | HARRISON | 2006-05-18 | 5:30P |  | EFFLUENT (BYPASS OF TREATMENT PROCESS) | EQUIPMENT FAILURE | MAKING REPAIRS TO COMPONENTS
IN0020460 | MILLTOWN MUNICIPAL STP | HARRISON | 2006-09-17 | 9/17 | 3000 | LIFT STATION 3 | EQUIPMENT FAILURE
IN0020460 | MILLTOWN MUNICIPAL STP | HARRISON | 2006-09-18 | 9/18 | 6000 | LIFT STATION 3 | EQUIPMENT FAILURE - PUMP | HAD PUMPER TRUCK PUMP LIFT STATION TO REPLACE PUMP
IN0020460 | MILLTOWN MUNICIPAL STP | HARRISON | 2006-09-19 | 9/19 | 1000 | LIFT STATION 3 | EQUIPMENT FAILURE - PUMP | REPLACED DAMAGED PUMP
IN0020460 | MILLTOWN MUNICIPAL STP | HARRISON | 2006-10-04 | ? - 8:00a | 1000 | LIFT STATION 3 | EQUIPMENT FAILURE - RUBBER GLOVES IN PUMP | REPLACED DAMAGED PUMP, PUMPING DOWN LIFT STATION
IN0042005 | SSK COMPANY COMMUNITIES | HARRISON | 2006-04-19 | 3:00A - 9:00A | 20000 | WASTEWATER TREATMENT PLANT (WWTP) | STORM, ELECTRIC COMPANY TRANSFORMER HIT BY LIGHTNING | REPAIRING PLANT
IN0042005 | SSK COMPANY COMMUNITIES | HARRISON | 2006-08-21 | ? - 12:00 | 500 | LIFT STATION OVERFLOW | LIFT STATION FAILURE | REPAIRS UNDERWAY
IN0042005 | SSK COMPANY COMMUNITIES | HARRISON | 2006-09-23 | 9/23 |  | TREATMENT PLANT | RAIN 7" | UNDER AGREEMENT TO INSTALL SURGE TANK, BUT BEHIND SCHEDULE
IN0043877 | AMO-COATSVILLE MUNICIPAL STP | HENDRICKS | 2006-03-10 | 3/10 | 60000 | OXIDATION DITCH OVERFLOED | RAIN 3.5"
IN0049581 | BELLEVILLE CONSERVANCY DISTRIC | HENDRICKS | 2006-04-03 | 8:00A - 9:30A |  | CO RD 121 LIFT STATION | EQUIPMENT FAILURE, PUMPS TRIPPED
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2006-01-19 | 12:00P - 1:18P | 693184 | CSO OUTFALL 002, DRY WEATHER OVERFLOW | ELECTRICAL FAILURE OF AUTOMATIC INFLUENT GATE | ELECTRIC COMPANY INVESTIGATING PUMP CONTROLS & PLC PROGRAM
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2006-06-19 | 1:36P - 3:42P | 204346 | CSO 002 & 003 | POWER FAILURE FEEDING MAIN PUMPING STATION | LTCP HAS A TANK INCLUDED TO MINIMIZE IMPACT
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2006-08-16 | 10:15P - 12:15A (8/17) | 200 | BASEMENT BACKUP - 1321 ODELL STREET | ROOTS IN SEWER CAUSING OBSTRUCTION | PREVENTATIVE MAINTENANCE AND CLEANING OF SEWERS
IN0057614 | HENDRICKS COUNTY RSD | HENDRICKS | 2006-03-10 | 8:00A - 12:00P | 1000 | LINDEN SQUARE LIFT STATION & MANHOLES AT WWTP | FLOODING, PUMPS PLUGGED WITH DEBRIS | CHECKING WAYS TO KEEP PUMP FROM PLUGGING
IN0057614 | HENDRICKS COUNTY RSD | HENDRICKS | 2006-03-26 | 2:00P - 6:00P |  | WYNBROOKS LIFT STATION | BOTH PUMPS FAILED, BEARINGS & BLOWN MOTOR
IN0057614 | HENDRICKS COUNTY RSD | HENDRICKS | 2006-07-16 | 5:30P - 7:30P | 1000 | WYNBROOKE LIFT STATION ( 21ST & RACEWAY RD) | BOTH LIFT STATION PUMPS FAILED | AREA CLEANED
IN0057614 | HENDRICKS COUNTY RSD | HENDRICKS | 2006-07-20 | 10:00P - 11:00P | 500 | WYNBROOKE LIFT STATION ( 21ST & RACEWAY RD) | LIFT STATION PUMP FAILED (ONE OUT FOR REPAIRS) | STAND-BY PUMP USED FOR PUMP-AROUND, AREA CLEANED
IN0040436 | NORTH SALEM MUNICIPAL STP | HENDRICKS | 2006-04-15 | 3:00A - 5:00P | 50000 | 1ST MANHOLE WEST OF LIFT STATION | POWER FAILURE (LINES DOWN), RAIN
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2006-11-10 | ? - 3:45 |  | 224 BRIXTON WOODS DRIVE WEST | BROKEN FORCE MAIN - WASTE TRUCKED TO WWTP DURING REPAIR | LIFT STATION CHECKED DAILY (MONDAY - FRIDAY)
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-01-13 | 7:15A - 12:45P | 250000 | PLANT CSO # 6 | RAIN 0.8"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-01-17 | 7:00A - 11:45A |  | PLANT CSO # 6 | RAIN 0.5"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-02-02 | 2:00P - 12:00A (2/3) |  | PLANT CSO | RAIN 1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-02-16 | 8:00P - 11:30P |  | PLANT CSO # 6 | RAIN 0.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-03-08 | 10:38 - 11:00 |  | PLANT CSO # 6 | RAIN 1.1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-03-09 | 3/9 - 3/10 |  | PLANT CSO # 6 | RAIN
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-03-11 | 3/11 - 3/13 |  | PLANT CSO # 6 | RAIN 2.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-03-31 | 8:45A - 7:10A (4/1) |  | PLANT CSO # 6 | RAIN 1.9"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-01 | 1:30P - 3:15P |  | PLANT CSO # 6 | RAIN 1.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-02 | 1:20P - 1:45P |  | PLANT CSO # 6 | RAIN 0.1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-02 | 11:00P - 12:00A (4/3) |  | PLANT CSO # 6 | RAIN 0.2"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-03 | ? - 3:30P |  | BRIDGE CREEK LIFT STATION | POSSIBLE POWER SURGE AT STATION | MONITOR MOER FREQUENTLY DURING SEVERE WEATHER
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-14 | 11:29P - 12:15A (4/15) |  | CLARKS CREEK RD LIFT STATION | POWER FAILURE | POWER COMPANY RESTORED POWER TO STATION
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-14 | 11:00P - 3:00A (4/15) |  | PLANT CSO # 6 | RAIN 0.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-14 | 4:00A - 8:00A |  | PLANT CSO # 6 | RAIN 1.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-15 | 12:00A - 12:25A |  | BRIDGE CREEK LIFT STATION | POWER FAILURE | UPSTREAM LIFT STATION SHUT DOWN TO MINIMIZE OVERFLOW
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-16 | 10:30P - 11:00P |  | CSO # 6 | RAIN 0.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-17 | 5:30A - 1:15P |  | CSO # 6 | RAIN 0.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-04-18 | 8:50A - 9:50A |  | MANHOLE TO STORM DRAIN | GREASE BLOCKAGE FROM HADLEY RD & CAMBRIDGE DRIVE | CLEARED SEWER LINE, CLEANED UP DEBRIS
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-05-02 | 2:00A - 3:00A |  | PLANT CSO # 6 | RAIN 0.7"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-05-03 | 8:15A - 9:45A | 45 | CLEANOUT 231 ANDREWS BLVD EAST DR | DEBRIS IN SEWER, OVERFLOW FROM CLEANOUT | CLEANED MAIN SEWER LINES, CLEANED UP DEBRIS
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-05-10 | 8:00P - 9:30P |  | PLANT CSO # 6 | RAIN 1.7"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-05-10 | 10:25P - 11:45P |  | PLANT CSO # 6 | RAIN 1.7"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-05-11 | 4:00A - 5:00A |  | PLANT CSO # 6 | RAIN 1.7"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-06-02 | 5:50A - 7:30A |  | CSO # 6 | RAIN 1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-06-07 | 9:45A - 10:20A |  | PLANT CSO # 6 | RAIN 0.5"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-06-18 | 9:30P - 11:00P |  | PLANT CSO # 6 | RAIN 0.7"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-06-19 | 3:00P - 4:00P |  | PLANT CSO # 6 | RAIN 0.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-06-25 | 3:59P - 5:30P |  | PLANT CSO # 6 | RAIN 0.3"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-07-11 | 8:30A - 4:45P |  | PLANT CSO # 6 | RAIN 2.4"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-07-21 | 10:50P - 1:50A (7/22) |  | CSO # 6 | RAIN 0.8"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-08-03 | 9:00A - 9:30A | 150 | MANHOLE AT FRENCH ST & CARR RD | SEWER BLOCKAGE (GRAVEL) | CLEANED 600 FT OF SEWER LINE
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-08-11 | 9:15A - 1:15P |  | PLANT CSO # 6 | RAIN 0.8"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-08-14 | 5:45P - 7:15P |  | CSO # 6 | RAIN 0.7"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-08-15 | 10:30A - 11:00A | 200 | WESTMERE LIFT STATION FORCE MAIN | FORCE MAIN DAMAGED BY DIRECTIONAL BORING CONTRACTOR | VACTORED UP SEWAGE & PLACED LIME ON GROUND
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-08-27 | 1:00A - 1:45A |  | CSO # 6 | RAIN 1.2"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-09-12 | 9/12 - 9/13 |  | PLANT CSO # 6 | RAIN 2.6"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-09-22 | 8:45A - 9:45P |  | PLANT CSO # 6 | RAIN 0.9"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-10-03 | 6:40A - 8:45A |  | PLANT CSO # 6 | RAIN 1.1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-10-27 | 10:15A - 12:30A (10/28) |  | PLANT CSO # 6 | RAIN 2.2"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-11-16 | 5:15A - 9:00P |  | PLANT CSO # 6 | RAIN 1.8"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-11-27 | 2:00P - 4:00P | 240 | TWO MANHOLES, LAKESIDE APT LAKE (PRIVATELY OWNED) | LIFT STATION & SEWER MAIN CLOGGED WITH GREASE | PLAINFIELD DPW CLEANED LS & UNCLOGGED SEWER
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-11-30 | 6:30P - 10:00P (12/1) |  | PLANT CSO # 6 | RAIN 1.2"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-11-30 | 9:30A - 1:45P |  | PLANT CSO # 6 | RAIN 1.1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-12-05 | 8:00A - 4:30P | 510 | GREASE TRAP AT CRACKER BARRELL RESTAURANT | SEWER BLOCKAGE - GREASE FROM AREA REATAURANTS | DPW WILL CLEAN SEWERS IN AREA MORE OFTEN (PREVENTIVE)
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-12-12 | 8:45A - 10:10A |  | PLANT CSO | RAIN 1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-12-21 | 12/21 |  | PLANT CSO # 6 | RAIN 1.5"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-12-22 | 5:15A - 6:30P |  | PLANT CSO # 6 | RAIN 1.7"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-12-25 | 12/25 - 12/26 |  | PLANT CSO # 6 | RAIN 1"
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2006-12-31 | 6:30A - 11:00P |  | CSO # 6 | RAIN 1"
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2006-03-17 | 10:00A - 11:00A | 10000 | FORCE MAIN | FORCE MAIN HIT BY BORING CONTRACTOR | SUCKED UP DEBRIS, FLUSHED AREA
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2006-08-27 | 4:00A - 12:30P | 35000 | MANHOLE UPSTREAM FROM WHITE LICK LIFT STATION | RAIN 0.9", LIFT STATION PANEL FAILURE | RENOVATE CONTROL PANEL, TAKING BIDS FOR BYPASS PUMP
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2006-08-27 | 4:00A - 12:30P | 35000 | MANHOLE UPSTREAM FROM WHITE LICK LIFT STATION | LIFT STATION PANEL FAILURE | INVESTIGATING RENOVATION OF LIFT STATION PANEL
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2006-09-09 | 6:15A - 6:45A | 500 | MANHOLE IN CRYSTAL SPRINGS SUBDIVISION | CRYSTAL SPRINGS LIFT STATION MALFUNCTION - INTERNAL POWER | CHECKING ALARMS ON ALL 40 LIFT STATIONS
IN0041181 | GOLDEN PEBBLE ESTATES M.H.P. | HENRY | 2006-03-13 | 3/13 | 100000 | SLUDGE PIT TO LAGOON, BYPASS TREATMENT | RAIN 3" | INSTALLING LARGER PUMPS
IN0041181 | GOLDEN PEBBLE ESTATES M.H.P. | HENRY | 2006-04-17 | 8:48A - 11:45A | 35000 | SLUDGE PIT TO LAGOON | RAIN 2", PUMP FAILURE | LOOKING FOR INFLOW SOURCES - INSTALLING LARGER PIT & PUMPS
IN0041181 | GOLDEN PEBBLE ESTATES M.H.P. | HENRY | 2006-05-13 | 12:45P - 11:00A (5/14) | 65000 | SLUDGE PIT | RAIN 3", SLUDGE PUMP FAILURE | BUILDING LARGER SLUDGE PIT WITH LARGER PUMPS
IN0041181 | GOLDEN PEBBLE ESTATES M.H.P. | HENRY | 2006-12-01 | 10:35A - 2:40P | 50000 | SLUDGE PIT TO LAGOON | RAIN 3.5", POWER FAILURE | USING GENERATOR TO POWER PUMPS
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-02-17 | 00:30 - 08:00 |  | CSO 3 NORTH (GARNER ST) | RAIN 0.44"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-09 | 3/9 - 3/10 | 8600000 | CSO 2 GARNER ST & CSO 3 BOWREY BROOK | RAIN 0.55"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-09 | 3/9 |  | CSO 3 NORTH | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-10 | 3/10 | 2800000 | CSO 2 GARNER ST & CSO 3 BOWREY BROOK | RAIN 1.15"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-11 | 12:00 - 16:00 | 247067 | CSO 3 BOUREY BROOK 7 CSO 2 GARNER ST | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-12 | 3/12 | 61200000 | CSO 3 GARNER STREET & CSO 3 BOUREY BROOK | RAIN 1.48"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-13 | 3/13 |  | CSO 2 & CSO3 | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-31 | 20:30 - 23:59 | 2400000 | CSO 3 BOWREY BROOK | RAIN 0.54"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-03-31 | 3/31 | 610000 | CSO 2 GARNER ST | RAIN 0.54"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-04-07 | 03:00 - 11:00 | 205586 | CSO 3 BOWREY BROOK | RAIN 0.6"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-04-07 | 03:00 - 11:00 | 4450 | CSO 2 GARNER ST | RAIN 0.6"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-04-14 | 05:00 - NOON (4/17) |  | CSO 3 BOWREY BROOK | RAIN 1.8"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-04-14 | 05:00 - NOON (4/17) |  | CSO 2 GARNER ST | RAIN 1.8"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-05-02 | 06:00 - 12:00 | 100000 | CSO 2 - GARNER ST | RAIN 0.62"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-05-02 | 07:00 - 13:00 | 1300000 | CSO 3 - BOWREY BROOK | RAIN 0.62"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-05-10 | 20:00 - 23:00 (5/14) | 1400000 | CSO 2 GARNER ST | RAIN 3.17"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-05-10 | 20:30 - 22:30 (5/14) | 7090000 | CSO 3 BOWREY BROOK | RAIN 3.17"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-05-17 | 21:00 - 23:00 (5/18) | 4450000 | CSO 3 BOWREY BROOK | RAIN 0.46"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-05-17 | 20:00 - 23:45 (5/18) | 280000 | CSO 2 FARNER ST | RAIN 0.46"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-05-25 | 16:00 - 23:50 | 210000 | CSO 2 - GARNER ST | RAIN 0.25"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-02 | 04:00 - 16:00 | 420000 | CSO 2 - GARNER ST | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-02 | 04:00 - 16:00 | 5520000 | CSO 3 - BOWREY BROOK | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-10 | 08:00 - 23:59 | 560000 | CSO 2 - GARNER ST | RAIN 0.23"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-10 | 08:00 - 23:59 | 5610000 | CSO 3 - BOWREY BROOK | RAIN 0.23"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-22 | 20:00 - 23:50 | 690000 | CSO 2 - GARNER ST | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-22 | 20:00 - 23:50 | 3630000 | CSO 3 - BOWREY BROOK | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-28 | 20:30 - 22:00 | 1280000 | CSO 3 - BOWREY BROOK | RAIN 0.03"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-06-28 | 20:00 - 22:00 | 270000 | CSO 2 - GARNER ST | RAIN 0.03"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-07-11 | 11:00 - 13:30 | 1280000 | CSO 3 - BOWREY BROOK | RAIN 0.54"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-07-11 | 10:30 - 13:30 | 90000 | CSO 2 - GARNER ST | RAIN 0.54"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-07-21 | 22:30 - 04:00 (7/22) | 5680000 | CSO 3 BOWREY BROOK | RAIN 1.81"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-07-21 | 22:00 - 04:00 (7/22) | 692000 | CSO 2 GARNER ST | RAIN 1.81"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-08-10 | 13:00 - 17:00 | 1100000 | CSO 2 GARNER ST | RAIN 1"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-08-10 | 13:00 - 17:00 | 540000 | CSO 3 BOWREY BROOK | RAIN 1"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-09-27 | 22:00 - 22:30 | 1690000 | CSO 2 GARNER ST | RAIN 0.43"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-09-27 | 20:00 - 22:30 | 700000 | CSO 3 BOWREY BROOK | RAIN 0.43"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-10-17 | 09:00 - 13:00 | 110000 | CSO 3 BOWREY BROOK | RAIN 2.26"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-10-17 | 09:40 - 14:00 | 1740000 | CSO 2 GARNER ST | RAIN 2.26"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-10-27 | 23:59 | 9240000 | CSO 3 BOWREY BROOK | RAIN 0.25"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-10-28 | 08:00 - 16:00 | 4360000 | CSO 2 GARNER ST | RAIN 0.25"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-11-16 | 09:00 - 12:00 | 250000 | CSO 3 BOWREY BROOK | RAIN 0.62"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-11-16 | 08:00 - 12:00 | 10000 | CSO 2 GARNER ST | RAIN 0.62"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-11-30 | 21:00 - 23:59 | 13990999 | CSO 3 BOWREY BROOK | RAIN 0.04"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-11-30 | 20:00 - 23:59 | 860000 | CSO 2 GARNER ST | RAIN 0.04"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-12-01 | 00:00 - 09:00 | 696000 | CSO 2 GARNER ST | RAIN 2.5"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2006-12-01 | 00:00 - 08:00 | 10970000 | CSO 3 BOWREY BROOK | RAIN 2.5"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-03-03 | 1:00P - 2:00P | 4000 | STORM DRAIN | WASTING VALVE PARTIALLY STUCK OPEN | LUBED VALVE, PUMPED BACK TO HEADWORKS
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-04-14 | 11:45P - 4:25A (4/15) | 160000 | OUTFALL #002 | RAIN 0.7" | TOWN IS MAKING REPAIRS TO COLLECTION SYSTEM & WWTP UPGRADE
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-04-16 | 4/16 - 4/17 | 1000000 | OUTFALL 002 | LIGHTNING STRIKE DESTROYED ELECTRICAL COMPONENTS | GETTING ESTIMATES FOR PROTECTION FROM ELECTRICAL SURGES
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-06-10 | 9:40A - 2:10P | 35000 | SSO # 002 | RAIN 1.75" | WORKING TO REPAIR COLLECTION SYSTEM & REDESIGN PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-08-10 | 1:40P - 3:05P | 9000 | SSO # 002 | POWER FAILURE KICKED OFF DRIVE UNIT FOR RAW SEWAGE PUMP 2 | REPROGRAMED DRIVE UNIT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-08-28 | 8:00A - 9:35A | 10000 | SSO # 002 | RAIN 1.5", RAW SEWAGE PUMPS CAN'T TAKE IN WATER THAT FAST | PLANNING REHAB OF COLLECTION SYS & RECONSTRUCTION OF WWTP
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-10-17 | 4:00A - 12:30P | 11000 | SSO # 002 | RAIN 2", RAW SEWAGE PUMPS COULDN'T KEEP UP WITH FLOW | PLANNING SOME RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-10-27 | 8:20P - 12:25A (10/28) | 160000 | SSO # 002 | RAIN 0.9" - RAW SEWAGE PUMPS COULD NOT KEEP UP WITH FLOW | PLANNED CONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-11-16 | 10:05A - 7:05P | 200000 | SSO # 002 | RAIN 1.3" | PLANNING RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-12-01 | 1:42A - 7:40P | 1000000 | SSO # 002 | RAIN 2.2" | PLANNING RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2006-12-26 | 4:55A - 9:50A | 300000 | SSO 002 | RAIN 0.91" | PLANNED RECONSTRUCTION OF PLANT
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-01-13 | 8:10A - 8:31A |  | SSR 127 | RAIN 0.75" | WWTP RUNNING AT NECESSARY FLOW
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-02-03 | 1:56P - 2:15P | 100 | MANHOLE OVERFLOW 1613 CADILAC DR | SANITARY SEWER BLOCKAGE, JET RODDER CREW DISPATCHED | SEWER UNPLUGGED, AREA CLEANED
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-03-09 | 10:15A - 3:30P |  | CSO 049 | STORM SEWER UNDER SANITARY SEWER COLLAPSED
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-04-16 | 11:00P - 3:00P (4/17) |  | MANHOLE AT THE VIADUCT ON MARKLAND AVE | RAIN 1.63" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-04-17 | 10:39 - 08:08 (4/18) |  | SSO # 151 - 1308 MAPLEWOOD DRIVE | RAIN | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-04-21 | 11:00A - 1:00P |  | MANHOLE AT 1756 FOX HAVEN DR | SEWER BLOCKAGE IN NEW HOUSING DEVELOPMENT | UNPLUG SEWER, TELEVISE LINE
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-05-12 | 10:44 - 12:01 |  | SSO # 139 - CARTER ST LIFT STATION | RAIN 0.36", GREASE CAUSED DIVERSION OF FLOW OVER WEIR | SEWER CREW REMOVED GREASE
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-05-15 | 12:07P - 2:45P |  | CHLORINE & SULFUR DIOXIDE OFF TO REPAIR WATER LEAK | WATER FOR CHLORINE & SULFUR DIOXIDE SYS DEVELOPED SEVERE LEAK | BACKHOE TO DIG UP LINES & MAKE REPAIR
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-05-25 | 5:02P - 6:10P |  | OUTFALL 028 | POWER FAILURE - STORM - PLANT POWER FEED - AERATION | TERTIARY PUMPS DOWN - STILL PROCESSING FLOW THROUGH WWTP
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-06-05 | 8:26A - 12:00P |  | CSO # 013 | WATER MAIN BROKE , HIGH VOLUME OF WATER (MIAMI & UNION ST) | TESTED & DETECTED NO CHLORINE
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-08-24 | 11:00A - 6:00P |  | FOXFIRE LIFT STATION FORCE MAIN | FORCE MAIN FROM LIFT STATION FAILED (TWO HOLES) | EMERGENCY EXCAVATED FORCE MAIN AND REPAIRED
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-10-17 | 8:30A - 7:33A (10/19) |  | MANHOLE # 672 D 018 | RAIN 1.9" - SEWER RUNNING AT FULL CAPACITY | CONST OF HIGHLAND PK LIFT STATION TO INCREASE CAPACITY
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-10-27 | 10:35A - 10:57A |  | # 617 B 025 | BLOCKAGE IN SANITARY SEWER | INVESTIGATION TO DETERMINE POSSIBLE SEWER REPLACEMENT
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-11-16 | 10:22A - 2:24P |  | SSO # 139 @ CARTER ST LIFT STATION | RAIN >1" | PROJECT OUT FOR BID TO ELIMINATE SSO # 139
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-11-17 | 8:44A - 1:03P |  | SANITARY SEWER OVERFLOW # 151 - MAPLEWOOD DR | RAIN 1.63" | CONST OF NEW HIGHLAND PARK LS & ASSOCIATED SEWER WORK
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-11-22 | 7:44A - 8:25A |  | OHIO ST BRIDGE (SIPHON) - CSO 046 | RESTRICTION IN CSO SIPHON | SIPHONS PUT ON QUARTERLY CLEANING SCHEDULE
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-12-01 | 8:33A - 3:52P |  | SANITARY SEWER OVERFLOW 139, 151 | RAIN 2.38" | LTCP TO REMOVE ALL SSO
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-12-01 | 12/1 & 12/2 - 12/3 |  | SSR # 151 & 139 | RAIN 2.38" | PROJECTS UNDERWAY TO MAKE AREA IMPROVEMENTS
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-12-01 | 4:30A - 10:30A |  | MANHOLE # 617 C 015 MARKLAND AVE W OF BERKLEY RD | RAIN 2.38" | WORK WITH ENGINEER TO CORRECT OVERFLOWS
IN0032875 | KOKOMO MUNICIPAL STP | HOWARD | 2006-12-02 | 11:21A - |  | SANITARY SEWER OVERFLOW # 139 | RAIN 2.38" | WWTP RUNNING AT NECESSARY FLOW VOLUME
IN0038784 | WOODLAND ESTATES MHP | HOWARD | 2006-04-17 | 4/17 - 4/19 | 1000 | EQ BASIN SEEPING OVER BANKS | RAIN 3" | COLLECTION SYSTEM BEING REPLACED
IN0038784 | WOODLAND ESTATES MHP | HOWARD | 2006-10-18 | 10:30A - 3:00P | 2000 | EQUALIZATION BASIN | RAIN 2.5" - EQ BASIN FULL, OVERFLOW OF BANK | REPLACING VITRIFIED CLAY COLLECTION SYSTEM
IN0038784 | WOODLAND ESTATES MHP | HOWARD | 2006-11-16 | 8:55A - 12:30P | 1000 | EQUALIZATION BASIN OVERFLOW | RAIN 2" | PLAN TO REPLACE COLLECTION SYSTEM
IN0052949 | JACKSON CO REGIONAL SEWAGE DIS | JACKSON | 2006-03-14 | 10:00 - 12:30 | 30000 | LIFT STATION | PUMP & ELECTRICAL FAILURE
IN0052949 | JACKSON CO REGIONAL SEWAGE DIS | JACKSON | 2006-12-04 | 8:30 - 12:15A (12/5) | 2000 | LIFT STATION | EQUIPMENT FAILURE - BROKEN PIPE | REPLACING PIPE INSIDE OF STATION
| JLM PHARMATECH | JACKSON | 2006-05-31 | 12:00P - 12:30P | 20 | MH OVERFLOW # H04-W009, 222 KILLION AVE INDUSTRIAL PARK | BUMPED SWITCH WHILE CLEANING LIFT STATION | BE CAREFULL AROUND L/S PANELS
IN0023744 | MEDORA MUNICIPAL STP | JACKSON | 2006-01-07 | NOON - NOON (1/9) | 500 | LATERAL UNDER MOBILE HOME | BLOCKAGE IN MAIN SEWER LINE, FOOD GREASE FROM GAS STATION | TALKED TO MANAGER RE: PROPER GREASE DISPOSAL
IN0023744 | MEDORA MUNICIPAL STP | JACKSON | 2006-03-11 | 3/11 - 3/15 | 10000 | MANHOLE RILEY & MILL ST, SCOTT & MILL ST | RAIN 8.5" | PLANNING STUDY FOR REPAIR OF SEWER SYSTEM
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-01-03 | 13:30 - 13:35 | 20 | 1280 COLONIAL DR | VAC-CON CREW CLEANING SEWER LINE, DEBRIS TANK OVERFLOW
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-01-06 | 18:00 - 19:00 | 15 | 616 NOBLE ST LATERAL OVERFLOW | CLOGGED HOME LATERAL, CLEANOUT OVERFLOW | INFORMED HOMEOWNER TO CALL PLUMBER, COPIED HEALTH DEPT
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-01-19 | 19:45 - 19:46 | 50 | MH F 10-W012 1025 S. PARK | EMERGENCY BYPASS PUMP HOSE FLOPPED OUT OF MANHOLE | PLACE WEIGHT ON HOSE
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-01-20 | 9:00 - 9:20 | 10 | F06-W033 4TH & O'BRIAN | MANHOLE OVERFLOWING DUE TO BLOCKAGE IN SEWER LINE | JETTED LINE REMOVED BLOCKAGE
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-04-04 | 10:30A - 11:45A | 50 | MANHOLE F10-W002 116 HARRISON DR | BLOCKAGE IN 8" SEWER LINE | TO FOLLOW UP WITH SEWER INSPECTION
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-04-05 | 9:30P - 10:15P | 55 | MANHOLE E06-W047 700 E INDIANAPOLIS | BLOCKAGE IN SEWER LINE | TO FOLLOW UP WITH SEWER INSPECTION
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-04-09 | 1:28P - 2:00P | 100 | M/H F08-W0008 311 E LAUREL ST | SEWER BLOCKAGE, CLEARED AREA VACUUMED UP WITH VAC-CON | TO TV LINE TO DETERMINE ADDITIONAL NEEDS
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-09-06 | 9:30A - 10:00A | 40 | PARK & REC LIFT STATION # 22 FREEMAN FIELD | EQUIPMENT FAILURE - BROKEN SEWER AT LIFT STATION | MAKING REPAIRS
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-10-30 | 8:00A - 9:30A | 60 | MANHOLE L05W007 | POWER FAILURE, TRANSFORMER FAILURE | DUKE REPLACED TRANSFORMER
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2006-12-27 | 9:00A - 10:15A | 20 | HWY 50 MANHOLE # F07-W030 | SEWER BLOCKAGE | SEND TV VAN TO CHECK LINE
IN0058521 | VECTREN (HYDROSTATIC TESTING) | JACKSON | 2006-08-30 | 2:00P | 2000 | WATER DISCHARGE NEAR SR 11 & WHITE RIVER (SEYMOUR) | FILTERING DEVICE DID NOT REDUCE TSS (150 MG/L) | REDUCE DISCHARGE RATE TO EFFECT BETTER FILTERING
IN0031275 | KANKAKEE REST AREA I-65 | JASPER | 2006-02-20 | 2/20 - 2/22 | 2000 | BYPASS OF POLISHING PONDS | HIGH AMMONIA CONCENTRATIONS IN POLISHING PONDS
IN0024414 | RENSSELAER MUNICIPAL STP | JASPER | 2006-03-26 | 16:00 - 13:00 | 414000 | 0021 CSO | ROCK COLLECTED DEBRIS AND BACKED UP SEWER LINE
IN0039101 | WATER SERVICE CO OF INDIANA | JASPER | 2006-04-10 | ? - 10:30A (4/10) |  | MH # 13 11988 PORT AV PRINCE | SEWER PLUGGED, CLEANED | SEWER MAINS BEING CLEANED
IN0020095 | PORTLAND MUNICIPAL STP | JAY | 2006-07-17 | 2:45 |  | CSO 11 | BROKEN WATER MAIN DISCHARGING TO STORM SEWER
IN0020095 | PORTLAND MUNICIPAL STP | JAY | 2006-09-06 | 2:30P |  | NORTH CSO 4 | RIVER BANK WASHED AWAY AND SEWER LINE FELL IN | CREW ON SITE TO REPAIR SEWER
IN0020702 | HANOVER MUNICIPAL STP | JEFFERSON | 2006-03-11 | 3/11 - 3/12 |  | MANHOLE 3-1A, 3-84 | RAIN 7"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-01-02 | 5:00P - 10:00P | 200000 | SECONDARY BYPASS STRUCTURE | RAIN 0.7" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-01-11 | 3:00A - 4:30A | 20000 | SECONDARY BYPASS STRUCTURE | RAIN 0.72" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-01-13 | 7:30P - 8:15P |  | SECONDARY BYPASS STRUCTURE | RAIN 0.6" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-01-13 | 11:30A - 2:30P | 30000 | SECONDARY BYPASS STRUCTURE | RAIN 0.6" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-01-14 | 12:00P - 4:00P | 20000 | SECONDARY BYPASS STRUCTURE | RAIN 0.15" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-01-17 | 8:15A - 8:15P | 380000 | SECONDARY BYPASS STRUCTURE | RAIN 0.8" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-01-23 | 1:00A - 3:00P | 210000 | SECONDARY BYPASS STRUCTURE | RAIN 0.27" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-02-04 | 7:00A - 7:00P | 50000 | SECONDARY BYPASS STRUCTURE | RAIN 0.52" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-03-09 | 1:00P - MIDNIGHT | 620000 | SECONDARY BYPASS STRUCTURE | RAIN 1.34" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-03-10 | 3/10 - 3/12 | 3190000 | SECONDARY BYPASS STRUCTURE | RAIN | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-03-13 | 3/13 | 760000 | SECONDARY BYPASS STRUCTURE | RAIN 0.2" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-03-14 | 12:00A - 10:45P | 20000 | SECONDARY BYPASS STRUCTURE | RAIN | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-03-31 | 3/31 - 4/2 | 370000 | SECONDARY BYPASS STRUCTURE | RAIN | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-04-03 | 12:00A - 9:00A | 70000 | SECONDARY BYPASS STRUCTURE | RAIN 0.3" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-04-06 | 4:00P - 10:15P | 250000 | SECONDARY BYPASS STRUCTURE | RAIN 0.98" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-04-07 | 4/7 - 4/8 | 100000 | SECONDARY BYPASS STRUCTURE | RAIN 1" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-04-19 | 7:30A - 8:00A | 20000 | SECONDARY BYPASS STRUCTURE | RAIN 0.9" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-04-21 | 3:00P - 9:00P | 300000 | SECONDARY BYPASS STRUCTURE | RAIN 0.56" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-05-02 | 6:00A - 1:00P | 460000 | SECONDARY BYPASS STRUCTURE | RAIN 1.2" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-05-18 | 1"00A - 11:00A (5/18) | 140000 | SECONDARY BYPASS STRUCTURE | RAIN 0.56" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-05-25 | 1:00A - 6:30A | 260000 | SECONDARY BYPASS STRUCTURE | RAIN 1" | SEWER REHABILIATATION IS PROGRESS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-06-02 | 11:00A - 1:30P | 80000 | SECONDARY BYPASS STRUCTURE | RAIN 0.63" | WORKING ON LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-06-10 | 1:30A - 6:30A | 290000 | SECONDARY BYPASS STRUCTURE | RAIN 1.55" | PHASE 1 OF LTCP COMPLETED, PHASE 2 UNERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-06-23 | 4:30P - 8:30P | 160000 | SECONDARY BYPASS STRUCTURE | RAIN 1.22" | PHASE 2 OT LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-07-12 | 2:30P - 5:00P | 50000 | SECONDARY BYPASS STRUCTURE | RAIN 1.15" | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-07-14 | 6:00P - 7:00P | 10000 | SECONDARY BYPASS STRUCTURE | RAIN | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-07-15 | 1:00A - 1:30A | 10000 | SECONDARY BYPASS STRUCTURE | RAIN | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-08-14 | 10:00P - MIDNIGHT | 150000 | SECONDARY BYPASS STRUCTURE | RAIN 1.7" | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-08-15 | 12:00P - NOON | 450000 | SECONDARY BYPASS STRUCTURE | RAIN 1.71" | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-08-27 | 5:30A - 7:30A | 60000 | SECONDARY BYPASS STRUCTURE | RAIN 1.7" | PHASE 2 OF LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-08-28 | 9:30A - 4:00P | 580000 | SECONDARY BYPASS STRUCTURE | RAIN 1.26" | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-09-22 | 8:30P - MIDNIGHT | 190000 | SECONDARY BYPASS STRUCTURE | RAIN 2" | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-09-22 | 11:30P - 9:00A (9/23) | 260000 | LIFT STATION (WELLS DR) | RAIN 5", POWER FAILURE, EQUIPMENT FAILURE | ORDERD SPARE PLC CARDS FOR BACKUPS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-09-22 | 9:20P - 8:00A (9/23) | 150000 | MANHOLE WEST OF LIFT STATION (GARAGE HILL RD) | RAIN 5" | CHECK PUMPS AND FORCE MAIN
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-09-22 | 9:00A - 11:35A (9/23) | 70000 | LIFT STATION (SHORTS ADDITION) | RAIN 5" | WORKING ON I & I REDUCTION
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-09-23 | 12:00A - 11:30P | 2070000 | SECONDARY BYPASS STRUCTURE | RAIN 1.04" | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-10-16 | 7:30P - MIDNIGHT | 30000 | SECONDARY BYPASS STRUCTURE | RAIN 1.5" | PHASE TWO OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-10-17 | 12:00A - 3:00P | 1180000 | SECONDARY BYPASS STRUCTURE | RAIN 0.87" | PHASE 2 OF LTCP UNDERWAY
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-10-27 | 11:30A - NOON (10/28) | 1320000 | SECONDARY BYPASS STRUCTURE | RAIN 1.35" | PHASE II OF LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-11-01 | 3:00P - 8:00P | 50000 | SECONDARY BYPASS STRUCTURE | RAIN 0.34" - WEST CLARIFIER DOWN FOR REPAIR / REHAB | WILL GET CLARIFIER BACK ONLINE AS SOON AS POSSIBLE
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-11-07 | 6:30A - 10:00P | 440000 | SECONDARY BYPASS STRUCTURE | RAIN 0.6" | WEST CLARIFIER DOWN FOR REPAIR
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-11-15 | 2:00P - MIDNIGHT | 920000 | SECONDARY BYPASS STRUCTURE | RAIN 0.9" | PROGRESS BEING MADE ON CLARIFIER REHAB
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-11-16 | 12:00A - 12:00P | 1200000 | SECONDARY BYPASS STRUCTURE | RAIN 0.4" | GETTING CLARIFIER BACK ONLINE AS QUICKLY AS POSSIBLE
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-11-17 | 12:00N - 3:00P | 80000 | SECONDARY BYPASS STRUCTURE | RAIN, WEST CLARIFIER DOWN FOR REPAIR | WEST CLARIFIER UNDER CONSTRUCTION
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-11-30 | 7:00P - 12:00A | 196000 | SECONDARY BYPASS STRUCTURE | RAIN 0.8", WEST CLARIFIER DOWN FOR REHAB & REPAIR | GET CLARIFIER BACK ON LINE
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-12-01 | 12:00A - 12:00P | 2540000 | SECONDARY BYPASS STRUCTURE | RAIN 0.87" | GET CLARIFIER BACK ON LINE ASAP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-12-12 | 2:45P - 6:30P | 60000 | SECONDARY BYPASS STRUCTURE | RAIN 0.4", WEST CLARIFIER DOWN FOR REPAIR
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-12-21 | 1:46P - 12:00A | 680000 | SECONDARY BYPASS STRUCTURE | RAIN 0.87" | STARTING UP WEST CLARIFIER 12/27
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-12-22 | 12/22 & 12/23 | 470000 | SECONDARY BYPASS STRUCTURE | RAIN 0.2"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-12-25 | 12/25 - 12/26 | 2340000 | SECONDARY BYPASS STRUCTURE | RAIN 1.7" | STARTING UP WEST CLARIFIER
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2006-12-31 | 12/31 - 1/1 | 1100000 | SECONDARY BYPASS STRUCTURE | RAIN 1.1" | PHASE II OF LONG TERM CONTROL PLAN UNDERWAY
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-01-09 | ? - 2:00P | 2100 | CLEAN OUT LOT NO. 3948 | SEWER LINE BLOCKED WITH DEBRIS, SEWER & AREA CLEANED | SEWER CLEANING
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-01-24 | ? - 3:00P | 420 | CLEANOUT LOT 1501 | SEWER LINE BLOCKED WITH GREASE | SEWER CLEANING
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-03-08 | 3/8 |  | MULTIPLE LOCATIONS INCLUDING STATION 9 | RAIN 2.1" | COLLECTION SYSTEM BEING STUDIED
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-03-10 | 3/10 |  | VENT PIPE LOT NO 1319 | VACUUM HOSE DISCONNECTED | INSPECTION OF VALVE PITS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-03-11 | 3/11 |  | SEVERAL LICATIONS INCLUDING STA NO 9 | RAIN 3.5" | COLLECTION SYSTEM BEING STUDIED
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-04-09 | ? - 3:30P | 840 | LOT NO 3403 ROTHSHIRE CIRCLE | VACUUM VALVE BLOCKED, SEWAGE BACKUP, OVERFLOW OUT OF CLENAOUT | COLLECTION SYSTEM BEING STUDIED
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-04-11 | ? - 11:10A | 7350 | CLEANOUT - LOT NO 483 HICKORY WAY | SEWER BLOCKED WITH GREASE & DEBRIS | COLLECTION SYSTEM BEING STUDIED FOR PROBLEMS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-04-15 | ? - 3:30P, EST 7 DAYS | 7350 | CLEANOUT - LOT NO 3920 | VACUUM VALVE FAILURE | COLLECTION SYSTEM BEING STUDIED TO ADDRESS OVERFLOWS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-04-17 | ONE DAY | 1050 | LOT NO 3405 CLENAOUT | VACUUM VALVE FAILURE, EQUIPMENT REPAIRED | COLLECTION SYSTEM BEING STUDIED TO ADDRESS PROBLEMS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-04-18 | THREE DAYS | 4410 | LOT NO 2404: CAMPER TAP | VACUUM VALVE FAILURE, EQUIPMENT REPAIRED | COLLECTION SYSTEM BEING STUDIED TO ADDRESS PROBLEMS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-07-29 | 1:00P - 2:15P | 30 | LOT NO 1909, STANDPIPE | SEWER LINE BLOCKED | COLLECTION SYSTEM BEING STUDIED TO ADRESS OVERFLOWS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-08-10 | 8:30P - 9:30P | 30 | LOT NO 1763 CLEANOUT | SEWER LINE BLOCKED CAUSING SEWER BACKUP | COLLECTION SYSTEM BEING STUDIED
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-08-27 | 8/27 - 8/28 |  | MULTIPLE LOCATIONS INCLUDING STATION # 7 & 9 | RAIN 6.5" | COLLECTION SYS BEING STUDIED TO CORRECT OVERFLOWS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-09-02 | ? - 1:00P | 55 | LOT NO 2740 CLEANOUT OVERFLOW | VACUUM VALVE CONTROLLER FAILURE | REPAIRED, AREA CLEANED - COLL SYS BEING STUDIED FOR REPAIRS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-10-09 | ? - 9:30A (10/10) | 55 | SMALL LEAK - LOT NO 1748, 3" GRAVITY PIPE JOINT | LEAKING EXPOSED PIPE JOINT - EQUIPMENT FAILURE | COLLECTION SYSTEM BEING STUDIED TO ADDRESS REPAIRS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-10-17 | ? - 10:30A | 210 | LOT NO 1994 CLEANOUT | 3" SEWER LINE BLOCKED WITH GREASE | COLLECTION SYSTEM BEING STUDIED
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-10-17 | ? - 9:30A | 840 | LOT NO 3463 VENT PIPE | BROKEN LINE BETWEEN VALVE PIT & HOLDING TANK | COLLECTION SYS BEING STUDIED TO ADDRESS OVERFLOWS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-12-08 | 12/8 - 12/10 | 210 | LOT NO 3935 / 3985, VACUUM VENTS | EQUIPMENT FAILURE, WATER LOGGED VACUUM LINE | COLLECTION SYSTEM BEING STUDIED
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2006-12-19 | ? - 11:00A | 4200 | LOT NO 2609 CLEANOUT | BROKEN CLEANOUT, PVC & DIRT BLOCKING SEWER | SNAKED SEWER, REPAIRED CLEANOUT
IN0038539 | MUSCATATUCK STATE DEV. CENTER | JENNINGS | 2006-08-28 | 06:00 - 11:00 | 25000 | MUTC LIFT STATION | RAIN 4+"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-03-08 | 3/8 |  | THREE LIFT STATIONS | RAIN 2.03"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-03-09 | 3/9 - 3/10 |  | THREE LIFT STATIONS | RAIN 3.58"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-03-11 | 3/11 |  | THREE LIFT STATIONS | RAIN
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-06-07 | 6/7 |  | MANHOLE FORD'S CROSSING GOLF COURSE | BLOCKAGE IN SEWER
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-07-07 | 7/7 - 7/8 |  | NORTHEAST LIFT STATION FORCE MAIN - N 7TH ST | CRACKED FORCE MAIN | FLOW OF WASTEWATER CONTAINED
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-07-10 | 7/10 |  | MANHOLE G8-A - NORTH OF WEST SR 50 | GREASE ACCUMULATED AND BLOCKED SEWER AT MANHOLE | SMALL OVERFLOW - APPLIED LIME TO AREA
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-08-27 | 8/27 - 8/28 |  | FOUR LIFT STATIONS | RAIN 4.5"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-09-12 | 11:30A - 5:30P |  | SOUTHWEST, NORTHWEST, NORTHEAST & NORRIS LIFT STATIONS | RAIN 3.5"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-09-22 | 1.25 HRS |  | SW, NW, NE LIFT STATIONS | RAIN 1.69"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-10-17 |  |  | MANHOLE G6-A - NORTH OF WEST SR 50 | GREASE ACCUMULATED AND BLOCKED SEWERLINE | SEWER CLEANED
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-10-17 | 1 HOUR |  | NORTHWEST LIFT STATION | RAIN 2.51"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2006-11-30 | 10:30P - 10:00A (12/1) |  | SOUTHWEST, NORRIS & NORTHEAST LIFT STATIONS | RAIN 2.47"
| VERNON COLLECTION SYS | JENNINGS | 2006-09-12 | 9/12 |  | MANHOLE AT COMMONS LIFT STATION | RAIN
| VERNON, TOWN OF | JENNINGS | 2006-03-11 | 3/11 - 3/13 |  | MANHOLE @ COMMONS LIFT STATION | RAIN
IN0022314 | BARGERSVILLE MUNICIPAL STP | JOHNSON | 2006-02-22 | 6:45 - 8:45 | 4000 | DIGESTER | OPERATOR ERROR, WASTE VALVE LEFT OPEN, DISTRACTED
IN0022314 | BARGERSVILLE MUNICIPAL STP | JOHNSON | 2006-12-01 | AM - 2:00P |  | PLANT CLARIFIERS (SLUDGE) | RAIN 3" | IN THE PROCESS OF DOING A PLANT EXPANSION
| GREENWOOD, CITY OF | JOHNSON | 2006-09-03 | ? - 9:15A | 1000000 | HURRICANE CREEK LIFT STATION | CONTROL PANEL FAILURE, DISABLED ALARM SYSTEM | SPILL CONFINED IN CREEK & PUMPED BACK INTO SANITARY SEWER
IN0020966 | NEW WHITELAND MUNICIPAL STP | JOHNSON | 2006-03-13 | 04:00 - 13:30 | 150000 | WWTP OVER CAPACITY | RAIN 5.09" | WILL DO I&I REPAIRS
IN0020966 | NEW WHITELAND MUNICIPAL STP | JOHNSON | 2006-04-05 | 6:00P - 7:20P | 150 | DEAD END MANHOLE ON MIDDLE DR | SEWER MAIN STOPPED UP, CLEANED | INCREASE FREQUENCY OF SEWER INSPECTIONS
IN0040681 | TRAFALGAR MUNICIPAL STP | JOHNSON | 2006-06-17 | 9:45A - 10:45A | 1000 | MANHOLE # 136 | POWER FAILURE
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2006-08-20 | ? - 11:00P | 2000 | LIFT STATION FORCE MAIN | BREAK IN DISCHARGE FORCE MAIN | DIG UP AND REPLACE OR REPAIR FORCE MAIN
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-01-02 | 1/2 - 1/3 | 800000 | WET WELL AT TREATMENT PLANT | RAIN 2", #1 RAW PUMP FAILURE | PLANT CONSTRUCTION TO BEGIN NEXT YEAR
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-01-13 | 6:00A - 5:30P | 1000000 | PLANT WET WELL, AERATION TANKS | HEAVY RAIN, I&I PROBLEM | NEW POTW IN THE DESIGN PHASE
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-01-17 | 06:00 - 13:00 | 500000 | PLANT WET WELL & AERATION TANKS | RAIN 1", SATURATED GROUND, I&I PROBLEM | INSITUFORM IS SLIPLINING MAIN LINE, TO BE COMPLETE IN ONE WEEK
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-02-02 | 3:30P - 7:00P | 100000 | WET WELL, AERATION TANKS | RAIN 0.75" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-03-08 | 3/8 - 3/10 | 6000000 | PLANT & COLLECTION SYSTEM (MANHOLES & LIFT STATIONS) | RAIN 1.75" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-03-08 | 3/8 - 3/9 | 2000000 | WET WELL, AREATION TANKS, LIFT STATION 3 | RAIN 2.5" | NEW PLANT & LIFT STATION IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-03-08 | 3/8 - 3/11 | 3000000 | WET WELL, AERATION TANKS & SECONDARIES | RAIN 1.5" | SEWER, WWTP & LIFT STATION PROJECTS PLANNED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-03-08 | 3/8 - 3/14 | 1000000 | WET WELL | RAIN 0.5" | NEW TREATMENT PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-03-12 | 3/12 | 1200000 | LIFT STATIONS # 1, 3, WET WELL & AERATION TANKS | RAIN 2" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-03 | 4/3 - 4/7 | 10000 | LIFT STATION # 2 | STORM CAUSED SEVERE ELECTRICAL DAMAGE | LIFT STATION ELECTRICAL NEEDS TO BE REBUILT
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-07 | 9:00A - 10:30A | 1000000 | WET WELL, AERATION TAKNS, & SECONDARIES AT WWTP | RAIN 1.5" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-07 | 9:00A - 10:30A | 20000 | LIFT STATION # 2 | PUMP LS DOWN TO MAKE CONNECTION TO FORCE MAIN | LIFT STATION TO BE REBUILT
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-16 | 10:00P - 6:00A (4/17) | 20000 | MANHOLE ON MARY STREET | RAIN 3" | NEW LIFT STATION BEING INSTALLED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-16 | 9:00P - 6:00A (4/18) | 1000000 | WET WELL | RAIN 3" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-16 | 10:00P - 8:00A (4/17) | 20000 | MANHOLE ON POWELL ST | RAIN 3" | NEW LIFT STATION BEING INSTALLED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-16 | 9:00P - 5:00A (4/17) | 50000 | LIFT STATION # 3 WET WELL | RAIN 3" | NEW LIFT STATION BEING INSTALLED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-16 | 9:00P | 1000000 | WET WELL, AERATION TANKS, SECONDARIES | RAIN 3" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-19 | 4:00A - 2:00A (4/20) | 50000 | MANHOLE ON POWELL ST | RAIN 2" | NEW LIFT STATION BEING INSTALLED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-19 | 2:00A - 9:00A | 20000 | MANHOLE ON MARY STREET | RAIN 2" | NEW LIFT STATION BEING INSTALLED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-19 | 2:00A - 5:30A (4/20) | 1000000 | WET WELL | RAIN 2" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-04-19 | 2:00A - 1:30P | 50000 | LIFT STATION # 3 WET WELL | RAIN 2" | NEW LIFT STATION BEING INSTALLED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-05-02 | 2:00A - 8:00A (5/3) | 1000000 | WET WELL | RAIN 1.5" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-05-11 | 4:00A - 1:00A (5/12) | 1000000 | PLANT WET WELL | RAIN 1.5" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-08-10 | 5:00P - 9:00P | 250000 | PLANT WET WELL, AERATION TANKS | RAIN 1.5" | NEW WWTP PLANNED
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-10-17 | 3:00A - 4:00A | 20000 | OVERFLOW AT PLANT WET WELL | RAIN 2.25" | WORK ON NEW PLANT TO BEGIN SOON
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-10-27 | 5:00A - 8:00A (10/28) |  | PLANT WET WELL / HEADWORKS | RAIN 2" - HEADWORKS OVERWHELMED | NEW PLANT IN FINAL DESIGN STAGE
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-11-15 | 10:30A - 8:00A (11/18) | 500000 | OVERFLOW AT WET WELL | RAIN 3.5" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-11-15 | 10:30A - | 1000000 | OVERFLOW AT PLANT WET WELL, AERATION TANKS | RAIN 3" | NEW PLANT IN THE WORKS
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-11-16 | 4:00A - 1:00P | 25000 | LIFT STATION # 3 | RAIN 3" | PLAN TRUNK LINE REHAB
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-11-30 | 3:00P | 1000000 | OVERFLOW AT WET WELL, AERATION TANKS | RAIN 2.75" | NEW TREATMENT PLANT TO BE BID SOON
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-12-12 | 10:00A - 9:00A (12/15) | 500000 | OVERFLOW AT WET WELL | RAIN 1" | NEW PLANT CONSTRUCTION TO BEGIN IN THE SPRING
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2006-12-21 | 12/21 - 12/27 | 6000000 | OVERFLOW AT WET WELL | RAIN 1.25" | NEW PLANT IN THE WORKS
IN0023795 | MONROE CITY MUNICIPAL STP | KNOX | 2006-04-19 | 03:00 - 08:30 | 8000 | MAIN LIFT STATION AT SEWER PLANT | RAIN 4.25", BOTH PUMPS UNABLE TO KEEP UP
IN0040444 | NORTH WEBSTER MUNICIPAL STP | KOSCIUSKO | 2006-08-27 | 6:00P - 9:00P | 600 | LIFT STATION # 2 - ALBERT ECKERT DR | LIFT STATION # 2 PUMP BURNED OUT | REPLACE PUMP, PUMP DOWN STATION, CHECK CONTROLS
IN0003387 | R. R. DONNELLEY & SONS COMPANY | KOSCIUSKO | 2006-01-17 | 3:00A |  | SANITARY SEWER PIPE NEAR LIFT STATION | DAMAGED SANITARY PIPE | REPAIRING SEWER PIPE
IN0025208 | SUBURBAN ACRES M.H.P. | KOSCIUSKO | 2006-04-18 | 8:00A - 10:00A | 2 |  | TREE ROOTS CLOGGING DRAIN | REMOVED ROOTS, CLEANED AREA
IN0021172 | SYRACUSE MUNICIPAL STP | KOSCIUSKO | 2006-02-10 | 2/10 | 100 | MANHOLE 1306 N HUNTINGTON | PLUG IN GRAVITY SEWER LINE, JETTED TO CLEAR | JETTED MAIN LINE
IN0021172 | SYRACUSE MUNICIPAL STP | KOSCIUSKO | 2006-02-11 | ? - 2:00P | 50 | MANHOLE 1306 N HUNTINGTON | PLUG IN GRAVITY SEWER LINE, JETTED TO CLEAR | DAILY CHECK OF LINE, CLEANING ENTIRE SECTION
IN0021172 | SYRACUSE MUNICIPAL STP | KOSCIUSKO | 2006-12-26 | 11:00 - 12:05 | 250 | MANHOLE AT 1316 N HUNTINGTON | CLOGGED MAIN SEWER | SEWER MAIN JETTED
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-01-09 | 9:15A - 9:20A | 10 | 519 N PARK AVENUE MANHOLE | BLOCKAGE IN SEWER | SEWER CREW USED TO CLEAR BLOCKAGE
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-01-20 | 2:40P - 2:58P | 200 | 527 E. WINONA AVE | SEWER BLOCKAGE | SEWER CREW CLEANED SEWER LINE
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-02-17 | 12:05P - 12:50P | 200 | MANHOLE NEAR BRUBAKER & SIMMONS LIFT STATION | GREASE BLOCKAGE IN SEWER LINE, VAC TRUCK USED TO CLEAR | MONITORING LINE
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-02-24 | 11:50A - 12:15P |  | MANHOLE BRUBAKER & SIMMS LIFT STATION | SEWER BLOCKAGE | SEWER TO BE TELEVISED & CLEANED
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-03-16 | 11:30A - 11:45A | 400 | ANEROBIC DIGESTER | OPENED WRONG VALVE DURING PUMP REPLACEMENT | AREA CLEANED & RETURNED TO DIGESTER
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-06-11 | 10:20A - 10:45A | 50 | MINER DRIVE LIFT STATION | LIFT STATION FLOATS HAD BECOME ENTANGLED | LIFT STATION BEING ADDED TO SCADA SYSTEM
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-07-15 | 2:20P - 4:20P | 50 | MANHOLE AT 315 N DETROIT ST | SEWER BLOCKED WITH GREASE & DEBRIS | INSPECTING MCDONALDS GREASE TRAP / INTERCEPTOR
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-08-28 | 9:50A - 9:51A | 250 | SLUDGE STORAGE TANK | SLUDGE LOADING CHUTE BROKE DURING LOADING | REPAIRS COMPLETED AND AREA CLEANED
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-09-18 | 7:30P - 7:35P | 15 | FAIRLANE DRIVE FORCE MAIN | PLUG BECAME DISLODGED DURING LS WET WELL REPLACEMENT | FREQUENTLY CHECK STATUS OF THE PLUG
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-09-22 | 10:15A - 10:19A | 20 | FAIRLANE DRIVE FORCE MAIN | CONTRACTOR TRACKHOE DAMAGED FORCE MAIN | PLACED ADDITIONAL CLAMP ON FORCE MAIN
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-10-20 | 10:04A - 10:05A | 10 | FAIRLANE DR SOUTH LIFT STATION | DAMAGE TO FORCE MAIN DURING REPLACEMENT OF VALVE PIT | CAREFUL EXCAVATION
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-11-13 | 3:40P - 3:45P | 30 | FAIRLANE DR FORCE MAIN | DURING VALVE PIT REPLACEMENT FORCE MAIN WAS DAMAGED
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-11-25 | 8:30A - 10:20A | 50 | MANHOLE AT NYE ST & TIPPECANOE DR | OBSTRUCTION IN SEWER | SPILL CONTAINED - SEWER TO BE CLEANED
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2006-12-31 | 9:25A - 10:15A | 100 | MANHOLE AT 529 E MARKET ST | BLOCKAGE IN SEWER | CLEAN SEWER LINE
IN0030911 | YOGI BEAR'S JELLYSTONE PARK | KOSCIUSKO | 2006-05-28 | 8:00P - 2:00A | 1000 | MANHOLE # 489 | PLUGGED MANHOLE & SEWER LINE | PERIODIC CLEANING OF MANHOLE & SEWER LINE
IN0050041 | AUTUMN CREEK MOBILE HOME PARK | LA PORTE | 2006-09-07 | 10:00A - NOON |  | WWTP LIFT STATION WET WELL | PUMPS CLOGGED WITH DEBRIS | PROPOSED TO HAVE WET WELL CLEANED WITH VAC TRUCK
IN0050041 | AUTUMN CREEK MOBILE HOME PARK | LA PORTE | 2006-09-11 | 10:00A - 11:45A |  | WWTP LIFT STATION WET WELL | PUMPS CLOGGED WITH DEBRIS | PROPOSED TO HAVE WET WELL CLEANED WITH VAC TRUCK
IN0024848 | WESTVILLE MUNICIPAL STP | LA PORTE | 2006-07-14 | 7/14 | 62700 | BYPASS OF FILTERS AT SPLITTER BOX TO POST-AIR (PROCESS BYPASS) | RAIN 1.5", TOO MUCH FLOW FOR FILTERS TO HANDLE | ADJUST VARIABLE SPEED PUMPS AT HEADWORKS
IN0062014 | LAGRANGE CO. SEWER DISTRICT | LAGRANGE | 2006-04-19 | 4/19 - 4/20 | 8000 | BROKEN SEWER MAIN - 0320 E / 450 S | CONTRACTOR DAMAGED SEWER LINE IN FARM FIELD | SEWER REPAIRED
IN0060097 | LAGRANGE CO. SEWER DISTRICT | LAGRANGE | 2006-06-11 | 12:30 - 12:50 | 9000 | LIFT STATION # 2 - 3515S / 1145E | ELECTRONICS CONTROLLER / PUMP FAILURE | REPLACING ELECTRONICS
IN0060097 | LAGRANGE COUNTY SD, REGION B | LAGRANGE | 2006-09-17 | 7:30P | 15000 | LIFT STATION # 4 - CO ROAD 1025 & CO ROAD 630 | ELECTRICAL DAMAGE TO LEVEL CONTROLLER & MONITORING EQ | LOOKING INTO ADDED LAYER OF SURGE PROTECTION
IN0020478 | LAGRANGE MUNICIPAL STP | LAGRANGE | 2006-03-13 | 7:00A - 9:30A | 50 | MANHOLE AT NORTH CANAL STREET | RAIN 1.9" | COLLECTION SYSTEM UNDER EVALUATION
IN0020478 | LAGRANGE MUNICIPAL STP | LAGRANGE | 2006-07-11 | 11:30P - 11:50P | 500 | TWO MANHOLES AT WAYNE & CANAL ST | RAIN 3" | AREA CLEANED, CONTINUE TO IDENTIFY INFLOW SOURCES
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2006-07-11 | 3:45A - 4:15A |  | LIFT STATION 1, PINECREST, 147TH COURT & LEE ST | RAIN 3.25", SEWER SURCHARGE
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2006-08-04 | 8:01A - 8:15A |  | LIFT STATION 6 | TREE BRANCH HAD FALLEN ON THE LINES CAUSING POWER LOSS
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2006-08-20 | 12:45P |  | LIFT STATION CEDAR RIDGE ESTATES - 134TH COURT | ELECTRICAL FAILURE AT LIFT STATION
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2006-09-13 | 2:00P - 2:30P |  | LIFT STATION #1 PINECREST MARINA 14415 LAUERMAN AVE | RAIN 3.1"
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2006-09-18 | 2:30P - 4:45P |  | MANHOLE - 128TH & CLINE AVE | SEWER LINE BLOCKAGE
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2006-12-17 | 8:30A - 10:30A |  | LIFT STATION # 8 - 125TH AVE E OF US 41 - WICKER AVE | NIPSCO POWER OUTAGE
IN0025763 | CROWN POINT MUNICIPAL STP | LAKE | 2006-03-13 | 3:00A - 4:00P | 78000 | NE CORNER EDGEWATER RD & CENTER RD | RAIN 1.3" | INCREASE STORAGE PLAN
IN0025763 | CROWN POINT MUNICIPAL STP | LAKE | 2006-03-13 | 3:00A - 4:00P | 78000 | NE CORNER EDGWATER RD & CENTER RUN | RAIN 1.3" | INCREASED STORAGE PLAN PROPOSED
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-01-13 | 2:30P - 2:30A (1/14) | 220000 | PARTIAL BYPASS OF TERTIARY FILTERS | RAIN, HIGH FLOWS
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-03-13 | 2:30A - 2:30P | 1075500 | SECONDARY CLARIFIERS | RAIN 1.04"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-04-16 | 4/16 - 4/18 | 7430000 | SECONDARY CLARIFIERS (BEFORE TERT. FILTERS) | RAIN 3.71"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-05-29 | 5:30P - 7:00P | 75000 | SECONDARY CLARIFIERS TO CHLORINE CONTACT TANK | RAIN 1.31" - PARTIAL BYPASS OF TERTIARY FILTERS (HIGH FLOWS)
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-06-10 | 5:00A - 7:00P | 1750000 | PARTIAL BYPASS OF THE TERTIARY FILTERS | HIGH FLOW - RAIN 2.02"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-08-19 | 1:20A - 4:40A | 407000 | PARTIAL BYPASS OF TERTIARY FILTERS | RAIN 1.64", HIGH FLOW
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-08-28 | 2:30P - 2:00A (8/29) | 1445000 | PARTIAL BYPASS OF TERTIARY FILTERS | RAIN 2.35", HIGH FLOWS | REMIXED WITH EFFLUENT, CHLORINATED & SAMPLED
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-09-11 | 11:00A - 4:30P | 230000 | PARTIAL BYPASS OF FILTERS - CHLORINATED & SAMPLED | RAIN 0.85"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-09-13 | 9:00A - 6:00P (9/14) | 4700000 | PARTIAL BYPASS OF TERTIARY FILTERS - REMIXED WITH EFFLUENT | RAIN 3.13"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-10-03 | 12:00A - 06:30A | 190000 | SECONDARY CLARIFIERS (BEFORE TERT. FILTERS) | RAIN 1.58" - PARTIAL BYPASS OF TERTIARY FILTERS DUT TO HIGH FLOWS
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-11-29 | 11:30P - 02:30P (11/30) | 638000 | SECONDARY CLARIFIERS (BEFORE TERT FILTERS) | RAIN 1.48"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-11-30 | 11:30P - 02:30A (12/2) | 2157000 | SECONDARY CLARIFIERS (BEFORE TERT FILTERS) | RAIN, 1.02" PARTIAL BYPASS OF FILTERS
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-11-30 | 2:00P - 03:00 (12/1) | 200000 | JACKSON COURT LIFT STATION | FORCE MAIN BREAK
IN0039331 | DYER MUNICIPAL STP | LAKE | 2006-12-22 | 8:00A - 5:30P | 1350000 | PARTIAL BYPASS OF TERTIARY FILTERS | RAIN 0.89"
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2006-07-17 | 7:30A - 9:30A | 10000 | 2698 CALHOUN - MANHOLE DISCHARGE | POWER OUTAGE TO 27TH AND CALHOUN PUMPING STATION | RESEARCHING ALTERNATIVE POWER SOURCE FOR STATION
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2006-09-13 | 10:00A - 10:30A (9/14) |  | MANHOLE 2698 CALHOUN | RAIN (4") WASHING DEBRIS INTO LIFT STATION PUMPS | RECOMMEND TO UPGRADE TO GRINDER PUMPS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2006-12-15 | 11:59A - 14:42P | 650000 | 15TH AND CLAY PUMP STATION - 15TH & ELKHART CSO | THE PUMP STATION'S PUMP CONTROL SYSTEM (PLC) FAILED | STEPS TAKEN TO REPLACE CONTROLLER
| GRIFFITH, TOWN OF | LAKE | 2006-04-17 | 14 HRS | 3500000 | PUMPING FROM EQ BASIN TO SWAMP NORTH OF FACILITY | RAIN 5"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-01-02 | 1:00P - 1/5 | 6000 | WHITE OAK LIFT STATION | FORCE MAIN RUPTURED WASHING OUT GROUND | EMERGENCY REPAIR, ADJUSTED SUMP TO MINIMIZE DISCHARGE
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-02-23 | 2/23 |  | WHITE OAK LIFT STATION | CONTINOUS LEAK IN FORCE MAIN, EMERGENCY REPAIR
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-03-15 | 7:25A - 10:25A | 30000 | 173RD & FOREST AVE STATION 013 | CONTINUATION OF RAIN EVENT ON 3/13
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-03-15 | 3:30P - 3:44P | 330000 | INDIANAPOLIS BLVD STATION OUTFALL 008 | DRY WEATHER PUMP FAILED, REPAIRED
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-04-19 | 12:00A -10:55P | 210000 | 173RD & FOREST AVE - OUTFALL 011 | RAIN 4.5"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-04-19 | 12:05A - 8:37P | 260000 | CALUMET / MUNSTER PUMP STATION - OUTFALL NO 014 | RAIN 4.5"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-05-29 | 1:30P - 10:30P | 60000 | WHITE OAK PUMPING STATION | NIPSCO POWER OUTAGE (LIGHTNING) | USED PORTABLE PUMPS TO PREVENT BASEMENT BACKUPS
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-05-30 | 7:08P - 8:38P | 3000000 | MAIN PLANT / SOHL AVE / KENNEDY AVE | WIDE SPREAD POWER OUTAGE & LIGHTNING STRIKE | USED GENERATORS TO POWER PUMPS
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-09-02 | 12:39A - 12:48A | 140000 | JACKSON AVE - OUTFALL # 011 | SEWER CAVE IN ON 177TH AVE NEAR STATION | SCHEDULED REPAIR
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-09-16 | 0.46 HRS | 160000 | CALUMET / MUNSTER - OUTFALL # 014 | RAIN 4.55"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-09-16 | 2.25 HRS | 2250000 | INDIANAPOLIS BLVD - OUTFALL # 007 | RAIN 4.55"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-09-16 | 0.05 HRS | 140000 | JACKSON AVE - OUTFALL # 010 | RAIN 4.55"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-09-16 | 0.08 HRS | 270000 | SOHL AVE STATION - OUTFALL # 004 | RAIN 4.55"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-09-16 | 1.83 HRS | 420000 | 173RD & FOREST AVE - OUTFALL # 011 | RAIN 4.55"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-09-16 | 0.07 HRS | 80000 | WALNUT AVE - OUTFALL # 008 | RAIN 4.55"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-03 | 12:33A - 9:20P | 450000 | JACKSON AVE LIFT STATION - OUTFALL # 010 | RAIN 1.74"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-03 | 12:00A - 11:32P | 220000 | 173RD & FOREST AVE LIFT STATION - OUTFALL # 011 | RAIN 1.74"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-03 | 12:52A - 12:58A | 30000 | CALUMET / MUNSTER LIFT STATION - OUTFALL # 014 | RAIN 1.74"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-04 | 12:08A - 8:44P | 40000 | 173RD & FOREST AVE LIFT STATION - OUTFALL # 011 | RAIN 1.74"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-04 | 11:07A - 8:34P | 250000 | JACKSON AVE LIFT STATION - OUTFALL # 010 | RAIN 1.74"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-24 | 4:10A - 10:40P | 300000 | JACKSON AVE OUTFALL #010 | RAIN 1.32", CONTINUATION OF RAIN EVENT ON 12/21 & 12/22
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-24 | 12:19A - 4:29P | 70000 | HOHMAN / MUNSTER OUTFALL #012 | RAIN 1.32", CONTINUATION OF RAIN EVENT ON 12/21 & 12/22
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-24 | 12:11A - 11:59P | 240000 | 173RD & FOREST OUTFALL #011 | RAIN 1.32", CONTINUATION OF RAIN EVENT ON 12/21 & 12/22
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-25 | 8:06A - 10:50P | 20000 | JACKSON AVE OUTFALL #010 | RAIN 1.32", CONTINUATION OF RAIN EVENT ON 12/21 & 12/22
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-25 | 12:19A - 11:59P | 120000 | 173RD & FOREST OUTFALL #011 | RAIN 1.32", CONTINUATION OF RAIN EVENT ON 12/21 & 12/22
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-26 | 7:56P - 8:00P | 50000 | 173RD & FOREST OUTFALL #011 | RAIN 1.32", CONTINUATION OF RAIN EVENT ON 12/21 & 12/22
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2006-12-26 | 11:50A - 7:52P | 20000 | 173RD & FOREST OUTFALL #011 | RAIN 1.32", CONTINUATION OF RAIN EVENT ON 12/21 & 12/22
IN0025283 | HERMITS LAKE WWTP | LAKE | 2006-01-06 | 9:00A - 11:00A |  | LIFT STATION 121 ST AVE | LIFT STATION PUMP FAILURE | SEPTIC SERVICE REMOVING WASTE FROM WET WELL
IN0025283 | HERMITS LAKE WWTP | LAKE | 2006-09-12 | 9/12 |  | LIFT STATION WET WELL 121ST AVE | RAIN 2+"
| HOBART | LAKE | 2006-03-13 | 4:20A - 1:55P |  | MANHOLE ALONG DEEP RIVER, N OF MAIN LIFT STATION | RAIN 3.07" | COVERED LID WITH SAND BAGS
| HOBART | LAKE | 2006-04-17 | 1:50A - 10:00A |  | MANHOLE ALONG DEEP RIVER N OF MAIN LIFT STATION | RAIN 1.83"
| HOBART | LAKE | 2006-07-20 | 11:46A - 5:30P |  | MANHOLE LIFT STATION | RAIN 2.53" | CHECKING ENTIRE SYSTEM FOR STORM INFLOW
| HOBART | LAKE | 2006-07-27 | 7:00P - 12:01A |  | MANHOLE | RAIN 1.75" | CHECKING ENTIRE SYSTEM FOR I&I
| HOBART | LAKE | 2006-08-28 | 3:05P - 9:10P |  | MANHOLE | RAIN 1.81" | CONTINUE TO CHECK ENTIRE SYSTEM FOR I&I
| HOBART | LAKE | 2006-09-13 | 10:45 - 1:45A (9/14) |  | MANHOLE # 705-063 | RAIN 2.25" - 4" | CONTINUE TO CHECK SYSTEM FOR I&I
| HOBART | LAKE | 2006-12-01 | 12/1 - 12/2 |  | MANHOLE 705 - 063 | RAIN 2.59" | VIDEOING SEWER LINES LOOKING FOR I&I
| HOBART | LAKE | 2006-12-22 | 8:10A - 5:30P |  | MANHOLE # 705-063 | RAIN 1.79" | WORKING ON I & I REDUCTION
IN0061344 | HOBART WWTP | LAKE | 2006-10-03 | 12:15A - 9:00A |  | MANHOLE # 705-063 | RAIN 2.5" | CONTINUE TO CHECK SYSTEM FOR I&I
IN0000094 | ISPAT INLAND INC. | LAKE | 2006-01-25 | 1/25 - 1/27 |  | POSSIBLE BYPASS OF SAMPLING POINT 602 | STARTUP OF 12" BARMILL COOLING TOWER MAY REQUIRE BYPASS | REQUIRED MAINTENANCE
IN0033081 | LAKE DALE DEVELOPMENT | LAKE | 2006-04-10 | 9:00 - 12:45 | 15000 | OVERFLOW OF AERATION TANK TO PLANT EFFLUENT SEWER | PIPE BETWEEN SETTLING & AERATION TANKS PLUGGED | BROKEN PIPE DISCOVERED & REPLACED
IN0033081 | LAKE DALE DEVELOPMENT | LAKE | 2006-09-14 | 9/14 - 9/15 |  | TREATMENT PLANT - HIGH FLOW THROUGH PLANT | RAIN 4" | INVESTIGATING CAUSE OF HIGH FLOW THROUGH PLANT
IN0000094 | MITTAL STEEL USA - INDIANA HARBOR E | LAKE | 2006-08-28 | 2:15P - 4:15P | 240000 | NO 6 PUMP HOUSE SURGE WELL - BYPASS OF TREATED WATER | RAIN 5.6" | OVERFLOW WATER DRAWN BACK INTO MAIN INTAKE OF THE PLANT
IN0000094 | MITTAL STEEL USA - INDIANA HARBOR E | LAKE | 2006-09-13 | 8:22A - 10:10A | 113184 | OVERFLOW FROM SURGE WELL AT # 6 PUMP HOUSE | RAIN 5.4" - OVERFLOW OF SHEET PILE DIVIDER WALL | ALL OVERFLOW DRAWN BACK INTO INTAKE OF THE PLANT
IN0000094 | MITTAL STEEL USA - INDIANA HARBOR E | LAKE | 2006-10-03 | 1:29A - 1:39A | 3140 | OVERFLOW FROM SURGE WELL AT # 6 PUMP HOUSE | RAIN 2.6" - OVERFLOW OF SHEET PILE DIVIDER WALL | ALL OVERFLOW DRAWN BACK INTO INTAKE OF THE PLANT
IN0000094 | MITTAL STEEL USA - INDIANA HARBOR E | LAKE | 2006-10-11 | 11:55P - 12:31P | 19742 | OVERFLOW FROM SURGE WELL AT # 6 PUMP HOUSE | CIRCUIT BREAKER (POWER FAILURE) EAST PUMP STATION | UPS POWER ADDED FOR CRITICAL CONTROL DEVICES
IN0000094 | MITTAL STEEL USA - INDIANA HARBOR E | LAKE | 2006-12-20 | 7:39A - 7:53A | 2189 | OVERFLOW FROM SURGE WELL AT # 6 PUMP HOUSE | ABRUPT SHUTDOWN OF 80 INCH HOT STRIP MILL | WORKING ON PROCEDURE TO PREVENT ABRUPT SHUTDOWN
IN0000094 | MITTAL STEEL USA INC | LAKE | 2006-12-14 | 8:00A - 9:00A | 3000 | OUTFALL 018 - BYPASS OF A TREATMENT PROCESS | CONTRACTOR ERROR WORKING ON MACT UPGRADE | RE-TRAINING CONTRACTORS
IN0000094 | MITTAL STEEL USA, INC | LAKE | 2006-02-18 | 10:00P - 6:00A (2/19) | 9000 | BYPASS AROUND 602 | PUMP FAILURE (LOW TEMP) | REPLACED HOSE ON PUMPS
IN0000094 | MITTAL STEEL USA, INC. | LAKE | 2006-08-04 | 9:07A - 9:13A | 5000 | SURGE WELL BASIN RECYCLE SYSTEM | EQUIPMENT FAILURE - TEMPORARY OVERFLOW - INVESTIGATING | CORRECTIVE ACTION WILL BE TAKEN - INVESTIGATING
IN0000094 | MITTAL STEEL USA, INC. | LAKE | 2006-08-18 | 8/18 - 9/5 | 108870 | BYPASS AROUND INTERNAL OUTFALL 602 SAMPLING POINT | PLANNED OUTAGE, BYPASS REQUIRED FOR MAINTENANCE | ALL WATER WILL BE TREATED OR NON-CONTACT COOLING WATER
IN0041891 | NOB HILL SUBDIVISION | LAKE | 2006-03-13 | 3/13 |  | CONTACT CHAMBER OVERFLOWED BYPASSING POND | RAIN, HIGH FLOW
IN0041891 | NOB HILL SUBDIVISION | LAKE | 2006-09-13 | 9/13 |  | WWTP LIFT STATION WET WELL | RAIN 2+"
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-03-13 | 12:00A - 7:00A |  | MANHOLE 83 LANE | RAIN 0.89", LIFT STATION AT CAPACITY
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-04-16 | 10:30P - 7:30P (4/17) | 33900 | MANHOLE @ 83RD LANE | RAIN 3.39", LIFT STATION AT 100% CAPACITY
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-07-28 | 8:20P - 11:20P | 55 | MANHOLE BEHIND 8294 BLAINE PL | RAIN 1.92" | CLEAN UP DEBRIS
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-09-13 | 1:00P - 10:00P | 54000 | MANHOLE 7950 84TH PLACE | RAIN 4.9" LIFT STATION RUNNING AT CAPACITY | CLEANED UP AREA AFTER OVERFLOW
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-09-13 | 10:00A - 10:00P | 4800 | MANHOLE 83RD LANE | RAIN 4.9" LIFT STATION RUNNING AT CAPACITY | CLEANED UP AREA AFTER OVERFLOW
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-09-13 | 3:00P - 7:00P | 3900 | MANHOLE BEHIND 8294 BLAINE PL | RAIN 4.9" LIFT STATION RUNNING AT CAPACITY | CLEANED UP AREA AFTER OVERFLOW
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-09-13 | 4:00P - 10:00P | 46800 | MANHOLE 7930 84TH PLACE | RAIN 4.9" LIFT STATION RUNNING AT CAPACITY | CLEANED UP AREA AFTER OVERFLOW
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-09-13 | 3:00P - 7:00A (9/14) | 10400000 | WWTP OUTFALL 001 - PARTIALLY TREATED RELEASE | RAIN 4.9", PLANT FLOODING
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-12-01 | 8:45A - 11:45A | 4770 | MANHOLE @ 83RD LANE | RAIN 1.12"
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2006-12-22 | 8:45A - 2:00P | 25500 | MANHOLE 7930 84TH PLACE | RAIN 1.08"
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2006-01-30 | 1/30 | 500 | LIFT STATION FORCE MAIN VENT, 3778 KINGSWAY | AIR RELEASE VALVE FAILURE ON FORCE MAIN | REPAIR, CLEAN UP AREA
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2006-07-20 | 1:15P - 4:00P | 2000 | WWTP (PARTIAL BYPASS), AERATION TANK OVERFLOW | RAIN 3.2", HALF OF AERATION SHUTDOWN BECAUSE OF HIGH FLOW
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2006-09-13 | 1:00P - 2:00P | 100 | AERATION TANK | RAIN 3.5" | REPLACING VALVES TO CONTROL FLOW
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2006-09-13 | 12:45P - 4:00P | 6000 | MANHOLE # 307 (E LAKESHORE DR) | RAIN 4.5" | WORKING ON I & I REDUCTION
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2006-11-15 | 5:00P - 8:15P | 585 | MANHOLE 307 | OBSTRUCTION IN SEWER MAIN | ADDITIONAL CLEANING OF SEWER MAINS
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2006-11-23 | 10:50A - 1:30P | 20 | MANHOLE 225 | PARTIAL OBSTRUCTION IN SEWER MAIN | SEWER CLEANED & VIDEOED
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2006-12-22 | 9:45A - 12:15P | 200000 | ONE HALF OF WWTP PUT IN BYPASS MODE TO SAVE BACTERIAL POP | RAIN 2" | I&I REDUCTION PROGRAM
IN0058343 | WINFIELD TOWNSHIP WWTP | LAKE | 2006-02-10 | 2/10 |  | POLISHING POND BYPASSED | LACK OF HYDRAULIC CAPACITY | PLAN TO REMOVE POND AS A TREATMENT PROCESS FROM PERMIT
IN0058343 | WINFIELD TOWNSHIP WWTP | LAKE | 2006-07-20 | 10:00A - 4:00P |  | 110TH LANE WEST & COUNTRY MEADOWS LIFT STATION | POWER FAILURE
IN0058343 | WINFIELD TOWNSHIP WWTP | LAKE | 2006-09-13 | 9/13 |  | 110TH LN LIFT STATION WET WELL | LIGHINING STRUCK CONTROL PANEL | CONTRACTOR CALLED, ONE PUMP OPERATING
IN0025577 | LAPORTE MUNICIPAL STP | LAPORTE | 2006-10-03 | 12:45A - 2:30A | 1300 | KNOLL LIFT STATION | LIFT STATION LOST UTILITY POWER DURING STORM | INVESTIGATING THE USE OF PORTABLE GENERATORS AT LIFT STATIONS
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2006-05-24 | 08:10A - 3:30P | 70000 | MANHOLE GFS TRUCKING - 923 W US 20 | GREASE CAUSING TRANSDUCER, FLOAT SWITCH & PUMP FAILURE | CREW DISPATCHED TO SERVIVE LIFT STATION
IN0024848 | WESTVILLE MUNICIPAL STP | LAPORTE | 2006-02-17 | 4:37A - 1:33P | 86600 | FILTER SPLITTER BOX | RAIN 0.75", BYPASS OF FILTERS
IN0024848 | WESTVILLE MUNICIPAL STP | LAPORTE | 2006-09-13 | 11:20A - 2:45P | 19200 | BYPASS OF FILTER AT SPLITTER BOX | RAIN, EQUIPMENT FAILURE
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2006-01-06 | 09:00 - 13:00 | 20000 | HOSPITAL LIFT STATION | PUMP ELBOW BASE FAILURE | BASE ELBOW REPLACED
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2006-01-16 | 10:30 - 11:30 | 6000 | HIGH PRESSURE LINE ROGERS LIFT STATION | CONTRACTOR HIT HIGH PRESSURE LINE
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2006-05-11 | 07:30 - 10:30 | 25000 | RILEY BLVD LS # 002 | INFLUENT LINE TO STATION PLUGGED UP | USED JET TO OPEN LINE
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2006-05-17 | 10:30 - 13:30 | 40000 | MANHOLE BEFORE SPIDER CREEK LS - # 007 | INFLUENT LINE TO STATION STOPPED UP CAUSING MANHOLE OVERFLOW | JET USED TO CLEAN LINE, TO CHECK LINE
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2006-06-17 | 22:00 - 09:00 (6/18) | 40000 | RILEY BLVD & BEDFORD HEIGHTS LIFT STATIONS | DURING STORM COMMERCIAL POWER WAS LOST TO BOTH STATIONS
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2006-10-20 | 13:00 - 15:00 | 30000 | BROADVIEW LIFT STATION | SEWER LINE BLOCKAGE CAUSING LIFT STATION DISCHARGE | CHECK MORE FREQUENTLY
IN0038920 | BRIARWOOD SUBDIVISION | LAWRENCE | 2006-06-12 | 6/12 - 7/5 | 12000 | FORCE MAIN ON LOT # 75 | BREAK IN FORCE MAIN DISCOVERED BY ODOR COMPLAINTS | CLEANED AND FLUSHED AREA, REPAIRED BROKEN PIPE AND TESTED
IN0023787 | MITCHELL MUNICIPAL STP | LAWRENCE | 2006-03-11 | 3/11 - 3/12 | 60000 | W VINE ST RESIDENTS CLEANOUT & HOLDING LAGOON | RAIN 4.5" | SEWER STUDY PLANNED, TO USE CHECK VALVE
IN0023787 | MITCHELL MUNICIPAL STP | LAWRENCE | 2006-05-11 | 5/11 - 5/12 |  | CLEANOUT 200 BLOCK WEST VINE ST | RAIN - SEWER SYSTEM FLOWING AT CAPACITY | INSTALLED CHECK VALVE
IN0023981 | OOLITIC MUNICIPAL STP | LAWRENCE | 2006-09-10 | 22:00 - 09:00 (9/11) | 50000 | LIFT STATION | EQUIPMENT FAILURE | 3 CONTROL FLOATS REPLACED
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-01-02 | 1/2 |  | MANHOLE BEFORE PLANT HEADWORKS | FLOW GATE TO PLANT WAS NOT OPENED FULLY | FLOW GATE TO REMAIN OPEN FULL
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-01-22 | 1/22 - 1/24 |  | CSO 005 | CSO FLOWING 24 HRS AFTER RAIN EVENT
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-02-17 | 2/17 - 2/18 |  | MANHOLE N OF CANAL ST | RAIN 0.92" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-05-18 | 10:00A - 10:00A (5/20) | 10000 | CURVE ST & PIPE ST | LINE OBSTRUCTED WITH GRIT | PREVENTIVE MAINTENANCE (CLEANING) ON LINE
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-10-01 | 8:00A - 8:00A (10/2) | 1084000 | PLANT EFFLUENT RECEIVED LITTLE OR NO DISINFECTION | CL2 GAGE ON TANK NOT WORKING | CLOSER INSPECTION TO INSURE TANKS ARE DISCHARGING
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-10-17 | 7:00A - 8:00A (10/21) | 300000 | MANHOLE NORTH OF CANAL ST | RAIN 2.25" | LONG TERM CONTROL PLAN
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-11-16 | 8:00A - 7:00A (11/18) | 200000 | MANHOLE N OF PIPT ST | RAIN 1.1" | LONG TERM CONTROL PLAN
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-12-01 | 12/1 - 12/2 |  | MANHOLE ON WASHINGTON ST (VILLAGE PANTRY) | RAIN 2.07" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2006-12-01 | 12:00A - 12:00P | 400 | LINCOLN HTS LIFT STATION | RAIN 2.07" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-02 | 17:45 - 7:15 (1/3) | 6200000 | PRIMARY CLARIFIERS | RAIN 0.55" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-02 | 18:05 - 20:05 | 2200000 | RAW WET WELL | RAIN 0.55" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-10 | 7:30P - 11:20P | 1200000 | PRIMARY EFFLUENT | RAIN 0.53" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-11 | 06:30 - 07:30 | 500000 | PRIMARY EFFLUENT | RAIN 0.55" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-11 | 03:25 - 04:55 | 1000000 | PRIMARY EFFLUENT | RAIN 0.55" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-12 | 15:20 - 16:20 | 100 | FORCE MAIN 60TH & MADISON | BROKEN AIR RELEASE VALVE | KEEPING LIFT STATION PUMPED DOWN AS NEEDED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-13 | 07:00 - 13:45 | 6000000 | RAW WET WELL | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-13 | 07:00 - 18:00 (1/14) | 28500000 | PRIMARY CLARIFIERS | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-14 | 04:30 - 09:50 (1/14) | 5000000 | RAW WET WELL | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-14 | 08:30 - 08:45 | 10000 | # 2 FILTER | FILTER PLANT OPERATOR ERROR DURING BACKWASH | COUNSEL OPERATOR ON SOP
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-17 | 9:00 - 12:30 | 3000000 | RAW WET WELL | RAIN 0.53" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-17 | 07:00 - 03:30 (1/18) | 16700000 | PRIMARY CLARIFIERS | RAIN 0.53" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-19 | 1:35P - 2:10P | 65000 | 005 DEWEY STREET PRIMARY BYPASS | MELTING SNOW
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-21 | 04:20 - 07:30 | 1500000 | PRIMARY EFFLUENT | RAIN 0.18" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-21 | 5:30P - 6:30P | 1900 | 5523 SCATTERFIELD (SEWER CLOGGED) | BYPASS CAUSED BY GREASE DISCHARGED BY WHITE CASTLE | ADVISED WHITE CASTLE TO CLEAN AREA & GREASE TRAP
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-23 | 9:00A - 3:00P | 5000 | SEWER LINE TO 56TH LIFT STATION | SEWER LINE TO LIFT STATION CAVED IN | MAKING REPAIRS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-01-29 | 8:10A - 12:30P | 2200000 | RAW WET WELL | RAIN 0.72" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-02-02 | 2:45P - 6:20A (2/3) |  | PRIMARY CLARIFIERS | RAIN 0.75" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-02-02 | 3:35P - 8:36P | 2100000 | RAW WET WELL | RAIN 0.75" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-02-03 | 8:30A - 8:30P | 2000000 | PRIMARY CLARIFIERS | RAIN 0.75" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-02-04 | 12:30A - 12:15A (2/5) | 5600000 | PRIMARY CLARIFIERS | RAIN 0.75" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-02-16 | 9:26P - 4:00A (2/17) | 4500000 | PRIMARY CLARIFIERS | RAIN 0.84" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-02-16 | 9:52P - 2:00A (2/17) | 2800000 | RAW WET WELL | RAIN 0.84" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-02-16 | 4:06A - 5:10A | 700000 | PRIMARY CLARIFIERS | RAIN 0.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-08 | 3/8 - 3/11 | 9500000 | PRIMARY CLARIFIERS | RAIN 1.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-08 | 3/8 - 3/9 | 1500000 | PRIMARY EFFLUENT | RAIN 0.26" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-09 | 9:20 - 10:20 | 270000 | PRIMARY EFFLUENT | RAIN 0.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-09 | 3/9 - 3/10 | 4200000 | RAW WET WELL | RAIN | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-09 | 4:40P - 6:20P | 10000 | 5TH & SYLVAN ST | RAIN 0.77"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-11 | 9:55A - 6:55P | 4500000 | PRIMARY CLARIFIERS | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-12 | 3/12 - 3/15 | 31000000 | PRIMARY CLARIFIERS | RAIN 1.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-13 | 3/13 | 5000 | SOUTH BIO TOWER | RAIN, HIGH FLOW CAUSED TOWER TO OVERFLOW | ADJUST BYPASS GATE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-13 | 3/13 - 3/14 | 37000000 | RAW WET WELL | RAIN 2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-13 | 6:30 - 7:30 | 200 | QUINCY DRIVE LIFT STATION | PUMP CLOGGED | MAKE MORE FREQUENT CHECKS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-14 | 12:00P - 2:00P |  | SEWER BRFORE 56TH ST LIFT STATION | BLOCKAGE BETWEEN TWO LIFT STATIONS | INVESTIGATING SOURCES
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-28 | 11:50 - 13:05 | 680000 | PRIMARY EFFLUENT | RAIN 0.22" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-31 | 9:30 - 14:30 | 1700000 | PRIMARY EFFLUENT | RAIN 0.45" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-31 | 19:15 - 0545 (4/1) | 6300000 | PRIMARY EFFLUENT | RAIN 1.27" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-31 | 19:30 - 23:45 | 4000000 | RAW WET WELL | RAIN 1.27" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-03-31 | 10:45 - 12:30 | 1000000 | RAW WET WELL | RAIN 0.45" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-02 | 22:00 - 04:30 (4/3) | 4300000 | PRIMARY EFFLUENT | RAIN 0.47" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-02 | 23:15 - 01:45 (4/3) | 2000000 | RAW WET WELL | RAIN 0.47" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-03 | 20:40 - 22:40 | 330000 | PRIMARY EFFLUENT | RAIN 0.1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-07 | 07:00 - 08:30 | 1000000 | PRIMARY EFFLUENT | RAIN 0.11" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-14 | 19:15 - 03:30 (4/15) | 7000000 | RAW WET WELL | RAIN 2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-14 | 03:00 - 08:00 | 1000000 | PRIMARY EFFLUENT | RAIN 0.63" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-14 | 03:30 - 07:00 |  | RAW WET WELL | RAIN 0.63" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-14 | 19:00 - 03:00 (4/16) | 14000000 | PRIMARY EFFLUENT | RAIN 2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-16 | 04:00 - 07:00 | 1000000 | PRIMARY EFFLUENT | RAIN 0.17" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-16 | 22:45 - 06:15 (4/17) | 6000000 | RAW WET WELL | RAIN 0.87" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-16 | 22:00 - 03:30 (4/19) | 12000000 | PRIMARY EFFLUENT | RAIN 0.87" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-17 | 08:00 - 20:00 | 9500000 | RAW WET WELL | RAIN 0.87" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-17 | 8:46A - 10:15A | 1000 | 5TH & SYLVAN STREET | RAIN 0.41" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-04-30 | 10:00 - 21:00 | 5500000 | PRIMARY EFFLUENT | RAIN 0.54" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-02 | 04:30 - 07:30 | 3000000 | RAW WET WELL | RAIN 0.67" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-02 | 04:30 - 12:30 | 6600000 | PRIMARY EFFLUENT | RAIN 0.67" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-10 | 23:45 - 00:45 (5/11) | 1000000 | RAW WET WELL | RAIN 0.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-10 | 22:00 - 23:00 | 1000000 | RAW WET WELL | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-10 | 7:00 - 21:45 (5/11) | 1600000 | PRIMARY EFFLUENT | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-11 | 04:45 - 10:00 | 4400000 | RAW WET WELL | RAIN 0.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-11 | 11:10A - 11:50A | 1000 | FORCE MAIN AT WOOCREST & ASHBOURNE | EQUIPMENT FAILURE | EMERGENCY REPAIR
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-12 | 12:30 - 11:30 (5/13) | 2500000 | PRIMARY CLARIFIERS | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-13 | 7:38A - 11:15P (5/14) | 14200000 | PRIMARY CLARIFIERS | RAIN 0.43" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-13 | 11:00 - 13:15 | 2000000 | RAW WET WELL | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-17 | 18:15 - 16:45 (5/19) | 8000000 | PRIMARY EFFLUENT | RAIN 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-17 | 20:30 - 01:00 (5/18) | 4000000 | RAW WET WELL | RAIN 0.68" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-17 | 16:55 - 17:36 | 37000 | BIO TOWERS | ELECTRICAL PROBLEM SWITCHING BIO TOWERS | PREVENTIVE MAINTENANCE ON SWITCH GATES & VALVES
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-25 | 19:50 - 23:35 | 3000000 | PRIMARY EFFLUENT | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-25 | 00:00 - 01:00 | 125000 | PRIMARY EFFLUENT | RAIN 0.15" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-05-25 | 20:00 - 22:00 | 2000000 | RAW WET WELL | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-02 | 02:25 - 06:25 | 4000000 | RAW WET WELL | RAIN 0.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-02 | 02:00 - 11:00 | 6000000 | PRIMARY EFFLUENT | RAIN 0.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-07 | 6/7 | 3000000 | PRIMARY EFFLUENT | RAIN 0.91" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-07 | 4:41P - 7:45P | 1500000 | RAW WET WELL | RAIN 0.91" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-10 | 06:25 - 01:25 (6/11) | 15800000 | PRIMARY EFFLUENT | RAIN 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-10 | 06:45 - 16:30 | 7300000 | RAW WET WELL | RAIN 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-10 | 9:35A - 10:05A | 1000 | UNAPPROVED CSO - 5TH & SYLVAN ST | RAIN 1.59" | TO BE ADDRESSED IN THE FUTURE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-11 | 13:45 - 17:45 | 2500000 | PRIMARY EFFLUENT | RAIN 0.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-18 | 10:25P - 12:44A (6/19) | 2000000 | RAW WET WELL | RAIN 0.67" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-18 | 10:00P - 2:45P (6/19) | 4500000 | PRIMARY CLARIFIERS | RAIN 0.67" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-18 | 21:58 - 22:13 | 2000 | 5TH & SYLVAN - NON-PERMITTED CSO | RAIN 0.68" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-19 | 7:05P - 11:30P |  | PRIMARY CLARIFIERS | RAIN 0.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-19 | 20:00 - 22:00 | 2000000 | RAW WET WELL | RAIN 0.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-21 | 05:00 - 09:00 | 1500000 | PRIMARY EFFLUENT | RAIN 0.17" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-22 | 9:21 - 9:26 |  | 5TH & SYLVAN | RAIN 0.87"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-22 | 6/22 - 6/23 | 2500000 | RAW WET WELL | RAIN 0.69" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-22 | 6/22 - 6/23 | 5000000 | PRIMARY EFFLUENT | RAIN 0.69" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-27 | 12:50P - 22:52A | 26000 | RAW WET WELL | RAIN 0.12" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-27 | 12:10P - 4:27P | 2300000 | PRIMARY CLARIFIERS | RAIN 0.45" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-28 | 18:15 - 18:30 | 6100 | 5TH & SYLVAN - NONPERMITTED CSO | RAIN 0.97"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-29 | 6:43P - 9:45P | 1300000 | RAW WET WELL | RAIN 0.87" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-06-30 | 9:15 - 12:00 (7/1) | 500 | MANHOLE SOMMERSET & WINDMERE | ELECTRICAL PROBLEM AT MEADOW WOODS LIFT STATION | STATION REPAIRED - WILL INSPECT SEWER & LIFT STATION
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-04 | 1:27-4:30 & 7:30-12:30 | 7600000 | PRIMARY CLARIFIERS | RAIN 0.85" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-04 | 2-3A & 8-16:40 | 1500000 | RAW WET WELL | RAIN 0.85" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-11 | 11:30 - 19:00 | 1500000 | RAW WET WELL | RAIN 0.85" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-11 | 10:45 - 20:30 | 9000000 | PRIMARY EFFLUENT | RAIN 0.85" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-21 | 18:40 - 20:40 | 1600000 | PRIMARY EFFLUENT | RAIN 0.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-21 | 23:00 - 00:00 | 500000 | PRIMARY EFFLUENT | RAIN 0.25" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-22 | 01:30 - 05:30 | 1600000 | PRIMARY EFFLUENT | RAIN 0.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-22 | 02:30 - 03:15 | 300000 | RAW WET WELL | RAIN 0.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-28 | 00:30 - 00:45 |  | NON PERMITTED CSO - 5TH & SYLVAN | RAIN 1.05" | SEWER REPAIRS UNDERWAY
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-28 | 00:45 - 09:00 | 8000000 | PRIMARY EFFLUENT | RAIN 1.05" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-28 | 01:00 - 06:00 | 4400000 | RAW WET WELL | RAIN 1.05" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-28 | 19:45 - 22:00 | 1600000 | PRIMARY EFFLUENT | RAIN 0.25" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-07-28 | 2:22A - 9:45A | 13500 | SEWER LINE IN BROADWAY CSO AREA | EQUIPMENT FAILURE | VACUUMING UP DISCHARGE, LINE SHALL BE REPAIRED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-03 | 19:25 - 21:30 | 1000000 | RAW WET WELL | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-03 | 19:15 - 22:45 | 3300000 | PRIMARY EFFLUENT | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-03 | 19:01 - 19:10 | 8000 | 5TH & SYLVAN CSO | RAIN 0.43", NON PERMITTED CSO | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-10 | 13:45 - 16:45 | 2500000 | RAW WET WELL | RAIN 1.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-10 | 13:11 - 15:18 | 80000 | 5TH & SYLVAN - NON PERMITTED CSO | RAIN 0.74" | SEWER REPAIRS ARE BEING DESIGNED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-10 | 13:30 - 19:45 | 5000000 | PRIMARY EFFLUENT | RAIN 1.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-10 | 1:40 - 2:00 | 2000 | MANHOLE AT 1021 N 300 E - CHESTERFIELD LIFT STATION | RAIN 1.46" | WILL CHECK LIFT STATION & SEWERS FOR OBSTRUCTION
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-11 | 09:30 - 13:30 | 5000 | CHESTERFIELD LIFT STATION | RAIN 0.4" | FUTURE RECONSTRUCTION OF THIS LIFT STATION
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-11 | 9:35A - 10:35A | 200000 | RAW WET WELL | RAIN 0.4" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-11 | 7:20A - 12:45P | 3500000 | PRIMARY CLARIFIERS | RAIN 0.4" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-18 | 01:27 - 1:32 | 50000 | CSO # 28 | CHESTERFIELD LIFT STATION SHUT DOWN FOR VALVE REPLACEMENT | FIVE MINUTE OVERFLOW, LIFT STATION BACK IN SERVICE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-21 | 16:30 - 17:00 | 275000 | FILTERS | POWER FAILURE - FIRE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-21 | 10:30 - 18:30 | 1000000 | TERTIARY & SECONDARY | ELECTRICAL FIRE | CALLED ELECTRICIANS TO REMEDY PROBLEM
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-26 | 2:50 - 05:35 | 3200000 | PRIMARY EFFLUENT | RAIN 1.7" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-26 | 22:28 - 22:44 | 100000 | 5TH & SYLVAN - NON PERMITTED CSO | RAIN 1.7" | SEWER REPAIRS BEING DESIGNED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-26 | 22:15 - 03:30 (8/27) | 4200000 | RAW WET WELL | RAIN 1.7" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-08-27 | 00:22 - 00:25 | 60000 | CHESTERFIELD LIFT STATION | RAIN 1.7" | CONTINUED PM ON LIFT STATION PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-07 | 9:00A - 11:00A | 5000 | 5TH & SYLVAN CSO | FLUSHING CITY WATER DOWN CSO TO DETERMINE FALL (TESTING) | NO RECEIVING STREAM INVOLVED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-12 | 09:30 - 13:15 | 1500000 | PRIMARY EFFLUENT | RAIN 0.25" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-12 | 10:00 - 11:45 | 1500000 | RAW WET WELL | RAIN 0.25" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-18 | 10:40 - 12:40 | 800000 | RAW WET WELL | RAIN 0.4" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-18 | 10:15 - 16:30 | 4200000 | PRIMARY EFFLUENT | RAIN 0.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-22 | 21:15 - 23:15 | 1500000 | RAW WET WELL | RAIN 0.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-22 | 21:00 - 05:00 | 4000000 | PRIMARY EFFLUENT | RAIN | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-22 | 08:50 - 10:35 | 1200000 | PRIMARY EFFLUENT | RAIN 0.23" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-23 | 02:40 - 03:25 | 500000 | RAW WET WELL | RAIN | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-27 | 19:10 - 22:30 | 2500000 | PRIMARY EFFLUENT | RAIN 0.29" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-09-27 | 19:10 - 20:55 | 1500000 | RAW WET WELL | RAIN 0.24" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-03 | 05:15 - 08:15 | 2000000 | PRIMARY EFFLUENT | RAIN 0.4" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-03 | 06:15 - 06:45 | 400000 | RAW WET WELL | RAIN 0.4" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-04 | 18:30 - 04:30 (10/5) | 4500000 | PRIMARY EFFLUENT | RAIN 0.97" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-04 | 18:45 - 02:15 (10/5) | 6000000 | RAW WET WELL | RAIN 0.97" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-16 | 10/16 - 10/18 | 12200000 | PRIMARY EFFLUENT | RAIN 2.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-16 | 20:45 - 12:45 (10/17) | 6900000 | RAW WET WELL | RAIN 2.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-16 | 10/16 |  | RAW WET WELL | RAIN 2.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-19 | 08:25 - 14:55 | 3000000 | PRIMARY EFFLUENT | RAIN 0.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-19 | 23:00 - 07:00 (10/20) | 2200000 | PRIMARY EFFLUENT | RAIN 0.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-19 | 08:45 - 10:15 | 400000 | RAW WET WELL | RAIN 0.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-26 | 11:00P - 12:45P (10/27) | 4400000 | PRIMARY CLARIFIERS | RAIN 0.75" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-26 | 11:16P - 12:09A (10/27) | 200000 | RAW WET WELL | RAIN 0.75" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-27 | 14:00 - 23:00 | 4000000 | RAW WET WELL | RAIN 1.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-27 | 23:00 - 23:50 | 1000 | NORTH BIO TOWER | PUMP # 2 & # 6 FAILED | MONITOR TOWERS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-27 | 13:00 - 04:00 (10/28) | 8000000 | PRIMARY CLARIFIERS | RAIN 1.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-10-31 | 10:00 - 13:45 | 1700000 | PRIMARY EFFLUENT | RAIN 0.29" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-02 | 11:51A - 12:45P | 500 | LATERAL CONNECTION 2317E 35TH | WET SPOT OBSERVED IN YARD - FLOW RUNNING INTO DITCH | EMERGENCY REPAIR ORDERED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-07 | 06:15 - 10:15 | 2900000 | PRIMARY EFFLUENT | RAIN 0.49" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-11 | 01:55 - 02:40 | 100000 | RAW WET WELL | RAIN 0.43" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-11 | 01:30 - 04:45 | 1500000 | PRIMARY EFFLUENT | RAIN 0.43" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-15 | 11/15 - 11/17 | 13000000 | PRIMARY EFFLUENT | RAIN 1.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-15 | 11/15 & 11/16 | 1500000 | RAW WET WELL | RAIN 0.79", PARTIAL PUMP BLOCKAGE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-15 | 11/15 & 11/16 | 4100000 | RAW WET WELL | RAIN 1.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-16 | 7:00A - 8:30 | 1000000 | RAW EFFLUENT | EQUIPMENT FAILURE, CLOGGED PUMP | REMOVED DEBRIS FROM PUMP
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-16 | 10:45 - 10:50 | 5000 | OVERFLOW OF BIOTOWERS | RAIN 0.79", HIGH FLOW BACKED UP IN CHANNEL
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-26 | 4:00P - 7:30P | 500 | PRIVATE SEWER - SANDOR DEVELOPMENT - PARKING LOT | SEWER BLOCKAGE | TO FOLLOW UP TO ENSURE SYSTEM OPERATING PROPERLY
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-30 | 10:30P - | 200000 | CSO 003 NORTH SHORE | RAIN 2.9", DEBRIS IN MAIN WWTP LIFT STATION, POWER FAILURES | PREVENTIVE MAINTENANCE ON LIFT STATION PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-30 | 10:05 - 24:00 | 4500000 | RAW WET WELL | RAIN 2.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-11-30 | 09:20 - 24:00 | 11500000 | PRIMARY EFFLUENT | RAIN 2.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 9:30P - 10:50P | 5500 | MANHOLE 4600 MADISON | EQUIPMENT FAILURE WHILE CLEANING SEWER | REMOVE BLOCKAGE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 19:00 - 19:30 | 42000 | NORTH BIO TOWER | RAIN 2.9" - HIGH FLOW | CYCLE SCREW PUMPS AS NECESSARY
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 06:30 - 18:00 | 50000 | SANITARY SEWER 4412 KEVON | RAIN 2.9" | PREVENTIVE MAINTENANCE TO SEWER SYSTEM IN THIS AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 06:30 |  | SANITARY SEWER 4412 KEUON | RAIN 2.9" | CLEAN / JET SEWER
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 00:00 - 00:00 | 18500000 | RAW WET WELL | RAIN 3.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 08:00 - 09:00 | 500 | EASTERN LIFT STATION | 3" | PREVENTIVE MAINTENANCE ON LIFT STATIONS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 12/1 - 12/2 | 21000000 | PRIMARY EFFLUENT | RAIN 3.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 07:00 - 07:35 | 1000 | MANHOLE CHESTERFIELD LIFT STATION | RAIN 2.9" | PREVENTIVE MAINTENANCE ON LIFT STATION PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-01 | 02:47 - 06:30 | 3000 | 5TH & SYLVAN | RAIN 2.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-02 | 00:00 - 21:00 | 28000000 | RAW WET WELL | RAIN 3.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-03 | 00:00 - 10:00P | 5800000 | PRIMARY CLARIFIERS | RAIN 2.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-04 | 3:30P - 3:35P | 40000 | PRIMARY CLARIFIERS | RAIN, MELTING SNOW & ICE | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-08 | 12/8 | 10000 | CSO 009 LOUISE ST | A LARGE WATER MAIN BUSTED CAUSING CSO OVERFLOW | REPAIRS MADE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-12 | 9:25A - 2:50A (12/13) | 13500000 | 005 DEWEY STREET PRIMARY BYPASS | RAIN 0.98" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-12 | 1:12P - 8:30P | 2100000 | 006 DEWEY STREET RAW SEWAGE BYPASS | RAIN 0.98" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-21 | 12/21 - 12/22 | 9000000 | PRIMARY EFFLUENT | RAIN 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-22 | 00:00 - 00:00 (12/23) | 8000000 | PRIMARY EFFLUENT | RAIN 1.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-22 | 18:00 - 23:00 | 2000000 | HIGH FLOW BLINDED FILTERS (FILTER BYPASS) | RAIN 1.5" | WATCH CYCLING OF SCREW PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-22 | 16:30 - 17:15 | 2000 | NORTH BIO TOWER | RAIN 1.5" - HIGH FLOW CAUSED BIO TOWER TO OVERFLOW | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-23 | 00:00 - 01:30 | 240000 | PRIMARY EFFLUENT | RAIN 1.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-25 | 14:55 - 18:00 | 6000000 | RAW WET WELL | RAIN 0.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-25 | 14:10 - 0000 (12/25) | 18500000 | PRIMARY EFFLUENT | RAIN 0.8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-26 | 12/26 - 12/27 | 13000000 | 005 DEWEY STREET PRIMARY BYPASS | RAIN 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-26 | 16:45 - 17:00 | 110000 | HIGH FLOW CAUSED BIO TOWERS TO OVERFLOW | RAIN 0.8" | VFP ADJUSTMENTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-26 | 13:30 - 13:30 (12/27) |  | HIGH FLOW BLINDED FILTERS (FILTER BYPASS) | RAIN 0.8" | VFP ADJUSTMENTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-29 | 13:15 - 16:00 | 3000000 | BYPASS TERTIARY PLANT | FOR THE FILTER REHAB PROJECT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-31 | 07:05 - 24:00 | 21000000 | PRIMARY EFFLUENT | RAIN 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-31 | 07:30 - 23:45 | 14000000 | RAW WET WELL | RAIN 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-31 | 09:08 - 09:10 | 100 | 5TH & SYLVAN | RAIN 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-31 | 05:00 - 05:15 | 1000 | OVERFLOW OF BIO TOWERS | RAIN 1.6" | CYCLE SCREW PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2006-12-31 | 02:45 - 10:00 | 1000 | SSO 1021 N 300 E | RAIN 1.2", PUMPS PLUGGED | CLEAN BOTTOM OF THE ANDERSON SIDE WET WELL
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2006-07-06 | 3:00P - 9:30A (7/7) | 670000 | PARTIAL TERTIARY FILTER BYPASSED | MECHANICAL FAILURE OF AUTOMATIC VALVE IN TERTIARY FILTER SYS | HAVE BEGAN ANNUAL MAINT ON TERTIARY FILTERS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2006-12-15 | 5:00P - 7:30P | 50000 | MANHOLE BY 19TH ST BRIDGE | SEWER CLOGGED | ADDED LINE TO SEWER CREW HOT LIST OF WEEKLY CHECKS
IN0049026 | FALL CREEK RSD STP | MADISON | 2006-12-01 | 12/1 | 15000 | US 36, PENDLETON MAIN, CR 100 LIFT STATIONS | RAIN 4", EQUIPMENT & POWER FAILURE
IN0020087 | LAPEL MUNICIPAL STP | MADISON | 2006-01-30 | 12:30P - 6:00P | 110000 | HEADWORKS | RAIN 0.55", EQUIPMENT FAILURE | REBUILDING PLANT
IN0053627 | RESTING WHEELS M.H.P. | MADISON | 2006-11-27 | 11/27 | 30 |  | CLEANING CLOGGED PUMP, SLUDGE DISCHARGED TO GROUND
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-02 | 7:54P - 2:45P (1/3) | 26000 | 7002 FALL CREEK RD, LS 403 | RAIN 0.75", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-03 | 1:00P - 4:00P | 3700000 | RAW EFFLUENT OVERFLOW FROM CSO 008 | COMMUNICATION RAW PUMP CONTROLLER FAILURE | STILL INVESTIGATING
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-04 | 11:24A - 1:05P | 4933 | 300 UNIVERSITY BLVD, CSO 038 | SEWER BLOCKAGE, SEWER CLEANED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-12 | 10:46A - 3:40P | 14360 | 4352 MITTHOEFER RD | SEWER PIPE COLLAPSE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-13 | 11:54A - 03:40A (1/14) | 15000000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW RESULT OF HIGH FLOW DURING WET WEATHER | TREATED MAXIMUM FLOW THROUGH FACILITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-13 | 9:30A - 12:15P | 98000 | 7002 FALL CREEK RD, LS 403 | RAIN 1", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-17 | 12:00A - 11:55P | 8480000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW RESULT OF HIGH FLOW DURING WET WEATHER | TREATED MAXIMUM FLOW THROUGH FACILITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-17 | 5:19P - 5:30P | 10000 | 7002 FALL CREEK RD, LIFT STATION 403 | RAIN 1", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-01-29 | 11:03A - 12:30P | 850 | 7002 FALL CREEK RD, LS403 | RAIN 1.0", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-02 | 7:26P - 4:25A (2/3) | 15796 | 7002 FALL CREEK RD, LS403 | RAIN 1", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-02 | 7:55P - 6:30A (2/3) | 8389000 | PRIMARY EFFLUENT OVERFLOW | RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-03 | 11:16P - 11:29P | 9000 | 6514 CREEKSIDE LN, LS 405 | RAIN 1", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-04 | 1:30P - 8:45P | 7480000 | PRIMARY EFFLUENT OVERFLOW | RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-06 | 4:12P - 5:00P | 13000 | 6514 CREEKSIDE LN, LS 405 | ELECTRICAL CONTROL CKT PROBLEM | REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-07 | 11:28A - 1:31P | 1202 | 3349 SUTHERLAND AVE, CSO 065 | MECHANICAL FAILURE AT CONTROL STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-08 | 1:27P - 2:22P | 54 | 1300 E 86TH ST | GREASE BLOCKAGE IN SEWER LINE, CLEANED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-10 | 10:23A - 2:00P | 212 | 10041 ELLIS DR | DEBRIS CAUSING SEWER BLOCKAGE | CLEANED SEWER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-14 | 10:47A - 12:47P | 703 | 5908 LAKESIDE MANOR AVE | GREASE CAUSING SEWER BLOCKAGE | CLEANED SEWER, FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-15 | 1:30P - 3:40P | 127 | 11427 FAIRPORT CIR | GREASE CAUSING SEWER BLOCKAGE | CLEANED SEWER, FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-16 | 1:35P - 3:00P | 500 | 7450 S FRANKLIN RD | LS ARV FAILURE | LIFT STATION REPAIRED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-18 | 4:30P - 6:30P | 117 | 8463 SLIPPERY ELM CT | GREASE BLOCKAGE IN SEWER | CLEANED SEWER BLOCKAGE, FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-24 | 10:00A - 11:20A | 78 | 6132 NELSON PL | SEWER BLOCKAGE, DEBRIS | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-02-25 | 12:04P - 2:45P | 157 | 1637 MCCOLLOUGH DR | DEBRIS IN SEWER, CLEANED BLOCKAGE FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-07 | 7:40P - 11:14P | 1672 | 5420 DANDY TRAIL, LS 113 | LS FORCE MAIN RUPTURE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-08 | 3/8 - 3/11 | 124129000 | PRIMARY EFFLUENT OVERFLOW | WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-09 | 12:46A - 2:39A | 110 | 8104 BARRY RD | ROOTS IN SEWER | CLEAN SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-09 | 8:08P - 8:30P (3/10) | 37800 | 7002 FALL CREEK RD, LS403, SSO 105 | RAIN 3", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-09 | 6:21P - 11:22P | 5881 | 2244 ADMIRAL DR | DEBRIS IN SEWER, CLEANED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-09 | 9:31P - 12:15P (3/10) | 17271 | 2593 HARLAN ST | WET WEATHER I&I
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-09 | 3:55P - 4:47P (3/12) | 172000 | 8400 WOODBURN DR, LS115, SSO 113 | RAIN 2.25", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-09 | 7:00P - 7:50A (3/10) | 120000 | 6514 CREEKSIDE LN, LS405, SSO 124 | RAIN 2.5", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-09 | 12:30P - 4:45P | 1495 | 5455 CAMDEN ST | DEBRIS IN SEWER | CLEANED SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-10 | 11:39A - 2:30P | 12528 | 5520 S STATE AVE | WET WEATHER I&I | NO CLEANUP NECESSARY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-10 | 2:40P - 2:41P | 150 | 2600 S KEYSTONE | WET WEATHER I&I | REMOVED DEBRIS
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-10 | 4:10P - 4:11P | 200 | 1830 WINCHESTER DR | WET WEATHER I&I | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-10 | 3/10 - 3/13 | 200 | 1830 WINCHESTER DR | WET WEATHER I&I CONTRIBUTION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-11 | 3/11 - 3/14 | 161000000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-11 | 12:22P - 7:30P | 24000 | 7002 FALL CREEK RD, LS403, SSO 105 | RAIN 2.5", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-12 | 4:00P | 100 | 626 FRONT ROYAL DR | WET WEATHER I&I CONTRIBUTION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-12 | 4:15A - 11:50P | 415000 | 6514 CREEKSIDE LN, LS405, SSO 105 | RAIN 2.25", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-14 | 3:50A - 4:48A | 717000 | 7002 FALL CREEK RD, LS403, SSO 105 | RAIN 3.5", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-16 | 12:00P - 2:29P | 291 | 8300 CRAIG ST | ROOTS, CLEANED SEWER BLOCKAGE, FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-23 | 1:00P - 4:00P | 176 | 8451 CHRISTIANA LN | SEWER BLOCKAGE (DEBRIS), CLEANED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-27 | 10:30A | 50 | 3508 WOODCLIFT DR | WET WEATHER I&I CONTRIBUTION | REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-27 | 9:00A - 11:11A | 2559 | 4352 N MITTHOFFER RD | SEWER BLOCKAGE, GREASE | CLEANED SEWER BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-29 | 1:35P - 1:55P | 391 | 7000 FALL CREEK RD, LS 403 | LS POWER FAILURE | REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-31 | 12:00P - 5:00A (4/1) | 25220000 | PRIMARY EFFLUENT OVERFLOW | HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-31 | 11:16P - 4:09A (4/1) | 286 | 8065 HOPKINS LN | SEWER BLOCKAGE, DEBRIS | CLEANED SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-03-31 | 9:51A - 5:00A (4/1) | 113000 | 7002 FALL CREEK RD, LS403, SSO 105 | RAIN 2", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-02 | 9:20P - 6:50A (4/3) | 127000 | 7002 FALL CREEK RD, LS403, SSO 105 | RAIN 1.5", LS WET WEATHER CAPACITY | REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-03 | 12:48P - 12:55P | 2735 | 10802 E TROY AVE, LS313 | RAIN 2", # 2 VFD WAS TRIPPED OUT | REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-03 | 5:37A - 7:55A | 1348 | 9245 SANDBURY RD, LS443 | LS POWER FAILURE | REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-06 | 5:51P - 1:00A (4/7) | 4191 | 5701 MCFARLAND RD, LS 317 | PRIVATE CONTRACTOR DAMAGED FORCE MAIN | EXCAVATE & REPAIR SEWER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-07 | 11:03P - 1:15A (4/8) | 3224 | 6404 MCFARLAND RD, LS 317 | PRIVATE CONTRACTOR DAMAGED - SEWER BLOCKAGE | USED PUMP TRUCK TO HOLD DOWN FLOW, REMOVE DEBRIS
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-08 | 8:05P - 9:00P | 100 | 6815 KNOLLCREEK DR, LS442 | LIFT STATION IN NEED OF REPAIR | FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-09 | 9:10P - 11:45P | 454 | 8065 HOPKINS LN | SEWER BLCOKAGE, CLEANED BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-10 | 3:28P - 4:45P | 1504 | 940 MEIKEL ST, CSO116 | DEBRIS CAUSING SEWER BLOCKAGE, CLEANED | FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-10 | 2:40P - 6:21P | 432 | 3919 COOPER RD | SEWER BLCOKAGE, CLEANED BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-11 | 10:58A - 1:00P | 358 | 940 MEIKEL ST, COS 116 | METAL PLATE BLOCKING DIVERSION | CLEAN SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-13 | 4:49P - 9:50P | 5881 | 5820 FORTUNE CIR W | GREASE IN SEWER | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-14 | 9:30P - 8:00P (4/15) | 270000 | 7002 FALL CREEK RD, LS403 | RAIN 2", LS WET WEATJER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-14 | 4:35A - 4:50A | 15000 | PRIMARY EFFLUENT OVERFLOW | RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-15 | 1:42A - 9:30P | 31000 | 6514 CREEKSIDE LN - LS405 | RAIN 2", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-15 | 3:04P - 6:26P | 3946 | 6815 KNOLL CREEK DR - LS442 | RAIN 2", LS WET WEATHER CAPACITY | FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-15 | 9:55A - 3:34P | 9935 | 1016 COUNTRY CLUB RD | WET WEATHER I/I CONTRIBUTION | REMOVE DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-15 | 10:55A - 5:30P | 77171 | 10802 E TROY AVE - LS313 | RAIN 2", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-15 | 4:59P - 8:00P | 177 | 9618 MERCURY DR | SEWER BLOCKAGE - DEBRIS | CLEARED BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-15 | 10:14A - 3:34P | 9378 | 2236 COUNTRY CLUB RD | WET WEATHER I/I CONTRIBUTION | REMOVE DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-16 | 12:30P - 3:00P | 440 | 8018 WINDHAM LAKE WAY | SEWER BLOCKAGE - DEBRIS | CLEARED BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-16 | 10:15P - 01:00A (4/18) | 25990000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW IS THE RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-17 | 12:52A - 11:00A (4/18) | 460000 | 7002 FALL CREEK RD - LS403 - SSO 105 | RAIN 2", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-18 | 3:36P - 3:45P | 18 | 4772 E PLEASANT RUN PKY N | SEWER BLOCKAGE - DEBRIS | CLEARED BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-18 | 9:23P - 8:45A (4/19) | 33311 | 6828 CABERNET WAY - LS201 | LS FORCE MAIN RUPTURE | EXCAVATE & REPAIR SEWER, REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-19 | 10:38A - 6:10P | 442 | 5400 DANDY TRAIL - LS 95006 | PRIVATE CONTRACTOR DAMAGE | EXCAVATE & REPAIR SEWER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-19 | 7:49A - 8:47A | 113 | 972 E PLEASANT RUN PKY M | SEWER BLOCKAGE - DEBRIS | REMOVED DEBRIS
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-19 | 11:46A - 6:10P | 375 | 5190 DANDY TRAIL - LS113 | LS FORCE MAIN RUPTURE | EXCAVATE & REPAIR SEWER, REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-04-22 | 1:48P - 4:30P | 633 | 3643 CEDAR PINE PL | DEBRIS CAUSING SEWER BLOCKAGE | CLEANED SEWER BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-02 | 4:43A - 5:00A | 571000 | PRIMARY EFFLUENT OVERFLOW | RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-06 | 10:07A - 11:59A | 100 | 940 MEIKEL ST, CSO 116 | SUDDEN BURST OF CUSTOMER SLUG FLOW | UNABLE TO LOCATE FROM WHERE FLOW ORIGINATED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-07 | 1:28P - 6:39P | 50 | 7600 W 56TH ST, LS 112 | FORCE MAIN RUPTURE | REMOVED DEBRIS, USED PUMP TRUCK TO HOLD FLOW
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-07 | 7:45A - 9:25A | 98 | 7118 TAPPAN DR | FLOATS RIDING ON GREASE IN LIFT STATION | REMOVED DEBRIS, REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-08 | 7:48P - 8:40P | 51 | 9119 WARWICK RD | DEBRIS CAUSING SEWER BLOCKAGE | CLEANED SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-10 | 23:35 - 23:45 |  | PRIMARY EFFLUENT OVERFLOW | RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-12 | 6:00P - 7:28P | 1719 | 750 GREEN WOODS DR, LS 102 - SPEEDWAY WOODS SUB | LIFT STATION POWER FAILURE | REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-13 | 2:40P - 18:00 | 10030000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW IS A RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-14 | 8:40A - 10:40 | 300000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW IS A RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-17 | 9:14A - 10:00A | 135 | 3604 E HANNA AVE | DEBRIS CAUSING SEWER BLOCKAGE | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-18 | 6:15A - 20:50 | 5200000 | PRIMARY EFFLUENT OVERFLOW | RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-05-30 | 9:00A - 10:06A | 64 | 2102 ORANGE ST - CSO 106 | SENSOR BAND DETATCHED & BECAME LODGED IN REGULATOR | CLEARED SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-02 | 3:15A - 8:00P (6/3) | 287000 | 7002 FALL CREEK RD - LS 403 - SSO 105 | RAIN 0.5", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-02 | 1:30A - 1:40A (6/3) | 50420000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW IS A RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-02 | 1:41P - 6:01P | 150 | 1300 E 86TH ST | GREASE BLOCKAGE IN SEWER | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-14 | 2:00P - 2:05P | 10 | 3839 COOPER LN | SEWER BLOCKAGE | CLEANED SEWER BLOCKAGE, FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-14 | 1:30P - 9:30P | 50 | 8701 HAGUE RD | LIFT STATION FORCE MAIN RUPTURE | EXCAVATE & REPAIR SEWER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-16 | 4:10A - 4:35A | 24 | 5313 PATRICIA ST | SEWER BLOCKAGE - GREASE | CLEANED SEWER BLOCKAGE, REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-18 | 9:15P - 11:47P (6/19) | 4665 | 8125 SARGENT RIDGE | LIFT STATION POWER FAILURE | REMOVED DEBRIS FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-18 | 4:00A - 10:23P | 21549 | 7002 FALL CREEK RD - LS 403 (SSO 105) | RAIN 1", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-21 | 10:45A - 3:00P | 249 | 4250 BRAEMAR DR | LS ARV FAILURE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-23 | 7:26P - 7:36P | 10 | 8639 BAY COLONY DR - LS 111 | TX LINE DOWN, BOTH PUMPS HAD FAILED | REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-06-24 | 11:00P - 2:21A | 9817 | 8018 WINDHAM LAKE WAY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-07-10 | 10:32P - 12:01A (7/11) | 4347 | 6850 W 86T ST - LS135 | LS POWER FAILURE | RESET PUMPS, STATION OPERATING PROPERLY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-07-11 | 10:53A - 11:00A | 1000 | 7002 FALL CREEK RD - LS403 | RAIN 1", LS WET WEATHER CAPACITY | CHECK STATION MAKE SURE IT WAS DOING ALL THAT IT COULD
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-07-11 | 12:55P - 10:00P | 18203000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW IS A RESULT OF HIGH FLOW DURING WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-07-15 | 12:23P - 2:15P | 1000 | CSO 084 - 5301 E ST CLAIR ST | BLOCKAGE IN LINE | REMOVED DEBRIS AND JETTED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-07-18 | 2:20P - 3:00P | 500 | 7602 WALNUT POINT RD, LS 122 | CONTRACTOR HIT & DAMAGED FORCE MAIN | AREA CLEANED & DEBRIS REMOVED
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-07-24 | 12:28P - 2:18P | 537 | 1600 N KEALING AVE - CSO 101 | DEBRIS CAUSING SEWER BLOCKAGE | CLEANED BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-07-25 | 10:10A - 10:34A | 234 | 3200 FALL CREEK PKWY NDR - CSO 063 | DEBRIS CAUSING SEWER BLOCKAGE | CLEANED BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-08-02 | 10:48A - 11:11A | 90 | 918 MEIKEL ST - CSO 116 | CUSTOMER SLUG LOAD
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-08-06 | 3:47P - 4:00P | 508 | MANHOLE OVERFLOW - 8635 ADMIRALS WOODS DR - LS 563 | LIFT STATION POWER FAILURE - IPL TRANSFORMER | REPAIR LIFT STATION, REMOVE DEBRIS
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-08-17 | 9:42P - 10:00P | 879 | MANHOLE - LIFT STATION 6850 W 86TH ST | LIFT STATION FAILURE | REPAIRED LIFT STATION, REMOVE DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-08-21 | 2:32P - 4:00P | 86 | 5115 ROCKVILLE RD | SEWER BLOCKAGE - GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-08-30 | 7:20A - 1:30P | 2000 | 8055 GUNNERY CIR - LS 135 | PRIVATE CONTRACTOR DAMAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-09-16 | 11:13P - 12:10A (9/17) | 1114 | 12131 ADMIRALS POINTE CIR - LS 562 | LS PUMP FAILURE | REPAIR LIFT STATION, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-09-16 | 1:48P - 3:41P | 1104 | 6616 ROCKVILLE RD | SEWER BLOCKAGE | CLEANED SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-09-25 | 8:43A - 4:05P | 1295 | 5443 CAMDEN ST | PIPE COLLAPSE | EXCAVATE & REPAIR SEWER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-09-26 | 12:40P - 6:25P | 337 | 5350 KNOLLTON RD | GREASE | REMOVE DEBRIS, CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-10-01 | 9:26A - 10:13A | 400 | 9242 GLEANNLOCH DR, LS 444 | DUMPING OF POOL WATER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-10-17 | 8:15A - 8:25A | 733 | 7002 FALL CREEK RD - LS 403 | RAIN 0.75", LIFT STATION WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-10-27 | 2:52P - 8:13P | 4704 | 7002 FALL CREEK RD - LS 403 | RAIN 1", LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-10-27 | 2:15P - 6:00A (10/28) | 37011111 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-10-28 | 1:50P - 2:39P | 1197 | 1830 WINCHESTER DR | WET WEATHER I&I CONTRIBUTION | FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-01 | 1:07P - 2:30P | 50 | 5218 KEYSTONE CT | SEWER BLOCKAGE - DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-01 | 12:15P - 4:30P | 1000 | 2629 PLAZA DR | SEWER BLOCKAGE - GREASE | CLEAN SEWER BLOCKAGE, EXCAVATE SOIL
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-02 | 1:49A - 3:44A | 15190 | 800 E WASHINGTON ST - CSO A38 | SEWER BLOCKAGE - DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-03 | 11:30A - 4:45P | 308 | 7601 W 56TH ST - LS 112 | LS FORCE MAIN RUPTURE | REPAIRED FORCE MAIN
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-08 | 12:42P - 2:48P | 123 | 7901 MADISON AVE | PIPE COLLAPSE | EXCAVATE & REPAIR SEWER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-10 | 5:00P - 8:45P | 440 | 10220 PINENEEDLE CT | SEWER BLOCKAGE - DEBRIS | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-11 | 01:15A - 3:30A | 5600000 | RAW 008 | LEAVES COMING IN FASTER THAN BAR SCREEN COULD HANDLE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-12 | 1:09P - 8:44P | 444 | 1515 CRUFT ST | SEWER BLOCKAGE - DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-13 | 1:32P - 1:51P | 37 | 261 W 25TH ST | DEBRIS | REMOVED DEBRIS FROM EQUIPMENT
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-16 | 6:24A - 1:30P (11/17) | 32120000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW IS THE RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-16 | 7:45A - 1:43P | 5246 | 7002 FALL CREEK RD - LS 403 | RAIN 1.25", LS WET WEATHER CAPACITY | LIFT STATION CHECKED, BOTH PUMPS RUNNING AT CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-17 | 5:32P - 5:30P | 100 | 3812 W 71ST ST - LS 128 | GREASE | REMOVE DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-24 | 3:00P - 6:57P | 46303 | 1016 COUNTRY CLUB RD | SEWER BLOCKAGE, DEBRIS | CLEANED SEWER BLOCKAGE, REMOVE DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-27 | 8:40P - 12:16A (11/28) | 5275 | 5835 MADISON AVE | SEWER BLOCKAGE, GREASE | CLEANED SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-30 | 9:50P - 4:00A (12/1) | 200000 | 7002 FALL CREEK RD - LS 403 (SSO 105) | RAIN 2" - LIFT SSTATION WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-11-30 | 3:25P - 2:30A (12/2) | 96840000 | PRIMARY EFFLUENT OVERFLOW | RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-01 | 8:00A - 8:15A | 2000 | 8242 SHAFTER RD - LS 402 | LIFT STATION INSTRUMENTATION FAILURE | REPAIRED EQUIPMENT AND CLEANED DEBRIS FROM AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-01 | 8:56P - 10:55P | 2325 | 9245 SNADBURY RD - LS 443 | RAIN 2" - LIFT STATION POWER FAILURE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-01 | 11:33A - 7:06P | 22126 | MANHOLE - 3122 N RICHARDT AVE | DEBRIS BLOCKAGE IN SEWER | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-01 | 7:48A - 12:30P | 945000 | 2400 COUNTRY CLUB RD - LS 115 (SSO 113) | RAIN 2" - LIFT STATION WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-01 | 3:38A - 9:15A | 111000 | 6514 CREEKSIDE LN - LS 405 (SSO 124) | RAIN 2" - LIFT STATION WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-02 | 4:31P - 6:30P | 2325 | 1237 BUTTERNUT LN - LS 147 | LIFT STATION POWER FAILURE
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-02 | 2:48P - 2:51P | 147 | 8455 E 96TH ST | LIFT STATION FAILURE | REPAIR LIFT STATION, REMOVED DEBRIS
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-03 | 4:24P - 6:30P | 510 | 7118 TAPPAN DR - LS 128 | GREASE BLOCKAGE IN SEWER | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-03 | 9:30A - 10:13A | 420 | MANHOLE - 7722 TARDELLI LN | DEBRIS BLOCKAGE IN SEWER | CLEAN SEWER BLOCKAGE, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-12 | 11:30A - 8:30P | 18200000 | BELMONT RAW OVERFLOW (008) | RAIN
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-12 | 1:52P - 2:40A (12/13) | 3300000 | PRIMARY EFFLUENT OVERFLOW | OVERFLOW RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-12 | 7:11P - 9:54P | 1000 | 7002 FALL CREEK RD - LS 403 - SSO 105 | RAIN 1.5" - LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-14 | 10:58A - 12:26P | 4298 | 10202 JOHN JAY DR | SEWER BLOCKAGE, GREASE | CLEAN SEWER BLOCKAGE, REMOVED DEBRIS FLUSHED AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-16 | 3:35P - 3:57P | 5000 | 10802 E TROY AVE, LIFT STATION 313 | LIFT STATION PUMP FAILURE | REPAIRED LIFT STATION
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-26 | 12:36A - 1:03A | 528 | 7002 FALL CREEK RD - LIFT STATION 403 - SSO 105 | RAIN 1", LIFT STATION WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-27 | 11:26A - 1:20P | 557 | 980 WESTERN DR | DEBRIS BLOCKAGE IN SEWER | CLEARED BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-27 | 7:53P - 11:00P | 183 | 8067 HOLLYBROOK CT | LIFT STATION PUMP FAILURE | USE PUMP TRUCK TO HOLD DOWN FLOW
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-28 | 4:00P - 7:05P | 3614 | 1888 RESEARCH WAY | CONSTRUCTION DEBRIS FROM NEW BUILDINGS IN MANHOLE | CLEARED BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-31 | 12:00P - 10:40A (1/1) | 49200000 | PRIMARY EFFLUENT OVERFLOW | RESULT OF WET WEATHER
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-31 | 10:17A - 12:15A (1/1) | 3000 | 6514 CREEKSIDE LN - LS 405 - SSO 124 | RAIN 2" - LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-31 | 9:40A - 12:45A (1/1) | 3000 | 7002 FALL CREEK RD - LS 403 - SSO 105 | RAIN 2" - LS WET WEATHER CAPACITY
IN0023183 | INDIANAPOLIS-BELMONT MUN. STP | MARION | 2006-12-31 | 1:00P - 12:14A (1/1) | 658 | 6301 LANDBOROUGH SDR - LS 405 | RAIN 2" - LS WET WEATHER CAPACITY | REMOVED DEBRIS, FLUSH AREA
| LAWRENCE SEWER DEPARTMENT | MARION | 2006-12-01 | 12/1 |  | MANHOLES 46TH & POST RD, 7600 E 53RD ST | RAIN | REPORTED FTOM IDEM ER
| TRI-COUNTY CONSERVANCY DIST | MARION | 2006-01-14 | 9:00A - 12:30P | 21000 | MANHOLE LIFT STATION 9117 HEARTLAND BLVD | RAIN 2.5", PUMP FAILURE | PLAN ON HAVING TRASH PUMP IN STOCK
IN0022438 | BOURBON MUNICIPAL STP | MARSHALL | 2006-08-28 | 6:08P - 10:30P | 9200 | LIFT STATION SSO # 3 | RAIN >3" | PLANNING PUMP UPGRADES
IN0021288 | CULVER MUNICIPAL STP | MARSHALL | 2006-01-10 | 8:00A - 8:30 | 2000 |  | PLUG IN SEWER LINE, JETTED SEWER
IN0021288 | CULVER MUNICIPAL STP | MARSHALL | 2006-02-10 | 11:30P - 8:40A (2/11) | 10000 | TWO MANHOLES ON WASHINGTON ST | GREASE CLOGGING SEWER LINE | JETTED SEWER LINE
IN0021288 | CULVER MUNICIPAL STP | MARSHALL | 2006-02-20 | 10:30 - 12:30 | 5000 | MANHOLE | GREASE PLUGG, JETTED LINE
IN0021288 | CULVER MUNICIPAL STP | MARSHALL | 2006-06-15 | 7:30 - 12:15 | 60000 | SEWER MAIN - SLATER | BORING WATER LINE - RAN THROUGH SEWER LINE
IN0021288 | CULVER MUNICIPAL STP | MARSHALL | 2006-08-08 | 9:35 - 9:45 | 1000 | MANHOLE OVERFLOW | CONSTRUCTION OF NEW SEWER, BYPASS PUMP QUIT WORKING | HAVE ANOTHER BACKUP PUMP
IN0021288 | CULVER MUNICIPAL STP | MARSHALL | 2006-10-03 | 3:00P - 6:00P | 60000 | MAIN LINE WHERE THEY WERE FIXING ROAD | COLAPSED MAIN LINE | REPLACE SEWER MAIN
IN0039241 | LOOGOOTEE, TOWN OF | MARTIN | 2006-01-13 | 10:30A - 11:15A |  | 4" CLEANOUT AT SHADED EST TR CT | FOUND BROKEN CLEANOUT DURING SYSTEM SURCHARGE | INSERT 4" AIR PLUG, TO REPAIR CLEANOUT
IN0039241 | LOOGOOTEE, TOWN OF | MARTIN | 2006-03-09 | 3/9, 3/11 - 3/12 |  | MANHOLES 21, 163, 156, 159 & LS 3 | RAIN 6.9"
IN0039241 | LOOGOOTEE, TOWN OF | MARTIN | 2006-04-27 | 11:00 - 11:10 | 100 | LIFT STATION AT WWTP | LIFT STATION OVERFLOWED DURING LAND APPLICATION OF SLUDGE | LABEL VALVING & MONITOR
IN0039241 | LOOGOOTEE, TOWN OF | MARTIN | 2006-07-12 | 4:30P - 7:30A (7/13) | 100000 | WWTP SLUDGE THICKENER | OPERATOR ERROR - AFTER WASTING, VALVE FELT & APPEARED TO BE CLOSED | CLEANED SPILL, EVALUATING CAUSE, REVISE OPERATOR PROCEDURES
IN0039241 | LOOGOOTEE, TOWN OF | MARTIN | 2006-10-17 | 06:00 - 08:00 | 200000 | RETENTION BASIN | RAIN 2.4"
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-01-13 | 11:40A - 2:40P | 45000 | MANHOLE # 1002 | ANOMALY IN POWER SYSTEM CAUSED MAIN BREAKER IN PUMPS TO TRIP | ELECT & PUMPS WILL BE CHECKED FOR PROBLEMS
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-03-08 | 3/8 - 3/9 |  | MANHOLE 1002, TERTIARY FILTERS | RAIN 2.12" | CHECKING SEWERS FOR I&I
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-03-09 | 3/9 - 3/10 |  | SEDIMENTATION PONDS 002 & 003 OVERFLOWING | RAIN 4.8" | CORRECTIVE MEASURES TO BE IMPLEMENTED
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-03-09 | 3/9 - 3/15 |  | SEDIMENTATION POND 3A / OUTFALL 003 | RAIN 7.7" | CORRECTIVE MEASURES TO BE IMPLEMENTED
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-03-11 | 3/11 - 3/12 |  | SEDIMENTATION POND 2 | RAIN 1.7" | WORKING TO CORRECT
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-03-12 | 3/12 - 3/13 |  | TERTIARY FILTERS & MANHOLE 1002 | RAIN 1.24" | CHECKING SEWER LINES FOR I&I
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-08-28 | 10:00A - 7:10P |  | TERTIARY / FILTER - PARTIALLY TREATED RELEASE | RAIN 3.3" | CHECKING SEWER LINES FOR INFILTRATION
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-10-17 | 00:45 - 10:00 |  | MANHOLE 1002, TERTIARY FILTER | RAIN 2.7", FILTER BYPASS TO PREVENT FLOODING (CONTROL BUILDING) | CHECKING SEWER LINES FOR INFILTRATION, DAMAGED LINES REPAIRED
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-10-17 | 01:00 - 18:00 |  | TERTIARY / FILTER | RAIN 2.7", BYPASS OF TERTIARY FILTER TO PREVENT FLOODING | CHECKING SEWER LINES FOR INFILTRATION
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-11-30 | 11/30 - 12/1 | 138000 | MANHOLE 1002, TERTIARY FILTER | RAIN 2.74" | CHECKING SEWER LINES FOR I&I
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-12-12 | 12:30 - 08:10 | 558000 | MANHOLE 1002, TERTIARY FILTER | RAIN 2.07", BYPASS TO PREVENT FLOODING OF CONTROL BUILDING | CHECKING SEWER LINES FOR I&I
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2006-12-22 | 05:00 - 06:00 (12/23) | 56250 | MANHOLE 1002, TERTIARY FILTER | RAIN 1.66" | CHECKING SEWER FOR I&I
IN0040631 | SHOALS MUNICIPAL STP | MARTIN | 2006-03-14 | 3/14 | 90000 | MAIN LIFT STATION | RAIN 7"
IN0039888 | CONVERSE MUNICIPAL STP | MIAMI | 2006-04-17 | 4/17 | 24000 | B-17 MANHOLE E WABASH & 4TH STREET | RAIN 1.8" | MANHOLE NEEDS REPAIR
IN0039888 | CONVERSE MUNICIPAL STP | MIAMI | 2006-08-11 | 1:00A - 7:45A |  | CLARIFIER | RAIN, ELECTRICAL STORM TRIPPED BREAKER ON # 2 CLARIFIER | CHECKING AUTOMATIC DIALER & ELECTRICAL EQUIPMENT
IN0039888 | CONVERSE MUNICIPAL STP | MIAMI | 2006-12-01 | 12/1 | 28800 | 4TH ST & WABASH ST | RAIN 1.75"
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2006-01-22 | 12:46P - 9:10P | 25650 | CSO 115 & 116 | PUMP FAILURE AT CASS STREET LIFT STATION
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2006-01-31 | 6:15P - 7:44P | 4450 | 116 TIPPECANOE CSO | EQUIPMENT FAILURE, PUL & PUMP FAILURE (NEW EQUIPMENT) | REPROGRAMING PUMP
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2006-02-01 | 08:00 - 10:30 |  | CSO 104 | PLUG IN SEWER LINE | NEW FLOW METERING BEING INSTALLED
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2006-02-02 | 4:47P - 5:12P |  | CSO 116, CASS ST LIFT STATION | # 1 PUMP FAILED | LOOKING TO FIX PROBLEM
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2006-02-18 | 11:59A - 1:55P | 1140 | 116 CSO, CASS ST LIFT STATION | EQUIPMENT FAILURE, PUMP
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2006-05-29 | 12:00 - 12:30 |  | CSO 014 | POSSIBLE PLUG OR FLOW RESTRICTION IN SEWER LINE | CREWS CHECKING CSO STRUCTURE FOR OBSTRUCTION
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2006-12-20 | 07:00 - 08:30 |  | CSO 005 | 12" WATER MAIN BREAK - DOMESTIC WATER RELEASED TO COLL SYS | MAIN IS BEING REPAIRED
| WOODLAND HILLS | MIAMI | 2006-04-17 | 6:00A - 11:00A |  |  | WORKING WITH ROTO-ROOTER TO CORRECT PROBLEM
IN0035726 | BLOOMINGTON N (BLUCHER POOLE) | MONROE | 2006-03-11 | 3/11 - 3/12 | 450000 | MANHOLES, RUSGAN/RAMBLE, CLUB HOUSE DRIVE | RAIN .51" | UNDER IDEM AGREED ORDER
IN0035726 | BLOOMINGTON N (BLUCHER POOLE) | MONROE | 2006-03-11 | 3/11 - 3/12 | 450000 | MANHOLES 9922 & 8926 / MH 3326 | RAIN 0.51" | AREA CLEANED OF DEBRIS
IN0035726 | BLOOMINGTON N (BLUCHER POOLE) | MONROE | 2006-03-13 | 10:10A - 9:45P | 500000 | MANHOLES RUSGAN/RAMBLE | RAIN .18" | UNDER IDEM AGREED ORDER
IN0035726 | BLOOMINGTON N (BLUCHER POOLE) | MONROE | 2006-04-20 | 12:30P - 12:45P | 1500 | MANHOLE WWTP DISCHARGE LINE | EQUIPMENT FAILURE | CLEAN UP AREA AROUND MANHOLE
IN0035726 | BLOOMINGTON N (BLUCHER POOLE) | MONROE | 2006-05-24 | 5:00P - 1:00P (5/25) | 370000 | ABANDONED ELLETSVILLE SEWER TO B P | INDIANA REMC DRILLED INTO A VACATED SEWER THAT WAS CAPPED
IN0035718 | BLOOMINGTON N (BLUCHER POOLE) | MONROE | 2006-07-21 | 11:20 - 2:50A (7/22) | 150295 | MANHOLE 6, 9922, 9926 & INDUSTRIAL LIFT STATION 4942 | RAIN 1.5" | AREAS CLEANED OF DEBRIS - UNDER IDEM AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-01-13 | 9:00A - 8:30P | 138712 | MANHOLE 3437 (GIFFORD RD) | RAIN 1.36" | AGREED ORDER WITH IDEM TO CORRECT
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-01-19 | 2:30P - 9:50A (1/20) | 42114 | MANHOLE 1949, 2357 | SEWER LINE BLOCKAGE | OPERATING UNDER AN IDEM AGRED ORDER (WET WEATHER MGT)
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-02-03 | 11:00A - 12:00P | 1770 | MANHOLE 1037 | EQUIPMENT FAILURE, AREA CLEANED OF DEBRIS | OPERATING UNDER IDEM AGREED ORDER, MANAGEMENT PLAN
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-03-01 | 10:00A - 10:30A | 900 | MANHOLE 3436 | ROOT CUTTER STUCK IN SEWER, IT HAD TO BE CUT OUT
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-03-08 | 3/8 | 131694 | MICRO MOTORS, 3RD & WALNUT, GIFFORD RD | RAIN 2.06" | OPERATING UNDER AN IDEM AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-03-09 | 3/9 - 3/10 | 2700176 | MANHOLES GRIMES LN, GIFFORD RD & COLLEGE MALL | RAIN 3.8" | OPERATING UNDER AN IDEM AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-03-09 | 3/9 - 3/10 | 2700176 | MANHOLES, GRIMES LN, GIFFORD RD, COLLEGE MALL RD | RAIN 3.8" | UNDER IDEM AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-03-11 | 3/11 - 3/12 | 6000000 | MANHOLES, MICRO MOTORS, GIFFORD RD, COLLEGE MALL RD | RAIN 3.34" | UNDER IDEM AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-03-12 | 7:45A - 8:25A | 31725 | SOUTHEAST DILLMAN MH 4742 | RAIN 2.1" | OPERATING UNDER AN IDEM AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-03-13 | 3/13 - 3/14 | 1000000 | MANHOLES, MICRO MOTORS, RUSGAN/RAMBLE, COLLEGE MALL RD | RAIN .61" | UNDER IDEM AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-04-06 | 5:05P - 7:00A (4/7) | 679785 | MH 6 GRIMES LN, MH 3437 GIFFORD RD, MH 9933 COLLEGE MALL | RAIN 1.44" | UNDER IDEM AO FOR WET WEATHER MANAGEMENT
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-04-07 | 7:00P - 9:00P | 11877 | MH 6 GRIMES LN, MH 3437 GIFFORD RD | RAIN 0.45", BOTH PUMPS DOWN AT THE SMITH AVE LIFT STATION | UNDER IDEM AO FOR WET WEATHER MANAGEMENT
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-06-07 | 11:00A - 12:00A | 14100 | INDUSTRIAL LIFT STATION WET WELL | RAIN 1.39" | UNDER IDEM AGREED ORDER TO RECTIFY
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-06-19 | 1:50A - 7:55A | 195758 | MICRO MOTORS - MH 6, STEELE CHIROPRACTIC - MH 9933 | RAIN 0.68" | AREA CLEANED OF DEBRIS, UNDER IDEM AGREED ORDER TO CORRECT
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-08-27 | 12:00A - 5:00A (8/28) | 18166 | INDUSTRIAL LIFT STATION WET WELL | RAIN 1.6" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-11-16 | 5:50A - 10:15A | 78000 | MANHOLES 6 & 3437 | RAIN 1.47" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-11-30 | 11/30 - 12/1 | 1811391 | MANHOLES - GRIMES LN, GIFFORD RD, COLLEGE MALL, S ROGERS | RAIN 2.5" - EQ BASIN LINER DAMAGED | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-12-01 | 8:45A - 10:15A | 21150 | MANHOLE 4742 | RAIN 1.8" - EQ BASIN LINER HAS BEEN DAMAGED | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-12-12 | 5:20P - 10:30P |  | GRIMES LN MH 6, GIFFORD RD MH 3437 | RAIN 1.28", EQ BASIN LINER DAMAGED | CONTRACTOR HIRED TO REPAIR LINER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2006-12-21 | 4:30P - 6:30P | 4566 | GIFFORD RD - MANHOLE 3437 | RAIN 1.26" | FACILITY OPERATING UNDER AN ENFORCEMENT ACTION TO ELIMINATE BYPASSING
| EASTERN RICHLAND SEWER CORP | MONROE | 2006-03-09 | 3/9 - 3/12 |  | MANHOLES 133, 169, 112, 103, 104 | RAIN 7.4" | TELEVISING LINES & REPAIRS
| EASTERN RICHLAND SEWER CORP | MONROE | 2006-07-21 | 11:30P - 12:30A (7/22) |  | MANHOLE 133 | RAIN 2.8" | TELEVISING & MAKING REPAIRS
IN0021083 | ELLETTSVILLE MUNICIPAL STP | MONROE | 2006-07-24 | 2:00A - 7:00A | 4000 | SMITHVILLE TELEPHONE LIFT STATION | EQUIPMENT FAILURE - DISCHARGE PIPE BROKEN OFF LS | CLEARED AREA WITH VAC-TRUCK
| INDIANA UNIVERSITY | MONROE | 2006-02-02 | 2/2 | 360 | LEAKING SEWER TO KARST ENVIRONMENT | LEAKING SEWER, REROUTED TO ANOTHER SANITARY | FROM EMER RESPONSE
IN0045187 | MONROE COUNTY RSD | MONROE | 2006-07-25 | 7/25 - 7/26 | 5000 | MT EBAL LIFT STATION | MALFUNCTION IN THE CONTROL PANEL OF THE LIFT STATION | REPAIRED CONTROLS
IN0045187 | MONROE COUNTY RSD | MONROE | 2006-11-24 | ? - 10:00A | 500 | FORCE MAIN FROM LIFT STATION (EAGLE BAY #1) | BREAK IN FORCE MAIN | REPAIR BROKEN PIPE & TEST
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2006-04-14 | 9:30P - 11:00P | 550000 | HEADWORKS EMERGENCY BYPASS 515 BLUFF | RAIN, CITY WIDE POWER FAILURE - GENERATOR STRUCK BY LIGHTNING
IN0023418 | LADOGA MUNICIPAL STP | MONTGOMERY | 2006-04-16 | 4/16 |  | SEWER MANHOLE COVER | RAIN 2" | TOWN REPLACING PROBLEM SEWER LINE
IN0023418 | LADOGA MUNICIPAL STP | MONTGOMERY | 2006-12-01 | 2:00A - NOON | 1000 | MANHOLE # 72 | RAIN 2"
IN0021041 | NEW MARKET MUNICIPAL STP | MONTGOMERY | 2006-04-17 | 7:00A - 3:00P |  | PARK ST, VINE ST | RAIN 3", POWER FAILURE 2HRS
IN0021041 | NEW MARKET MUNICIPAL STP | MONTGOMERY | 2006-06-18 | 10:00P - 11:00A (6/19) | 165000 | VINE ST LOCATION 1 | RAIN 4.5"
IN0021041 | NEW MARKET MUNICIPAL STP | MONTGOMERY | 2006-06-18 | 10:00P - 11:00A (6/19) | 165000 | PARK ST LOCATION 2 | RAIN 4.5"
IN0021041 | NEW MARKET MUNICIPAL STP | MONTGOMERY | 2006-08-28 | 6:30A - 2:30P |  | VINE ST & PARK ST LIFT STATIONS | RAIN 3" | CREEK BACK-FLOW
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-01-13 | 9:45A - 11:45A |  | MANHOLE # 76 | RAIN 0.75"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-02-02 | 3:30P - 9:00P |  | MANHOLE # 76 | RAIN 0.1"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-03-09 | 3/9 - 3/10 |  | # 76 | RAIN 3/15"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-03-12 | 3/12 |  | # 147 7 76 | RAIN 3"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-03-13 | 3/13 - 3/14 |  | # 76
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-03-14 | 7:00P - 10:30P |  | # 76 | DEBRIS STUCK IN GATE VALVE
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-04-02 | 8:30P - 10:30P |  | MANHOLE # 76 | RAIN 3.65"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-04-04 | 4:30P - 2:00A (4/5) |  | LIFT STATION | EQUIPMENT FAILURE
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-08-09 | 10:30P - 11:00P | 500 | MANHOLE 32 | EQUIPMENT FAILURE - PUMP IMPELLER
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-11-16 | 4:45A - 7:05A |  | # 76 | RAIN 1.75"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-11-30 | 6:40P - 9:00P |  | # 26, # 147 | RAIN 3.25"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2006-12-31 | 6:00A - 11:00A |  | # 76 & # 32 | RAIN 1.5"
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2006-01-02 | 5:30P - 12:00P (1/3) | 90000 | 003 | RAIN
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2006-10-19 | 8:00A - 2:30P (10/21) | 108000 | 002 | PUMP STOPPED UP
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2006-12-12 | 12:00A - 7:00P (12/14) |  | LIFT STATION ON 252 | RAIN 2.10"
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2006-12-21 | 7:30P - 11:30P (12/22) | 84000 | 002 LONG RUN | RAIN 1.75"
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2006-12-25 | 9:00P - 9:00A (12/27) | 108000 | LIFT STATION 102 | RAIN 0.9"
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2006-12-31 | 8:00A - 12:00A (1/1) | 48000 | LIFT STATION ON 252 #102 | RAIN 0.25"
IN0060798 | MOROCCO WWTP | NEWTON | 2006-03-26 | 4:00A - 5:30A | 3000 | MANHOLE AT 3060 W 275 S | GREASE BUILDUP UNDER LIFT STATION FLOATS, AREA CLEANED | SERVICE TWO LIFT STATIONS EVERY SIX MONTHS
IN0022144 | ALBION MUNICIPAL STP | NOBLE | 2006-12-01 | 8:00A - 3:00P |  | SSO # 2 OVERFLOW | RAIN 2" | PLAN TO SEPARATE MORE STORM WATER OUT OF SYSTEM
IN0020664 | AVILLA MUNICIPAL STP | NOBLE | 2006-07-29 | 18:30 - 22:00 (7/31) | 100000 | MANHOLE NEAR LIFT STATION # 1 | ALARM SYSTEM FAILURE, OPERATOR DID NOT NOTICE DURING CHECK | EMPLOYEE TO PERFORM BETTER DAILY CHECKS
IN0021814 | CROMWELL MUNICIPAL STP | NOBLE | 2006-03-10 | 3/10 | 12000 | PARTIAL PLANT WASHOUT | RAIN 1.5" | PLANT IMPROVEMENTS PLANNED
IN0024431 | RISING SUN MUNICIPAL STP | OHIO | 2006-03-12 | 6:45A - 8:00A |  | MANHOLE 15 & A-6 | RAW PUMP # 2 FAILURE, HEAVY RAIN | UPGRADE TO PLANT STARTED
IN0022951 | FRENCH LICK MUNICIPAL STP | ORANGE | 2006-03-09 | 6:00P - 8:00P | 192000 | CAPACITY EXCEEDED | RAIN 3.8" | PLANT EXPANSION TO BE COMPLETE END OF 2006
IN0022951 | FRENCH LICK MUNICIPAL STP | ORANGE | 2006-03-11 | 3/11 |  | MANHOLES, HWY 56, LARRY BIRD BLVD | RAIN 4.3" | LIFT STATION # 2GETTING UPGRADED PUMP, 3.3 MG STORM POND
IN0021601 | ORLEANS MUNICIPAL STP | ORANGE | 2006-03-12 | 3/12 - 3/18 | 4493000 | OXIDATION DITCH | RAIN 8.7"
IN0021601 | ORLEANS MUNICIPAL STP | ORANGE | 2006-11-27 | 11/27 - 12/8 | 1300000 | BYPASS OF UV - INSTALLATION ON NEW SYSTEM | INSTALLATION OF NEW UV SYSTEM
IN0021601 | ORLEANS MUNICIPAL STP | ORANGE | 2006-11-27 | TWO WEEKS |  | BYPASSING UV DISINFECTION SYSTEM - USING CHLORINE | INSTALLATION OF A TROJAN UV SYSTEM | MONITORING CHLORINE DURING INSTALLATION
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2006-03-12 | 3/12 - 3/14 |  | # 004 WILLOW CREEK RD | RAIN 8.1"
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2006-09-24 | 7:00A - 9:00P |  | MANHOLE # 004 WILLOW CREEK RD | RAIN 3.77" | KEEP ALL PUMPS RUNNING AT PLANT
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2006-01-03 | 3:00A - 8:00A |  | AUGER MONSTER HEADWORKS BUILDING | DEBRIS IN SEWER CAUSED OVERFLOW, GRINDER TO KICK OUT | TO DISCUSS WITH WASTEWATER ENGINEER
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2006-03-12 | 2:50A - 3:30A | 4000 | STRAWBERRY RD LIFT STATION | POWER FAILURE
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2006-04-19 | 8:40A - 10:50A | 12000 | MANHOLE AT PARKE COUNTY JAIL | DEBRIS IN SEWER MAIN, RAGS & DEBRIS FROM JAIL | CLEARED WITH JET TRUCK
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2006-05-10 | 10:20A - 10:40A | 2000 | WET WELL LID - STRAWBERRY ROAD LIFT STATION | POWER FAILURE, TREE TRIMMERS MADE CONTACT WITH POWER LINE | LIFT STATION HOSED DOWN & CLEANED UP
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2006-05-31 | 5:00P - 5:30P | 3000 | STRAWBERRY RD LIFT STATION | POWER FAILURE | ELECTRICAL LINES TO BE UPDATED
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2006-06-16 | 2:40P - 5:20P | 14000 | STRAWBERRY ROAD LIFT STATION WET WELL | LIFT STATION PUMP FAILURE | TO KEEP SPARE PARTS ON HAND
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2006-06-18 | 7:40 - 7:55 | 2000 | STRAWBERRY ROAD LIFT STATION | LINE FUSE BLEW DUE TO LIGHTNING
| CANNELTON, CITY OF | PERRY | 2006-01-22 | 7:55P - 1:30A (1/23) | 2000 | FORTH STREET LIFT STATION | RAIN 2.1" | RECENTLY SMOKE TESTED AREA SEWERS, TO CONTACT OWNERS
| CANNELTON, CITY OF | PERRY | 2006-03-09 | 3/9 - 3/10 | 2000 | FORTH STREET LIFT STATION | RAIN 3.1" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-03-12 | 7:55A - 6:05P | 2000 | FORTH STREET LIFT STATION | RAIN 2.1" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-04-21 | 11:45A - 2:45P | 2000 | FORTH STREET LIFT STATION | RAIN 2.6" | LOOKING FOR INFLOW SOURCES
| CANNELTON, CITY OF | PERRY | 2006-05-24 | 10:45P - 8:20A (5/25) | 2000 | FOURTH STREET LIFT STATION | RAIN 3.3" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-06-02 | 6:15A - 8:20P |  | FORTH STREET LIFT STATION | RAIN 3.6" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-06-02 | 6:20A - 7:40A | 2000 | ADAMS STREET LIFT STATION | RAIN 3.6" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-07-11 | 4:25P - 9:20P | 2000 | FOURTH STREET LIFT STATION | RAIN | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-07-13 | 12:45A - 5:20A | 2000 | FOURTH STREET LIFT STATION | RAIN 1.8"
| CANNELTON, CITY OF | PERRY | 2006-07-21 | 4:30P - 8:30P | 2000 | 4TH STREET LIFT STATION | RAIN 2.5"
| CANNELTON, CITY OF | PERRY | 2006-09-22 | 7:45P - 9:20P (9/23) | 2000 | FORTH STREET LIFT STATION | RAIN 6.2" | SEARCH & REPAIR SOURCES OF INFLOW - SMOKE TESTING
| CANNELTON, CITY OF | PERRY | 2006-10-16 | 9:55P - 9:00A (10/17) | 2000 | FOURTH STREET LIFT STATION | RAIN 3.4" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-10-27 | 6:30A - 6:00A (10/28) | 2000 | FOURTH STREET LIFT STATION | RAIN 3.9" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-11-07 | 2:40A - 11:00A | 2000 | FOURTH STREET LIFT STATION | RAIN 1.8" | WORKING ON I & I REDUCTION, TV, SMOKE TESTING
| CANNELTON, CITY OF | PERRY | 2006-11-15 | 10:38A - 6:30P | 2000 | FOURTH STREET LIFT STATION | RAIN 1.8" | ONGOING EFFORT TO LOCATE I & I
| CANNELTON, CITY OF | PERRY | 2006-11-16 | 1:52A - 1:30P | 2000 | FOURTH STREET LIFT STATION | RAIN 1.1" | WORKING ON I & I REDUCTION
| CANNELTON, CITY OF | PERRY | 2006-12-01 | 1:21A - 7:30A | 2000 | FOURTH STREET LIFT STATION | RAIN 2.1" | WORKING ON I & I REDUCTION
IN0004391 | HOOSIER ENERGY REC, INC. | PIKE | 2006-09-14 | 9/14 | 100000 | FLY ASH POND - 25' SECTION OF BERM | CATASTROPHIC FAILURE OF BERM - USED STRAW BLAES & LIMESTONE PILE TO FILTER WATER | BRINGING IN ENGINEER TO ASSESS CONDITION OF BERM
IN0020061 | HEBRON MUNICIPAL STP | PORTER | 2006-07-20 | 7/20 |  | MONROE LIFT STATION | RAIN 2" | MAINTAIN LIFT STATIONS
| PORTER PUBLIC WORKS | PORTER | 2006-03-13 | 2:30A - 4:00A | 10000 | PORTER AVE LIFT STATION | RAIN | CALLED CONTRACTOR TO PUMP LIFT STATION
| PORTER PUBLIC WORKS | PORTER | 2006-08-23 | 9:00P - 9:30P | 50 | TRIANGLE TRAIL LIFT STATION | RAIN | VAC TRUCK CALLED TO CLEAN UP SPILL
| PORTER PUBLIC WORKS | PORTER | 2006-08-28 | 3:00P - 8:00P | 5000 | TRIANGLE TRAIL LIFT STATION | RAIN | PULLING PUMPS & EVALUATE LIFT STATION
| PORTER PUBLIC WORKS | PORTER | 2006-08-28 | 2:15P - 7:00P | 200000 | PORTER AVE LIFT STATION | RAIN | USING VACTOR TRUCK TO PUMP EXCESS WATER
| PORTER PUBLIC WORKS | PORTER | 2006-09-12 | 8:15P - 10:35P | 3000 | PORTER AVE LIFT STATION | RAIN 2.4" | USED VAC TRUCK TO PREVENT ANY MORE OVERFLOW
| PORTER PUBLIC WORKS | PORTER | 2006-09-12 | 8:15P - 11:30P | 3000 | TRIANGLE LIFT STATION | RAIN 2.4" | USED VAC TRUCK TO PUMP OUT WET WELL
| PORTER PUBLIC WORKS | PORTER | 2006-09-13 | 9/13 | 1000 | PORTER AVE LIFT STATION | RAIN | USED VAC TRUCK TO PUMP EXCESS WATER
| PORTER PUBLIC WORKS | PORTER | 2006-09-13 | 10:00A - 11:30A | 1000 | TRIANGLE LIFT STATION | RAIN | USED VAC TRUCK TO PUMP EXCESS WATER
| PORTER PUBLIC WORKS | PORTER | 2006-10-02 | 11:45P - 1:30A (10/3) | 500 | LIFT STATION | RAIN, PUMPS COULD NOT KEEP UP WITH RAIN INFLOW | CALLED LOCAL VAC TRUCKS TO SUCK WET WELL
| PORTER PUBLIC WORKS | PORTER | 2006-10-02 | 11:30P - 1:30A (10/3) | 1000 | PORTER AVE LIFT STATION | RAIN, PUMPS COULD NOT KEEP UP WITH RAIN INFLOW | CALLED LOCAL VAC TRUCKS TO SUCK WET WELL
| PORTER PUBLIC WORKS | PORTER | 2006-11-30 | 11/30 | 300 | MANHOLE NEAR TRIANGLE TRAIL LIFT STATION | RAIN 0.8" | CHECK PUMPS, VAC TO SUCK LIFT STATION DOWN
| PORTER PUBLIC WORKS | PORTER | 2006-12-22 | 3:30P - 5:00P | 1000 | MANHOLE STD-A-1 | SEWER LINE PLUGGED | VAC OUT MANHOLE, JETTED SEWER
| PORTER, TOWN OF | PORTER | 2006-07-27 | 7:45 - 10:30 |  | TRIANGLE TRAIL LIFT STATION | RAIN 5", LS PUMPS COULD NOT KEEP UP | CLEANED AFFECTED AREA
| PORTER, TOWN OF | PORTER | 2006-07-27 | 7:15 - 9:00 | 200000 | PORTER AVE LIFT STATION | RAIN 5", POWER FAILURE
| PORTER, TOWN OF | PORTER | 2006-08-03 | 7:40A - 8:00A |  | TRIANGLE TRAIN LIFT STATION | RAIN, POWER FAILURE
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-01-28 | ? - 8:45A | 50 | LEAKING HOSE ON CONST PROJECT, SOUTH OF 755 FOX RIVER ROAD | LEAKING HOSE ON SEWER BYPASS HOSE, REPAIRED | REPLACING BYPASS HOSE
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-02-17 | 9:05A - 10:00A | 545 | MANHOLE OVERFLOW 405 NEWCASTLE RD | SEWER BLOCKAGE | AFFECTED AREA CLEANED WITH VACUUM TRUCK
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-02-25 | 10:00A - 2:00P | 600 | FORCE MAIN CR 500 N CR 250 W | NIPSCO DAMAGED FORCE MAIN (HAMPTON FARMS SUB) | VAC TRUCK RECOVERED SEWAGE TO WWTP
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-03-13 | 3/13 | 333508 | FORCE MAIN & SEVEN MANHOLES | RAIN 2.54" | WORKING ON SEWER SYSTEM EVALUATION STUDY
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-03-19 | 3/19 - 3/20 |  | NEAR 756 EAGLE CREEK RD - PUMP DISCHARGE HOSE LEAK | DISCHARGE PIPE FITTING SEPARATED, SUSPECT VANSALS | TO INSTALL FENCE, REQUESTING POLICE PATROLS
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-04-07 | 1:15P - 2:00P |  | 115 GREENFLIED LN | DEFECTIVE SEWER CONNECTION 115 GREENFIELD LN | ADDING SEWER TO MAINTENANCE CLEANING SCHEDULE
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-04-17 | 1:58P - 5:00P | 3676 | GREASE BLOCKAGE IN SEWER - LOT 88 GREENFIELD LANE | GREASE BLOCKAGE IN SEWER, SUSPECT UPSTREAM RESTAURANTS | SEWER ADDED TO CLEANING SCHEDULE
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-04-26 | 1:30P - 2:15P |  | 12" SANITARY SEWER - 272 WEST COUNTY ROAD 500 NORTH | GAS UTILITY DAMAGED A 12" FORCE MAIN WHILE INSTALLING MAIN | WORKING ON REPAIRS - SOUTH HAVEN TO LOCATE SEWERS
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-05-08 | 1:09P - 1:35P |  | CRAWL SPACE DRAINS FROM THREE HOMES | SEWER MAIN BLOCKAGE | SEWER BLOCKAGE CLEARED, AREA CLEANED
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-05-08 | 8:30A - 10:40A |  | SANITARY SEWER SPANNING PEPPER CREEK | SMALL LEAK FROM SANITARY SEWER
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-05-10 | 7:45A - 8:15A |  | SIX INCH FORCE MAIN - CO RD 150 W & RANSOM RD | GAS UTILITY DAMAGED FORCE MAIN WHILE BORING NEW GAS MAIN | WORKING WITH UTILITIES TO LOCATE SEWERS
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-05-10 | 10:30A - 11:05A |  | MANHOLE 382 SASSAFRAS RD | SEWER BLOCKAGE, POSSIBLE VANDALS | REPLACE & SECURE MANHOLE LID
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-05-16 | 3:22P - 4:00P |  | LOT 84 GREENFIELD LANE | DEFECTIVE SANITARY SEWER CONNECTION | ADDED TO ROUTINE MAINTENANCE CLEANING
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-06-03 | 7:13P - 8:20P |  | MANHOLE @ 419 PLYMOUTH ROAD - BACK YARD | BLOCKAGE IN SEWER MAIN | ADDING SEWER TO ROUTINE CLEANING SCHEDULE
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-09-13 | 10:50A - 5:00P | 85710 | 5 MANHOLES - PORTLAND, MCCOOL, PLYMOUTH & LAHONDA | RAIN | CONDUCTING SEWER SYSTEM EVALUATION STUDY
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-10-03 | 9:30A - 9:50A | 2424 | FORCE MAIN SERVICE TAP, 272 WEST 500 NORTH | PIPE SEPARATED DURING REPAIR OF 2" FORCE MAIN
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-12-01 | 6:55A - 12:45P |  | MANHOLES TIMBERLINE, LAHONDA, PORTLAND | RAIN 2.13" | REPAIR & REHAB SANITARY SEWER MAINS
IN0030651 | SOUTH HAVEN SEWER WORKS, INC. | PORTER | 2006-12-22 | 7:20A - 4:15P | 415135 | 11 MANHOLES - PORTLAND, KEYSTONE, TIMBERLINE & LAHONDA | RAIN 1.3" | REPAIR & REHABILITATING NINE SEWER MAINS - COMPLETE 12/2006
IN0037176 | TWIN LAKES UTILITIES | PORTER | 2006-10-16 | ? - 11:30A |  | CLEANOUT @ 2195 HIDDEN VALLEY | MAIN BREAKER TRIPPED ON MAIN LIFT STATION (ALARM FAILURE) | INVESTIGATION ALARM FAILURE
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2006-07-20 | 6:45A - 8:35A | 1600000 | CSO OUTFALL # 002 | WWTP POWER FAILURE (STORM) - SWITCH GEAR FAILED | SWITCH GEAR TO BE ANALYZED BY MANUFACTURER
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-01-10 | 1/10 | 12650 | E&S HOUSING SSO | RAIN 1.5"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-01-13 | 4:45A - 11:00A | 14805 | E&S HOUSING SSO | RAIN 1"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-01-22 | 10:00P - 4:00A (1/23) | 14805 | E&S HOUSING SSO | RAIN 1"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-01-24 | 1:30A - 5:30P | 2484000 | MILLCREEK LIFT STATION CSO # 003 | POWER / EQUIPMENT FAILURE, PUMP FAILURE | RENTED PORTABLE PUMP, INCREASE PREVENTIVE MAINTENANCE
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-02-02 | 12:00P - 11:00P | 145000 | E&S HOUSING LIFT STATION SSO | RAIN 1.7"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-03-09 | 3/9 | 144000 | E&S HOUSING LIFT STATION | RAIN 1.5"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-03-11 | 8:00A - 5:30P | 91200 | E&S HOUSING LIFT STATION SSO | RAIN 1"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-03-12 | 3/12 | 115200 | E&S HOUSING LIFT STATION | RAIN 1.8"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-06-08 | 1:00A - 10:00A |  | PLANT HEADWORKS | POWER FAILURE - WEST SIDE OF MT VERNON - BREAKER FAILURE
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-07-12 | 10:00A - 2:00P | 28800 | E&S HOUSING LIFT STATION | RAIN 0.86"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-07-14 | 5:00P - 11:00P | 57600 | E&S HOUSING LIFT STATION | RAIN 1.65"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-07-21 | 7/21 | 230400 | E&S HOUSING LIFT STATION | RAIN 2.4", POWER FAILURE (VECTREN) | THE CITY NEEDS TO BUY A PORTABLE GENERATOR
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-09-22 | 9/22 - 9/23 | 326400 | E&S HOUSING LIFT STATION | RAIN 6.8"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-09-23 | 12:20P - 12:00A (9/24) | 230400 | E&S HOUSING LIFT STATION | RAIN 4"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-10-16 | 10:00A - 8:00A (10/17) | 9600 | E&S LIFT STATION | RAIN 2.6" | IN LTCP THEY PLAN ON ELIMINATING SSO
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-10-27 | 3:40P - 2:00A (10/28) | 105600 | E&S HOUSING LIFT STATION | RAIN 2.1"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-11-16 | 2:45A - 2:00P | 124800 | E&S HOUSING LIFT STATION | RAIN 1.4"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-11-30 | 11/30 - 12/1 | 115200 | E&S LIFT STATION | RAIN 2"
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2006-12-12 | 10:35A - 1:35 | 28800 | E&S LIFT STATION | RAIN 0.5"
IN0040517 | POSEYVILLE MUNICIPAL STP | POSEY | 2006-02-21 | ? - 7:00A (2/22) |  | WWTP INFLUENT STRUCTURE | CONTRACTOR SHUT OFF MICROSTRANER CAUSING OVERFLOW | WORKING WITH ENGINEER & CONTRACTOR TO REDESIGN STRUCTURE
IN0040517 | POSEYVILLE MUNICIPAL STP | POSEY | 2006-03-09 | 3/9 - 3/10 |  | WWTP EFFLUENT MANHOLE | RAIN | RAISE ELEVATION OF MANHOLE
IN0040517 | POSEYVILLE MUNICIPAL STP | POSEY | 2006-06-22 | ? AM - 5:40A | 10000 | 4901 MULKEY RD - WWTP DIGESTER | WASTING VALVE LEF OPEN, CONTRACTOR LEFT CAP ON OVERFLOW | CAP ON DIGESTER OVERFLOW PIPE HAS BEEN REMOVED
IN0052191 | SIGECO, A. B. BROWN STATION | POSEY | 2006-03-30 | 11:45A - 7:00A (3/31) | 2800000 | COULD NOT CONTROL PH OF LANDFILL POND SURGE WATER | FAILURE OF ELECTRIC SYSTEM THAT FEEDS CO2 | CHECK ELECTRIC SYSTEM PERIODICALLY
IN0045527 | CLEAR CREEK CONSERVANCY DISTRI | PUTNAM | 2006-02-18 | 4:30P - 7:00P | 20000 | LIFT STATION | LIFT STATION PUMP FAILURE, ALARM DIALER FAILED | TO FIX ALARM NOTIFICATION SYSTEM
IN0045527 | CLEAR CREEK CONSERVANCY DISTRI | PUTNAM | 2006-12-19 | 4:30P - 7:00P | 20000 | LIFT STATION P 2 | LIFT STATION PUMP FAILURE, ALARM DIALER FAILED, PAGER BATTERY LOW | FIX THE ALARM NOTIFICATION SYSTEM
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-01-12 | 12 NOON - 12:15 | 15 | DIGESTER OVERFLOWING TO FINAL TANK OUTFALL BASIN | OPERATOR INADVERTENTLY ALLOWED TANK TO OVERFLOW | INSTRUCTING OPERATOR TO ENSURE PROPER OPERATION
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-01-13 | 7:45A - 1:00A (1/14) | 139580 | 102 | RAIN 0.65", SATURATED GROUND
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-01-17 | 8:00A - 12:00 MIDNIGHT | 225700 | 102 | RAIN 0.68", GROUND SATURATED | PUT AS MUCH FLOW THROUGH PLANT AS POSSIBLE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-01-29 | 7:00A - 7:00P | 86650 | 102 | RAIN 1.01", PLANT RUNNING OVER CAPACITY
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-02-02 | 2:45P - 2:00P (2/3) | 358340 | 102 | RAIN 0.83" | PLANT EXPANSION BEING DESIGNED, WORKING ON I&I
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-02-16 | 10:15P - 1:15A (2/17) | 29610 | 102 | RAIN 0.64"
IN002216 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-03-08 | 3/8 - 3/14 | 1908510 | 102 PARTIAL PLANT BYPASS | RAIN 4.52"
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-03-31 | 20:45 - 21:15 | 2000 | MANHOLES W 205 & W 206 | RAIN 1.5", POSSIBLE SEWER OBSTRUCTION | WORKING ON A WWTP UPGRADE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-03-31 | 7:30A - 5:15P (4/1) | 344850 | 102 PLANT AT OR ABOVE CAPACITY | RAIN 1.64" | MANAGED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-04-02 | 10:00P - 1:00A (4/3) | 24510 | 102 | RAIN 0.31", PLANT OVER CAPACITY | MANAGING PLANT TO MINIMIZE IMPACT
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-04-06 | 12:45P - 10:30A | 454740 | 102 | RAIN 0.74"
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-04-14 | 5:00A - 7:30A | 4590 | 102 | RAIN 1.08"
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-05-02 | 2:30A - 8:00A | 78300 | 102 | RAIN 1.06" | OPERATING PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-05-11 | 4:00A - 1:30P | 717700 | 102 | RAIN 1.3" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-05-17 | 11:00P - 4:00A (5/18) | 28160 | 102 | RAIN 0.57"
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-05-22 | 10:00A - 6:00P |  | 102 - BYPASS OF CONTACT TANK FOR CLEANING | HIGH FLOWS CAUSED SOLIDS IN CONTACT TANK
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-05-31 | 10:15P - 11:45P | 7520 | 102 | RAIN 0.61" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-06-02 | 6/2 | 9390 | 102 | RAIN 0.61" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-06-10 | 8:15P - 11:45P | 6510 | 102 | RAW SEWAGE PUMP FAILURE - BELIEVE LIGHTNING STRIKE | REPAIR & REPLACING PUMPS & CONTROLS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-06-18 | 10:00P - 3:00A (6/19) | 131880 | 102 | RAIN 1.3", PLANT ONLY RUNNING WITH ONE SEWAGE PUMP | USING 4" GAS PUMP
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-06-19 | 3:30P - 5:30P | 10300 | 102 | RAIN 0.46"
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-06-26 | 6:15P - 8:15P | 12160 | 102 | RAIN 0.66" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-08-27 | 5:30P - 9:30P | 24550 | 102 | RAIN | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-08-31 | 3:45A - 4:00A | 200 | MANHOLE W-3 | RAIN 0.71" | ONGOING EFFORT TO LOCATE I & I
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-08-31 | 3:45A - 4:30A | 1490 | PLANT HEADWORKS | RAIN 0.71" | PLANS FOR CONSTRUCTION OF NEW TREATMENT FACILITY
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-09-12 | 8:00P - 8:00A (9/13) | 103390 | 102 | RAIN 1.98" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-09-22 | 8:30P - 1:30A | 64110 | 102 | RAIN 1.01" | CONTINUE TO LOCATE & ELIMINATE I&I FROM SYSTEM
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-10-03 | 5:15A - 4:15P | 122150 | 102 | RAIN 1.39" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-10-07 | 5:15A - 6:00A | 5820 | WWTP OUTFALL 102 | RAIN 0.54" | PLANT UPGRADES ARE IN THE PROCESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-10-16 | 8:00P - 12:30P (10/17) | 142770 | 102 | RAIN 2.11" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-10-21 | 6:00P - 6:30P | 500 | MANHOLE # W3 | HEADWORKS LIFT STATION PUMP FAILURE | TAKING BIDS TO UPGRADE PLANT
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-10-27 | 10:00A - 8:00A (10/28) | 327000 | 102 | RAIN 1.6" - ONE RAW SEWAGE PUMP DOWN | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-11-10 | 11:45P - 3:30A (11/11) | 21580 | 102 | RAIN 0.62" | PLANT UPGRADES IN PROGRESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-11-15 | 2:00P - 11:00P | 48075 | PLANT OUTFALL 102 | RAIN 0.96" | WORKING ON CONSTRUCTION OF PLANT UPGRADES
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-11-16 | 5:00A - 7:30A | 232665 | OUTFALL 102 | RAIN 1.02" | OPERATED PLANT TO MAINTAIN SOLIDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-11-21 | 2:00P - 8:00P | 15000 | LIFT STATION # 1 MANHOLE | BROKEN SHAFT ON PUMP | INVESTIGATING CAUSE FOR FAILURE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-11-30 | 11/30 - 12/1 | 611746 | OUTFALL 102 | RAIN 2.26" | PLANT EXPANSION & COLLECTION SYS IMPROVEMENTS IN PROCESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-12-12 | 5:00P - 8:00P | 16660 | OUTFALL 102 | RAIN 1.17" | UPGRADES IN PROCESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-12-12 | 8:00A - 4:00P | 39930 | OUTFALL 102 | RAIN 1.17" | UPGRADES IN PROCESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-12-21 | 1:15P - 10:30P (12/22) | 327270 | OUTFALL 102 | RAIN 1.51" | UPGRADES IN PROGRESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-12-25 | 1:45P - 5:45P | 39430 | OUTFALL 102 | RAIN 0.46" | PLANT UPGRADES IN PROCESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-12-25 | 11:00P - 9:30A (12/26) | 91220 | OUTFALL 102 | RAIN 0.38" | UPGRADES IN PROCESS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2006-12-31 | 6:30A - 5:00P | 96460 | OUTFALL 102 | RAIN 0.73" | PLANT UPGRADES IN PROCESS
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2006-03-12 | 06:30A - 12:10P | 25000 | N JACKSON L. S. | RAIN 4" | LARGER FORCE MAIN
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2006-09-01 | 06:40A | 25000 | NORTH JACKSON ST LIFT STATION | POWER FAILURE (DUKE ENERGY) | CLEANED UP DEBRIS
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2006-09-04 | 09:20A - 09:50A | 5000 | CORNSTALK LIFT STATION | PUMP KICKED OFF BREAKER KILLING POWER | CLEANED UP DEBRIS
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2006-11-13 | 9:10A - 1:30P (11/14) | 25000 | FORCE MAIN FROM SWAMPY LIFT STATION | BROKEN FORCE MAIN
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2006-11-16 | 9:15A - 1:00P | 10000 | SHERWOOD LIFT STATION | RAIN 1.75" | CLEAN UP DEBRIS
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2006-11-19 | 2:30P - 3:00P | 25000 | FORCE MAIN FROM SWAMPY LIFT STATION | BROKEN FORCE MAIN | PICKED UP DEBRIS
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2006-11-22 | 6:00P - 11:00P | 10000 | FORCE MAIN FROM SWAMPY LIFT STATION | BROKEN FORCE MAIN | GETTING PRICE TO REPLACE ENTIRE SECTION OF FORCE MAIN
IN0039624 | VAN BIBBER CONSERVANCY DISTRIC | PUTNAM | 2006-05-14 | 11:00A - 2:00P (5/15) | 70000 | MANHOLE AT SEWER PLANT | CLARIFIER SURFACE SKIMMER FAILURE | PUMP CLARIFIER DOWN & MAKE REPAIRS
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2006-01-28 | 1/28 | 50000 | COLLECTION SYSTEM | RAIN 0.8"
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2006-03-09 | 3/9 - 3/13 | 250000 | COLLECTION SYSTEM | RAIN 3.92"
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2006-03-31 | 3/31 - 4/1 | 30000 | COLLECTION SYSTEM | RAIN 1.21"
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2006-05-11 | 5/11 |  | COLLECTION SYSTEM
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2006-05-25 | 7:30P - NOON (5/27) | 200000 | COLLECTION SYSTEM | RAIN 1.33"
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2006-10-17 | 10/17 - 10/19 | 120000 | COLLECTION SYSTEM | RAIN 2.42"
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2006-11-30 | 11/30 - 12/2 | 200000 | COLLECTION SYSTEM | RAIN 2.75"
IN0020001 | RIDGEVILLE MUNICIPAL STP | RANDOLPH | 2006-12-18 | 8:00A - 9:00A | 200 | LIFT STATION - PLANT | LARGE FILTER BACKWASH FLOW FROM WATER DEPT | COMM WITH BOARD AND WATER DEPT
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-01-02 | 6:00A - 1:30P | 540000 | 24" SOUTH DIVERSION | RAIN | ENGINEERING FIRM WORKING ON SOLUTIONS TO CORRECT
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-03-12 | 7:20A - 9:00A | 900000 | JACKSON LIFT STATION | RAIN 1.2"
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-05-11 | 7:00P - 7:00A (5/12) | 230000 | JACKSON LIFT STATION | RAIN 2"
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-11-30 | 2:45P - 2:00P (12/1) | 125000 | 24" SOUTH DIVERSION | RAIN 2.75" | WORKING ON SOLUTIONS TO CORRECT PROBLEM
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-11-30 | 2:00P - 7:00P (12/1) | 3210000 | 30" NORTH DIVERSION | RAIN 2.75" | WORKING TO CORRECT PROBLEM
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-12-01 | 1:00P - 7:30P | 430000 | HEADWORKS | RAIN 2.75" | MONITORING SITUATION TO MINIMIZE BYPASS
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-12-01 | 1:00P - 7:30P | 230000 | JACKSON LIFT STATION | RAIN 2.75"
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-12-31 | 9:30A - 6:30A (1/1) | 540000 | 24" SOUTH DIVERSION | RAIN 0.62" | ENGINEERING FIRM WORKING ON SOLUTIONS TO CORRECT
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2006-12-31 | 9:30A - 6:30A (1/1) | 830000 | 30" NORTH DIVERSION | RAIN 0.62" | ENGINEERING FIRM WORKING ON SOLUTIONS TO CORRECT
IN0021024 | WINCHESTER MUNICIPAL STP | RANDOLPH | 2006-03-31 | 9:30 - 11:00P | 200000 | 901 N W ST LIFT STATION | RAIN 1.5", STORMS, LIGHTNING STRIKE CAUSED DAMAGE TO LS | REPAIR DAMAGED EQUIPMENT
IN0021024 | WINCHESTER MUNICIPAL STP | RANDOLPH | 2006-04-20 | 2:00A - 4:30A | 250000 | FILTER INFLUENT TANK | POWER SURGE SHUT DOWN PUMPS, POLICE DIDN'T NOTIFY WWTP STAFF | REWORKING POLICY WITH POLICE RE ONCALL EMPLOYEES
IN0023779 | MILAN MUNICIPAL STP | RIPLEY | 2006-03-09 | 3/9 - 3/10 | 82000 | WWTP LIFT STATION | RAIN 3.4"
IN0023779 | MILAN MUNICIPAL STP | RIPLEY | 2006-03-11 | 3/11 - 3/12 | 1100000 | WWTP & E CARR LIFT STATIONS | RAIN 3.3" | LOOKING FOR INFLOW SOURCES
IN0023779 | MILAN MUNICIPAL STP | RIPLEY | 2006-04-02 | 4/2 |  | MAIN LIFT STATION TO PLANT DOWN - RAW TO EQ BASIN | MAIN LIFT STATION TO PLANT HAD A FAULT MODE | LOOKING FOR ALTERNATE ALARM FOR LIFT STATION
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2006-03-08 | 2:00P - 6:00P | 30000 | HEADWORKS | RAIN 2.4" | WORKING ON I & I REDUCTION
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2006-03-11 | 3/11 - 3/12 | 60000 | HEADWORKS | RAIN | WORKING ON I & I REDUCTION
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2006-04-21 | 6:00P - 7:00P | 5000 | WWTP HEADWORKS | RAIN 0.9" | CONTINUE WORKING ON I & I REDUCTION
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2006-11-30 | 10:00P - 8:00A (12/1) | 30000 | HEADWORKS | RAIN 2.9" | WORKING ON I & I REDUCTION
IN0021679 | SUNMAN MUNICIPAL STP | RIPLEY | 2006-03-12 | 3/12 | 200000 | ONE CELL LAGOON | RAIN 5.7" | WORKING ON I & I CORRECTIONS
IN0021679 | SUNMAN MUNICIPAL STP | RIPLEY | 2006-03-12 | 3/12 - 3/13 | 250000 | LAGOON AT PLANT | RAIN 2.2" | WORKING ON I & I REDUCTION
IN0109746 | ANDERSON TOWNSHIP RSD | RUSH | 2006-03-12 | 06:30 - 17:00 | 10000 | WOODS LIFT STATION | RAIN 5.1" | SEWER REHABILIATATION IS PROGRESS
IN0109746 | ANDERSON TOWNSHIP RSD | RUSH | 2006-05-22 | 16:00 - 16:05 | 100 | FORCE MAIN - FT WAYNE RD | HIT 3" FORCE MAIN WHILE DIGGING
IN0109746 | ANDERSON TOWNSHIP RSD | RUSH | 2006-07-18 | ? - 9:00 |  | 3" FORCE MAIN - FT WAYNE RD | SPLIT FORCE MAIN, REPAIRED
IN0109746 | ANDERSON TOWNSHIP RSD | RUSH | 2006-12-01 | 3:30A - 2:00P | 3300 | MANHOLE 7352 ST RD 3 | RAIN 2.3" | WORKING ON I & I REDUCTION
IN0061531 | WESTERN WAYNE RSD | RUSH | 2006-03-11 | 3/11 - 3/13 | 462100 | WWTP | RAIN 5.75" | LOOKING FOR INFLOW SOURCES
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2006-02-24 | 9:35A - 12:30P |  | CSO 019 | SEWER PARTIALLY OBSTRUCTED WITH DEBRIS, SEWER JETTED
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-02 | 7:00A - 11:00A | 87000 | PLANT | RAIN 0.7"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-13 | 4:00P | 350000 | PLANT | RAIN0.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-13 | 3:30P - 7:45A (1/14) | 1772000 | PLANT | RAIN 0.3" | WORKING ON PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-17 | 10:00A - 8:00A (1/18) |  | # 47, PLANT | RAIN 0.8" | WORKING ON PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-18 | 8:00A - 6:00A (1/19) | 858000 | PLANT | RAIN 0.6" | WORKING ON PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-20 | 2:00P - 3:30P | 500 | LIFT STATION | POWER FAILURE, CINERGY POWER LINE / TRANSFORMER
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-22 | 9:30A - 10:30A (1/23) | 1386000 | PLANT MANHOLE # 47 | RAIN 1.1" | WORKING ON PHASE TWO IMPROVEMENTS, IDEM AGREED ORDER
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-01-23 | 10:30 - 6:00A (1/24) | 1780000 | PLANT, MANHOLE # 47 | RAIN 1.1" | WAITING ON IDEM TO RETURN PERMIT
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-02-03 | 9:30A - 2:00P | 322000 | PLANT | RAIN 0.6" | GOT BACK CONST PERMIT FROM IDEM TODAY
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-02-03 | 3:15A - 9:30A | 578888 | PLANT | RAIN 0.6" | WORKING ON PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-02-04 | 7:45A - 8:00A (2/5) |  | # 47 PLANT | RAIN 0.7" | WORKING ON PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-02-12 | 9:30 - 10:00A | 50 | LIFT STATION AT PLANT | BAD ALTERNATING RELAY, REPLACED
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-02-17 | 7:00A - 9:30A | 104000 | PLANT | RAIN 0.4"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-03-09 | 3/9 - 3/10 | 2004000 | PLANT, MH 47, 191 | RAIN 2"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-03-10 | 7:00A - 3:15P | 974000 | PLANT | EQUIPMENT FAILURE
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-03-11 | 3/11 - 3/12 | 2347000 | PLANT MH 47-79-191 | RAIN 3.8", EQUIPMENT FAILURE
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-03-12 | 3/12 - 3/13 | 2590000 | PLANT MH 47-79-191 | RAIN 1.5", EQUIPMENT FAILURE
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-03-13 | 3/13 - 3/14 | 2684000 | PLANT | RAIN 1.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-03-14 | 7:00A - 3:30P | 881000 | PLANT | INFILTRATION
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-03-31 | 3/31 - 4/1 | 1537000 | PLANT | RAIN 1.2"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-02 | 4/2 - 4/3 | 1421000 | PLANT | RAIN 4"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-03 | 7:00A - 2:15P | 736000 | PLANT | RAIN 4"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-06 | 4:00P - 7:00A (4/7) | 837000 | PLANT | RAIN 1.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-07 | 7:00A - 9:00A (4/8) | 1393000 | PLANT MH 47 | RAIN 1.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-08 | 9:00A - 7:00A (4/9) | 1335000 | PLANT | UPSETTING PLANT
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-19 | 9:00A - 11:00A | 157000 | PLANT | RAIN 0.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-20 | 4/20 - 4/21 | 1324000 | PLANT | RAIN 0.7"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-21 | 4/21 - 4/22 | 1321000 | PLANT, MH 47 78 | RAIN 0.7"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-04-22 | 4/22 - 4/23 | 1001000 | PLANT | RAIN 0.7"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-05-02 | 9:00A - 6:30A (5/3) | 1839000 | PLANT MH 47 | RAIN 0.8"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-05-03 | 12:30P - 2:10P | 102000 | PLANT | RAIN 0.8"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-05-11 | 2:00P - 7:00A (5/12) | 822000 | PLANT | RAIN 0.7"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-05-18 | 5/18 | 660000 | PLANT | RAIN 0.3"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-05-25 | 7:00A - 10:00A | 283000 | PLANT | RAIN 0.9"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-06-02 | 11:00A - 1:30P | 220000 | PLANT | RAIN 0.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-06-08 | 7:00A - 3:30P | 804000 | PLANT | RAIN 2.3"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-06-11 | 8:15A - 3:30P | 741000 | PLANT | RAIN 1.2"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-06-22 | 7:00A - 3:20P | 531000 | PLANT | RAIN 2.3"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-06-30 | 6/30 | 200 | # 6 FORCE MAIN | BROKEN FORCE MAIN - REPAIRED WITH 6" CAST IRON PIPE | BLOCKED OFF FLOW IN DITCH & PUMPED BACK TO # 6 LIFT STATION
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-07-12 | 7/12 - 7/13 | 618000 | PLANT | RAIN 0.8"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-07-13 | 8:30A - 11:00A | 200 | BROKEN FORCE MAIN | BROKEN FORCE MAIN | REPAIRED WITH BAND
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-07-14 | 7/14 | 200 | FORCE MAIN | BROKEN FORCE MAIN, REPAIRED | PUMPED BACK INTO LIFT STATION, HAULED WITH TRUCK
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-07-28 | 12:30P - 2:30P | 215000 | 001 | RAIN 5"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-08-16 | 6:30A - 8:30A |  | BROKEN FORCE MAIN | BROKEN FORCE MAIN | REPAIRED WITH 6" CLAMP
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-08-28 | 7:00A - 2:00P | 530000 | PLANT | RAIN 0.6" | WORKING ON PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-09-18 | 8:00A - 9:30A |  | MANHOLE # 351 | TOO MUCH FLOW FROM PEPSI - PUMPS IN LS WILL NOT HANDLE FLOW
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-09-19 | 8:00A - 9:30A |  | MANHOLE # 351 | TOO MUCH FLOW FROM PEPSI - PUMPS IN LS WILL NOT HANDLE FLOW
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-09-22 | 9:30A - 0:15A (9/23) | 880000 | PLANT, MH #47, #82 | RAIN 2" | WAITING FOR RURAL DEVELOPMENT TO START PHASE 2
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-09-23 | 9/23 - 9/24 | 850000 | PLANT | RAIN 0.6" | WAITING FOR RURAL DEVELOPMENT TO START PHASE 2
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-09-24 | 2:00P - 9:00P | 800000 | PLANT | RAIN 0.6" | WAITING FOR RURAL DEVELOPMENT TO START PHASE 2
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-10-17 | 7:00A - 9:00P | 1325000 | PLANT MANHOLE # 47 | RAIN 2"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-10-20 | 8:00A - 9:00A | 100 | MANHOLE 351 | HEAVY FLOW FROM PEPSI - PUMPS WILL NOT HANDLE | VAC TRUCK TO KEEP LIFT STATION PUMPED DOWN
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-10-27 | 10/27 | 2044000 | PLANT | RAIN 1.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-10-28 | 7:00A - 9:00A (10/29) | 2272000 | PLANT | RAIN 1.6"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-10-31 | 1:30P - 8:00P | 523000 | # 47 PLANT | RAIN 0.4" - HEAVY RAIN UPSETTING PLANT | WORKING ON PHASE 2 OF IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-11-07 | 6:30A - 6:30P | 509000 | PLANT | RAIN 1.6" - HEAVY RAIN UPSETTING PLANT
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-11-15 | 12:45P - 7:00A (11/16) | 1917000 | PLANT MANHOLE 47 | RAIN 1.3" | TAKING BIDS FOR PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-11-17 | 9:00A - 2:30P | 400000 | PLANT | RAIN | BIDS BEING TAKEN FOR PHASE TWO IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-11-29 | 7:45A - 3:00P | 729000 | PLANT | RAIN 0.5" | BIDS FOR PLANT / COLLECTION SYSTEM IMPROVEMENTS, UNDER AO
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-11-30 | 9:00A - 2:30P | 340000 | PLANT | RAIN 1.7" | BIDS FOR PLANT / COLLECTION SYSTEM IMPROVEMENTS, UNDER AO
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-11-30 | 7:00P - 7:00A (12/1) | 1241000 | PLANT | RAIN 1.7" | BIDS FOR PLANT / COLLECTION SYSTEM IMPROVEMENTS, UNDER AO
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-12-01 | 12/1 - 12/2 | 1328000 | PLANT MANHOLE E44, 82 | RAIN 1.7" | TAKING BIDS FOR PLANT IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-12-14 | 7:00P - 3:30 | 225000 | PLANT | HEAVY FLOW UPSETTING PLANT | TAKING BIDS FOR PLANT / COLLECTION SYSTEM IMPROVEMENTS
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-12-21 | 12:20A | 2010000 | PLANT | RAIN 1.8"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-12-22 | 12/22 - 12/23 | 1328000 | MANHOLE 47 | RAIN 1.2" | PREBID MEETING 1/14/2007
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-12-26 | 7:00A - 6:30A (12/27) | 2016000 | PLANT | RAIN 1" | PRE BID MEETING 1/14/07
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2006-12-31 | 11:45A - 7:30A (1/1) | 1999000 | PLANT | RAIN 0.4" | WORKING ON PHASE TWO IMPROVEMENTS
IN0032867 | SHELBYVILLE MUNICIPAL STP | SHELBY | 2006-03-09 | 3/9 - 3/10 | 1575000 | CONREY LIFT STATION | RAIN 1.8"
IN0032867 | SHELBYVILLE MUNICIPAL STP | SHELBY | 2006-03-12 | 3/12 - 3/13 | 4470000 | COREY LIFT STATION | RAIN 5"
IN0032867 | SHELBYVILLE MUNICIPAL STP | SHELBY | 2006-03-13 | 3/13 - 3/14 | 5474000 | CONREY STREET LIFT STATION | RAIN 6" | WORKING ON I & I REDUCTION
IN0051845 | AMERICAN ELECTRIC POWER, ROCKP | SPENCER | 2006-05-23 | NOON - 2:00P |  | FLYASH SILO SUMP - 2791 NORTH US HWY 231 | BREAK IN AN UNDERGROUND WATER PIPE | PLAN TO REROUTE STORM DRAIN SYSTEM TO WASTEWATER POND
IN0039306 | CHRISNEY MUNICIPAL STP | SPENCER | 2006-09-23 | 4:15A - 6:45A |  | MANHOLE # 81 | POWER FAILURE TRIPPED BREAKER AT MAIN LIFT STATION | INVESTIGATING ALARM FOR MAIN LIFT STATION
IN0021598 | DALE MUNICIPAL STP | SPENCER | 2006-03-11 | 3/11 - 3/12 | 500000 | WEST SIDE LIFT STATION | RAIN 9" | SLIP LINNING SEWERS
IN0021598 | DALE MUNICIPAL STP | SPENCER | 2006-09-23 | 12:00P - 6:00P | 200000 | WEST SIDE LIFT STATION | RAIN 7" | SLIPLINEING SEWERS, MANHOLE REHAB
| FULDA RSD | SPENCER | 2006-12-19 | 09:00 - 10:00A | 700 | 1.25" FORCE MAIN | FORCE MAIN CRACK | REPAIRED LINE
IN0061662 | ROCKPORT MUNICIPAL STP | SPENCER | 2006-06-26 | ? - 8:00A | 10000 | LIFT STATION ON BASE ROAD | RAIN 2.5", BLOWN FUSE (STORM) | DAILY LIFT STATION INSPECTIONS
IN0021067 | ROCKPORT MUNICIPAL STP | SPENCER | 2006-07-30 | 7/30 - 7/31 | 1500 | LIFT STARION AT ROCKY SIDE PARK | ONE PUMP OUT FOR REPAIR, REMAINING PUMP KICKED OUT | INSPECTION & INCREASED MAINTENANCE
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2006-03-11 | 3/11 - 3/12 |  | MANHOLE # 36, LS # 24 | RAIN 4.5" | CONTINUE WITH COLLECTION SYSTEM REPAIRS
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2006-04-14 | 12:30 - 1:30 | 200 | LIFT STATION | POWER FAILURE
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2006-04-21 | 14:35 - 15:00 | 3000 | MANHOLE # 36 LS # 24 | RAIN 2.67"
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2006-07-05 | 11:00A - 2:00P | 1800 | MANHOLE #2 & #7 | ELECTRICAL TRANSFORMER MALFUNCTION | ALERTED UTILITY PROVIDER
IN0023540 | LAKEVILLE MUNICIPAL STP | ST JOSEPH | 2006-03-13 | 4:30A - 6:00P | 24300 | SSO 003, MANHOLES GRAND ST, 323 S GRAND HOME BACKUP | RAIN 2" | LOOKING FOR INFLOW SOURCES
IN0023540 | LAKEVILLE MUNICIPAL STP | ST JOSEPH | 2006-07-18 | 7:00A - 9:00A |  | SSO # 003 | RAIN 2.2" | WORKING ON I & I REDUCTION
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2006-02-28 | 10:00A - 12:30P |  | CSO 004 CALHOUN ST | SEWER OBSTRUCTED WITH DEBRIS, REMOVED
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2006-04-04 | 2:00P - 2:30P |  | CSO 019 | FLOW MONITOR COLLECTED DEBRIS THAT OBSTRUCTED FLOW | FLOW MONITOR REMOVED
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2006-04-27 | 11:00A - 12:00P |  | CSO 019 MAIN ST | LARGE ROCK RESTRICTING FLOW IN SEWER CAUSING OVERFLOW | REMOVE ROCK, MONITOR CSO
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2006-07-11 | 10:00A - 10:02 | 300 | CSO 017 - UNPERMITTED | RAIN 1.3" | APPROVED CSO OPERATIONAL PLAN IN PLACE
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2006-07-14 | 11:00A - 1:10P | 725500 | CSO 017 - UNPERMITTED | RAIN 2.3" | APPROVED CSO OPERATIONAL PLAN IN PLACE
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2006-07-18 | 3:00A - 3:28A | 2800 | CSO 017 - UNPERMITTED | RAIN 2" | APPROVED CSO OPERATIONAL PLAN IN PLACE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-01-11 | 1/11 |  | ILLEGAL SEWER CONNECTIONS TO CSO OUTFALL 042 | TWO HOUSES & CATCH BASIN CONNECTED TO CSO OUTFALL | WORKING ON CLOSURE OF THE LATERALS
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-02-24 | 2/24 - 2/27 | 10000 | CSO 026 | ROOTS & RAGS IN THROTTLE LINE, VACTOR CREW REMOVED DEBRIS
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-05-10 | 5/10 |  | CSO 007 THROTTLE LINE | CONTRACTOR BROKE THROTTLE LINE FOR CSO 007
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-05-21 | 1:00P - 10:15A (5/22) | 300 | OVERFLOW FROM TOP OF CLAY FIRE LIFT STATION | FORCE MAIN FLANGE FAILURE | REPAIR FLANGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-07-23 | 12:01A - 2:15P | 20000 | CSO 044 | BLOCKAGE IN THROTTLE LINE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-08-04 | 8/4 - 3:00P | 290000 | CSO 14 | CSO 14 THROTTLE LINE PLUGGED WITH DEBRIS | CHECK REGULARY AFTER RAIN EVENTS
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-08-07 | 8/7 - 9:00A | 25000 | CSO 14 | THROTTLE LINE PLUGGED WITH DEBRIS | CLEAN WITH VACTOR, CHECK REGULARY AFTER RAIN EVENTS
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-10-09 | ? - 10:30A (10/10) | 60000 | CSO 026 | THROTTLE LINE PLUGGED WITH DEBRIS (ROCKS) | DEBRIS FROM SEWER SEPERATION PROJECT, CONT. NOTIFIED
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-11-15 | 1:00A - 8:50A | 20000 | CSO 026 | THROTTLE LINE PLUGGED WITH DEBRIS (LEAVES & STICKS) | REVIEWING MAINTENANCE FREQUENCY OF STRUCTURE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-11-21 | 12:01A - 2:30P | 1000 | MANHOLE - WILLOWGATE FORCE MAIN AIR RELIEF VALVE | DEBRIS IN AIR RELEASE VALVE - REMOVED | SERVICE VALVE - WORKING WITH DEVELOPER OF NEW SUBDIVISION
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-12-02 | 12:01A - 9:50A (12/4) | 30000 | CSO 044 | CSO THROTTLE LINE PLUGGED WITH DEBRIS | REVIEWING MAINTENANCE FREQUENCY
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-12-19 | 11/2 - 12/17 | 195000 | CSO 037 DRY WEATHER OVERFLOWS - 22 EVENTS (11/2 - 12/17) | CITY'S WATER WORKS BACK WASHING FILTERS DURING HIGH FLOW | REQUESTED NOT TO BACK WASH DURING DAYS
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2006-12-28 | 2:00P - 6:30P | 10000 | FERNWOOD LIFT STATION (NOT UNDER CITY CONTROL) | SURCHARGING MANHOLE - LIFT STATION PUMP FAILURE | CITY TO CONTACT DEVELOPER
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2006-03-13 | 3/13 | 65000 | CSO OUTFALL 004 | RAIN 1.75"
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2006-07-11 | 105 MIN | 105000 | OVERFLOW OF COLLECTION SYSTEM | STORM SEWERS ON STATE ROAD 39 CONNECTED TO SANITARY
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2006-08-10 | 8/10 - 8/11 | 330000 | CSO # 004 | RAIN 3.52" | TOWN WORKING TO CORRECT PROBLEM
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2006-08-10 | 1 HR 35 MIN | 285000 | CSO 004 | RAIN 3.52" | WORKING WITH IDEM & IN DOT TO REMOVE STORM DRAINS ON HWY 39
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2006-08-28 | 20 MIN | 20000 | CSO # 004 | RAIN 2.09" | TOWN WORKING TO CORRECT PROBLEM
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2006-08-28 | 20 MIN | 20000 | CSO 004 AT THE WASTEWATER PLANT | RAIN 2.09" | TOWN IS WORKING TO CORRECT THE PROBLEM
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2006-10-03 | 12:45A - 1:50A | 65000 | TREATMENT PLANT | RAIN 1.6" | INCREASING CSO PUMPS TO HANDLE MORE FLOW
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2006-12-08 | 7:00A - 9:00A (12/11) | 216000 | SANITARY SEWER MANHOLE | GREASE, RAGS & SAND CAUSING SEWER BLOCKAGE | LINE TO BE INSPECTED ONCE PER MONTH
IN0022292 | ASHLEY MUNICIPAL STP | STEUBEN | 2006-03-12 | 07:00 - 19:00 | 70000 | MAIN LIFT STATION | RAIN 0.7" | CONSTRUCTING NEW PLANT
IN0022292 | ASHLEY MUNICIPAL STP | STEUBEN | 2006-03-16 | 08:45 - 12:30 | 2800 | MAIN LIFT STATION | CONSTRUCTION - CUT IN TEE FOR NEW RAW SEWAGE LINE | TEE PART OF CONST TO ELIMINATE BYPASS
IN0022942 | FREMONT MUNICIPAL STP | STEUBEN | 2006-05-24 | 9:30A - 11:30A | 500 | MANHOLE OVERFLOW 600 N WHITE ST | LIFT STATION FLOATS FAILURE | CLEAN LIFT STATION
IN0050822 | HAMILTON LAKE C.D. | STEUBEN | 2006-11-03 | 10:15A - 10:50A | 300 | 3" FORCE MAIN | VERIZON DROVE A GROUND ROD THROUGH FORCE MAIN | LINES WERE LOCATED
IN0050822 | HAMILTON LAKE C.D. | STEUBEN | 2006-11-08 | 4:00P - 4:30P | 500 | DISCHARGE LINE / SEWER MAIN | CONTRACTOR HIT DISCHARGE LINE WHILE DIGGING FOOTERS | LINE WILL BE MOVED
IN0039322 | DUGGER MUNICIPAL STP | SULLIVAN | 2006-03-09 | 3/9-3/10 & 3/12-3/14 | 225000 | BYPASSED POND DUE TO POSSIBLE LEVEE DAMAGE | RAIN 3.2"
IN0039322 | DUGGER MUNICIPAL STP | SULLIVAN | 2006-03-09 | 3/9 - 3/10 |  | EFFLUENT MANHOLE | RAIN 3.2"
IN0039322 | DUGGER MUNICIPAL STP | SULLIVAN | 2006-05-30 | 08:30 - 16:15 | 3500 | MANHOLE LIFT STATION # 1 | BOTH PUMPS AIR LOCKED DUE TO FLOAT PROBLEM | CONTINUE TO MONITOR LIFT STATION
IN0039322 | DUGGER MUNICIPAL STP | SULLIVAN | 2006-09-12 | 9:00A - 11:30A | 20000 | AERATION TANK OVERFLOW | RAIN 3.75"
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-03-09 | 3/9 - 3/12 | 1000 | EQ BASIN & MANHOLE | RAIN 3.2" | SMOKE TESTING
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-03-18 | 01:00 - 06:30 | 2000 | SAWMILL RD MANHOLE 145 | BOTH LIFT PUMPS NOT WORKING, VACUUM LEAK
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-03-31 | 09:15A - 12:00P | 500 | SAWMILL RD LIFT STATION - MANHOLE 145 | RAIN 1.2", BOTH PUMPS CAN'T KEEP UP WITH FLOW | PICKED UP DEBRIS
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-04-06 | 13:30 - 17:00 (4/7) | 3000 | LIFT STATION MANHOLE ON SAWMILL RD & MANHOLE 15 | RAIN 2+"
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-06-22 | 21:30 - AM (6/23) | 1500 | LIFT STATION & TWO MANHOLES | RAIN 3.15" | TOWN UPGRADING WWTP
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-07-12 | 7/12 |  | MANHOLE 15, 145 | RAIN 2.4" | TOWN IN MIDDLE OF PLANT UPGRADE
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-09-12 | 06:45 - 09:30 | 15000 | MANHOLE # 145, LIFT STATION # 2 ON SAWMILL RD | RAIN 3.05", LIFT PUMP # 1 FAILURE | WEEKLY INSPECTIONS OF LIFT PUMPS, BEING UPGRADED
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-09-13 | 09:30 - 10:30 | 5000 | MANHOLE # 145 LS #2 | RAIN 1.25"
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-09-18 | 9/18 | 20000 | LIFT STATION # 1, MANHOLE # 145 | RAIN 2.3", AUTO DIALER FAILURE | SUBCONTRACT VAC TRUCK TO PUMP & HAUL
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-11-16 | 11/16 |  | MAIN LIFT STATION ON SAWMILL ROAD | RAIN 2", LIFT STATION CAN'T KEEP UP | COLLECTION SYSTEM IMPROVEMENTS BEING DESIGNED
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2006-12-12 | 8:00A - 10:45A | 2000 | 408 SAWMILL RD LIFT STATION | RAIN 1.5", BOTH LIFT STATION PUMPS NOT WORKING (VACUUM) | LIFT STATION TO BE UPGRADED
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2006-01-31 | 10:00 - 14:00 | 10800 | SEWER LINE BETWEEN FGD THICKNERS & WWT | PUMP FAILURE FGD SYSTEM, FLOW ROUTED TO WWTP | EVALUATION OF EQUIPMENT TO PREVENT RECURRENCE
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2006-02-02 | MIDNIGHT - 10:00A | 250000 | FROM EMER HOLDING BASIN TO DISCHARGE CANAL 001 | PUMP FAILURE IN # 2 FGD CAUSED PLUGAGES OF PIPING | EVALUATIONS OF EQUIP AND PROCESSES
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2006-03-01 | 07:00 - 13:00 (3/4) | 73800 | SEAL WATER TANK OVERFLOW (MAKEUP WELL WATER) | LEVEL CONTROL VALVE LEAKING, TO BE REPLACED
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2006-03-09 | 3/9 - 3/15 |  | BASIN 2 | RAIN 2.5" | KEEP BASIN LEVEL LOW
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2006-04-07 | 19:37 - 09:00 (4/10) |  | BASIN 2 OVERFLOW | RAIN 1.5", UNIT OUTAGES | PLANS BEING DEVELOPED FOR WATER & WASTEWATER MGT
IN0040134 | HYMERA MUNICIPAL STP | SULLIVAN | 2006-03-11 | 3/11 - 3/13 | 5000 | MAIN ST LIFT STATION # 2, MANHOLES | RAIN 5" | LOOKING FOR INFLOW SOURCES
IN0040134 | HYMERA MUNICIPAL STP | SULLIVAN | 2006-03-21 | 3/21 - 3/22 | 2000 | LS # 1 DEPOT ST | LS # 1 TRIPPED OUT, MOISTURE IN ELECTRICAL COMPONENTS | RESET PUMPS, PICKED UP DEBRES
IN0040134 | HYMERA MUNICIPAL STP | SULLIVAN | 2006-04-10 | 4/10 | 5000 | MANHOLE LS # 1 | RAIN 3"
IN0040134 | HYMERA MUNICIPAL STP | SULLIVAN | 2006-08-08 | 12:00 - 15:00 (8/9) | 20000 | LIFT STATION # 2 | RAIN - LS PUMP AIR LOCKED, OVERFLOW FROM OVERFLOW CAP | CITY WORKING TO REVAMP WWTP & LIFT STATIONS
IN0040134 | HYMERA MUNICIPAL STP | SULLIVAN | 2006-11-08 | ? - 09:41 | 500 | LIFT STATION # 1 | RAIN 0.8", BOTH LIFT PUMPS TRIPPED OUT | TO REBUILD LIFT STATION, CHECK LIFT STATION DURING RAIN EVENTS
IN0030228 | SHAKAMAK STATE PARK | SULLIVAN | 2006-08-31 | ? - 3:30P | 5000 | SEWER LINE | CONTRACTOR HIT SEWER WITH BORING EQUIPMENT | REPAIRED, LIME APPLIED
IN0024554 | SULLIVAN MUNICIPAL STP | SULLIVAN | 2006-08-07 | 2:30P |  | FIELD TILE DRAIN BY STORM POND OVERFLOW | INVESTIGATING FLOW FROM FIELD TILE
IN0058041 | EAST ENTERPRISE RSD | SWITZERLAND | 2006-10-16 | 10/16 - 10/17 | 50000 | PLANT | RAIN 5"
IN0056391 | PATRIOT MUNICIPAL STP | SWITZERLAND | 2006-03-12 | 1:00 - 3:00 |  | FINAL LIFT STATION | RAIN 4"
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2006-06-26 | 10:00 - NOON (6/27) |  | FORCE MAIN | FORCE MAIN FAILURE | REPLACED AFFECTED SEGMENT OF FORCE MAIN
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2006-10-02 | AM - 18:30 |  | FORCE MAIN IN WOODS | BROKEN FORCE MAIN | HAULING WASTE WATER TO STP UNTIL REPAIRED
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-01-31 | 2:00P - 2:45P | 100 | 3543 MCCARTY LANE | ILLEGAL SEWER CONNECTION, SUMP PUMP FAILURE | AREA TO BE CLEANED. RESIDENTS MOVING, LINE PLUGGED
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-02-01 | 11:25A - 12:00P | 20 | MANHOLE 2406 SOUTH 30TH ST | SEWER LINE PLUGGED, JET CLEANED SEWER & AREA | WILL DO TELEVISION FOLLOWUP ON SECTION OF SEWER
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-05-03 | 1:15P - 7:49P | 1750000 | SOUTH SIDE OF LAFAYETTE | COLLAPSE OF 36 TO 48" SEWER, REPORT FROM IDEM ER | MAKING EMERGENCY REPAIRS - NEW LIFT STATION & SEWER
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-05-03 | 5:28A - 4:20P | 210600 | 003 CINCINNATI ST | WATER PLANT DRAINING COOLING TOWER FOR CLEANING ADDED FLOW | STOPPED WATER TOWER FLOW, COMMUNICATION WITH WATER PLANT
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-07-09 | 12:00P - 8:00 | 100000 | PEARL RIVER LIFT STATION | DUKE ENERGY POWER FAILURE - USED GENERATOR - POWER SURGE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-07-12 | 7/12 | 1000000 | PARKING LOT LIFT STATION | MAIN BREAKER FOR PUMPS FAILED - PUMPS BURNED UP | UNDER CONSTRUCTION OF NEW REGIONAL LIFT STATION
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-07-17 | 1:00P - 1:15P | 1000 | OVERFLOW 012 - FAIRGROUNDS | EQUIPMENT FAILURE - VANDALISM OF OVERFLOW GATE | REPAIRED GATE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-11-01 | 8:20A - 9:00A | 600 | MANHOLE 605 BRAZOS TRAIL | PLUGGED SEWER | SEWER JET VAC'D APPROXIMATELY 150 FT
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-11-03 | 10:13A - 10:15A | 5000 | OVERFLOW # 009 | TRANSDUCER MALFUNCTION AT HEADWORKS | PLACING TRANSDUCERS ON MONTHLY CLEANING SCHEDULE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-11-10 | 6:30P - 7:00P | 1000 | MANHOLE IN VALLEY OFF OF OLD US 231 | BLOCKED SEWER (STICKS & DEBRIS POSSIBLE VANDALISM) | SEALING MANHOLES
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-11-11 | 4:43P - 6:32P | 150000 | LIFT STATION - PARKING LOT | 2 OF 3 PUMPS PLUGGED WITH DEBRIS FROM HEAVY RAIN | CONSTRUCTION UNDERWAY ON NEW LIFT STATION WITH SCREENING
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-11-17 | 9:35A - 10:03A | 10000 | OVERFLOW # 011 (14TH STREET) | DEBRIS BLOCKED CHANNEL DUE TO 2" RAIN | CONTINUE POST RAIN EVENT INSPECTIONS
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-11-30 | 7:15 - 8:30A | 75000 | 1ST MANHOLE UPSTREAM OF PRAIRE OAKS LIFT STATION | RAIN SENDING ROOTS & DEBRIS PLUGGING PUMPS AT LIFT STATION | CONTINUED INSPECTION OF COLLECTION SYSTEM
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-12-19 | 3:48A - 4:35A | 48000 | PARKING LOT LIFT STATION - OVERFLOW 003 CINCINNATI ST | BREAKER AT THE LIFT STATION TRIPPED OUT | NEW PARKING LOT LIFT STATION SCHEDULED COMPLETE IN 2007
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-12-26 | 6:58A - 7:30A | 111000 | CSO 004 | SHORT IN # 3 PUMP AT PARKING LOT LIFT STATION | NEW STATION BEING BUILT 8/2007
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-01-13 | 1:35P |  | CATCH BASIN STATE STREET & NORTHWESTERN | CLOGGED SEWER, RAIN | SET UP BYPASS PUMP & CLEANING SEWER
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-03-10 | 3/10 | 10000 | GREEN MEADOWS LIFT STATION | RAIN 1.26" | SCHEDULED TO BE REPLACED THIS YEAR
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2006-09-10 | 3:00 |  | PRIVATE MANHOLE AT DOG & SUDS | PRIVATE SEWER CLOGGED | W LAFAYETTE CLEANED SEWER & USED VACTOR TO CLEAN AREA
IN0021474 | TIPTON MUNICIPAL STP | TIPTON | 2006-12-22 | 11:00 - 24:00 | 29710 | LIFT STATION A | RAIN 0.9" | WORKING ON I & I REDUCTION
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2006-06-23 | 12:11A - 4:36A | 5300000 | EAST WWTP | RAIN 1.2", PLC FAILURE THAT CONTROLS INFLUENT PUMPS | OPERATORS INSTRUCTED TO OBSERVE CHART RECORDER & PLC
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2006-08-30 | 6:50P - 4:30A (8/31) | 186177 | WWTP DIVERSION STRUCTURE - BLENDED WITH WWTP EFFLUENT | PLC FAILURE AT INFLUENT GATE | PLC INSPECTED & TESTED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2006-09-01 | 2:15A - 4:45A | 96215 | EAST WASTEWATER TREATMENT PLANT | BLOCKAGE AT THE TRANSDUCER CAUSING INFLUENT GATE TO CLOSE | AREA AROUND TRANSDUCER WILL BE INSPECTED DAILY
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-03-08 | 3:00P - AM (3/9) | 40000 | FORCE MAIN BROADWAY AVE & CARPENTER CREEK BRIDGE | LEAKINF FORCE MAIN | SEWER LINE TO BE INSPECTED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-04-20 | 12:00P - 12:30P | 2000 | MANHOLE JOHNSON LANE & BERNICE RD | STARTER PN PUMPS FAILED AT THE BROADWAY & JOHNSON LIFT STATION | STARTER REPAIRED, AREA TO BE INSPECTED DAILY
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-04-20 | 12:00P - 12:30P | 2000 | MANHOLE IN FIELD - JOHNSON LANE & BERNICE RD | STARTER FAILURE AT BROADWAY & JOHNSON LIFT STATION | AREA TO BE INSPECTED DAILY
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-06-23 | 9:00A - 9:15A | 1000 | MANHOLE NEAR PPG LIFT STATION | RAIN 1.2" | AREA TO BE MONITORED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-07-05 | 11:35A - 4:00P | 2000 | FORCE MAIN 15000 BLOCK US HIGHWAY 41 | FORCE MAIN DEVELOPED A DIME-SIZED LEAK | INCREASED PATROLS WILL BE CONDUCTED IN THE AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-07-12 | 9:10A - 3:00P | 198182 | BROADWAY & JOHNSON LIFT STATION | RAIN 2.77" | SEWER TO BE REPLACEDWITH A NEW GRAVITY LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-08-30 | 10:55A - 11:45A | 1500 | 8" GRAVITY SEWER ALONG ST GEORGE RD | SEWER DAMAGED BY COUNTY WORK CREW | SEWER TO BE MONITORED FOR LEAKS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-08-31 | 9:55A - 10:00A | 200 | NOURBORNE & MILL RD | UNTREATED RELEASE DURING MANHOLE REPLACEMENT | WILL MONITOR FOR LEAKS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-09-22 | 5:45P - 2:30P (9/23) | 905288 | BROADWAY & JOHNSON LIFT STATION | RAIN 4.5" | SITUATION TO BE MONITORED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-09-23 | 2:40P - 11:15P | 491448 | BROADWAY & JOHNSON LIFT STATION | RAIN 4.76" | SITUATION TO BE MONITORED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-10-16 | 2:00P - 10:00A (10/17) | 531421 | BROADWAY & JOHNSON LIFT STATION | RAIN 2.5" | SEWER LINE HAS BEEN BID FOR REPLACEMENT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-10-27 | 8:10A - 4:00A (10/28) | 676530 | BROADWAY & JOHNSON LIFT STATION | RAIN 2.+" | SEWER LINE HAS BEEN BID FOR REPLACEMENT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-11-02 | 1:30P - 2:30P | 9018 | BROADWAY & JOHNSON LIFT STATION | PUMP FAILURE & REPLACEMENT | INCREASE PATROL OF SITE TO ENSURE NO PROBLEM WITH NEW PUMP
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-11-06 | 7:15P - 11:15P | 45000 | BROADWAY & JOHNSON LIFT STATION | RAIN 1" | BIDS SUBMITTED FOR SEWER LINE REPLACEMENT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-11-15 | 3:15P - 2:30P (11/16) | 275000 | BROADWAY & JOHNSON LIFT STATION | RAIN 1.6" | BIDS SUBMITTED TO REPLACE SEWER LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-11-30 | 11/30 - 12/1 | 501756 | BROADWAY & JOHNSON LIFT STATION | RAIN 1.5" | SEWER LINE BID FOR REPLACEMENT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-12-12 | 8:30A - 11:15P | 436727 | BROADWAY & JOHNSON LIFT STATION | RAIN 1.5" | BIDS BEING RECEIVED FOR SEWER LINE REPLACEMENT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-12-22 | 2:30A - 1:10P | 680000 | BROADWAY & JOHNSON LIFT STATION | RAIN 1.3" | SEWER TO LIFT STATION TO BE REPLACED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2006-12-25 | 12/25 - 12/26 | 540000 | BROADWAY & JOHNSON LIFT STATION | RAIN 1.2" | LINE FEEDING LIFT STATION TO BE REPLACED
IN0003506 | NEWPORT CHEMICAL DEPOT | VERMILLION | 2006-09-14 | 9:00A | 5 | 3" SEWER LINE | CONTRACTOR DAMAGED SEWER LINE | ENSURE EQUIPMENT OPERATORS ARE AWARE OF UTILITIES
IN0001601 | AET PACKAGING FILMS | VIGO | 2006-06-21 | 08:25 - 08:45 | 350 | WASTED SLUDGE PIT OVERFLOW | WASTING VALVE NOT FULLY CLOSED | INVESTIGATE AUTOMATING / MONITORING LEVEL IN SLUDGE PIT
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-03-12 | 3/12 |  | WEST POLISHING POND & EQ BASIN OVERFLOWING | RAIN 2"
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-03-30 | 3/30 | 10000 | WEST POLISHING POND OVERFLOWING | WEST POLISHING POND DISCHARGE LINE PLUGGED WITH DEBRIS | CLEAR DISCHARGE LINE
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-03-31 | 3/31 | 20000 | WEST POLISHING POND OVERFLOW | RAIN 0.94" | HAVING DISCHARGE LINE CLEARED WITH JET
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-05-09 | EARLY AM - 2:00P | 100000 | FRY ROAD LIFT STATION | LIFT STATION FAILURE (ELECTRICAL) | REMOVE DEBRIS, APPLIED LIME
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-06-11 | 6/11 |  | MAIN LIFT STATION MANHOLE | RAIN 0.66" - STATION DOWN - LIGHTNING STRIKE | CLEAN AREA, APPLY LIME
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-06-19 | 6:00P | 90000 | MAIN LIFT STATION FRY RD | LIFT STATION PUMP FAILURE | CLEAN AREA AROUND LIFT STATION
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-07-27 | 7/27 | 25000 | MAIN LIFT STATION | LIFT STATION DOWN - POWER FAILURE | REMOVE DEBRIS
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-07-29 | 8:00P - 9:00A (7/31) | 234000 | MAIN LIFT STATION ON FRYE RD | LIFT STATION DOWN OVER THE WEEKEND, PROBLEM IN THE CONTROLS' | CALLED SERVISE, REMOVER DEBRIS, APPLIED LIME
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-09-26 | 9:00P - 9:30A (9/27) | 48750 | MAIN LIFT STATION MANHOLE | POWER FAILURE BOTH PUMPS TRIPPED OUT
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-11-16 | 10:00A - 11:00A | 2500 | WEST POLISHING POND | RAIN 1.58"
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-12-01 | 6:00A - 12:15P | 32400 | WWTP WEST POLISHING POND | RAIN 2.65"
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-12-12 | 12:00P - 2:15P | 7500 | OVERFLOW OF WEST POLISHING POND | RAIN 1.2", PUMP FAILURE | DIVERTED FLOW TO EQ BASIN
IN0020800 | RILEY MUNICIPAL STP | VIGO | 2006-12-26 | AM - 12:15P | 40000 | FINAL EFFLUENT POLISHING POND | RAIN 0.77", POSSIBLY DEBRIS IN OUTFALL LINE | USE EXCESS FLOW PUMPS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-01-24 | 10:00A - 10:18A | 100 | WOODGATE SOUTH LIFT STATION | POWER / EQUIPMENT FAILURE, MAIN BREAKERS TRIPPED | RUNNING TEST ON EQUIPMENT OT IDENTIFY PROBLEM
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-01-27 | 7:30A - 7:40A | 100 | WOODGATE SOUTH LIFT STATION | EQUIPMENT / POWER FAILURE (MOTOR STARTERS) | REPLACED MOTOR STARTERS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-01-29 | 9:00A - 9:45A | 150 | GLEN NORTH LIFT STATION | RAIN 1.2", STATION HAVING TROUBLE KEEPING UP | CALLED VACTOR TRUCK
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-01-29 | 11:55A - 1:00P | 319000 | PRIMARY TANKS TO FINAL CONTACT TANK | RAIN 1.2", EQUALIZATION'S WERE FULL, PLANT AT CAPACITY
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-02-02 | 9:20P - 10:00P | 100 | WOODGATE SOUTH LIFT STATION | RAIN 0.75",FLOW TOO MUCH FOR STATION TO KEEP UP | WORKING ON UPDATING / UPSIZING STATION
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-02-02 | 7:40P - 9:10P | 286000 | PRIMARY SEDIMENTATION TANKS (PARTIALLY TREATED) | RAIN 0.75", EQ BASINS FULL
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-03-09 | 3/9 - 3/10 | 6969000 | PRIMARY SEDIMENTATION TANKS | RAIN 1.5"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-03-09 | 3/9 - 3/10 | 3000 | WOODGATE NORTH MANHOLE & S LIFT STATION | RAIN 2.3"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-03-12 | 6:15P - 11:15P | 5800000 | PRIMARY SEDIMENTATION TANKS | RAIN
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-03-12 | 3/11 - 3/12 | 7000000 | PRIMARY SEDIMENTATION TANKS, PLUGGED SEWER (JESICA DR) | RAIN
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-03-13 | 3/13 | 1300 | WOODGATE S LIFT STATION & WYNDAM LIFT STATION | RAIN
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-03-13 | 9:30A - 12:10P | 1400000 | PRIMARY SEDIMENTATION TANKS | RAIN
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-03-31 | 7:55A - 11:15A | 6000 | WOODGATE SOUTH LIFT STATION | RAIN | VACTORED OUT FIVE LOADS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-04-03 | 9:05A - 10:15A | 500 | WOODGATE SOUTH | POWER FAILURE DUE TO STORMS | GENERATOR USED UNTIL POWER RESTORED
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-04-06 | 12:25P - 10:45A (4/7) | 4200 | WOODGATE SOUTH | RAIN 2", LIFT STATION NOT ABLE TO KEEP UP | COMBO TRUCK - 2 LOADS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-04-06 | 5:30P - 7:30A (4/7) | 5700000 | PRIMARY CLARIFIER TO FINAL CONTACT TANK | RAIN 2", EQ BASIN FULL
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-04-07 | 7:37A - 9:20A | 16800 | WOODGATE NORTH | RAIN 2", LIFT STATION NOT ABLE TO KEEP UP | COMBO TRUCK - 8 LOADS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-04-20 | 10:50A - 11:25A | 2000 | SEELYVILLE LIFT STATION | LIFT STATION POWER FAILURE (CINERGY)
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-05-10 | 11:33P - 8:45A (5/11) | 3700000 | PRIMARY SEDIMENTATION TANKS TO FINAL CONTACT TANK | RAIN 1.5"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-05-24 | 9:00A - 9:15A | 300 | WYNDHAM LIFT STATION | CONTRACTOR DROVE A COPPER GROUND ROD THROUGH FORCE MAIN | CREW TO REPAIR FORCE MAIN, PUT STATION ONLINE
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-06-02 | 6:00A - 7:30A | 1000000 | PRIMARY SEDIMENTATION TANKS TO FINAL CONTACT TANK | RAIN
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-06-02 | 12:10A - 12:20A | 160 | GLENN NORTH LIFT STATION | RAIN 0.8"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-07-10 | 4:00P - 4:30P | 500 | PRISON LIFT STATION # 77 | DUKE ENERGY SHUT DOWN POWER TO MOVE TELEPHONE POLES
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-09-04 | 3:13P - 3:30P | 100 | 46TH & POPLAR LIFT STATION | LIFT STATION FLOAT FAILURE ALLOWING STATION TO FLOOD | FLOAT REPLACED, VACTOR CREW CLEANED DITCH
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-09-18 | 8:55A - 11:38A | 1700000 | PRIMARY SEDIMENTATION TANKS (PARTIALLY TREATED) | RAIN 1"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-10-17 | 3:50A - 9:45A | 2300000 | PRIMARY SEDIMENTATION TANK | RAIN 2.5"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-10-27 | 12:23P - 10:05P | 4000000 | PRIMARY SEDIMENTATION TANK | RAIN 1" | FEASIBILITY STUDY TO DETERMINE PLANT NEEDS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-11-16 | 11:00 - 1:20 | 1300 | WOODGATE SOUTH LIFT STATION # 39 | RAIN 0.9"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-11-16 | 4:40P - 11:00P | 1000000 | PRIMARY SEDIMENTATION TANK | RAIN 1.1"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-11-16 | 10:30 - 1:20 | 1500 | DALLAS ROAD | RAIN 0.9"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-11-16 | 10:50P - 2:00P | 900000 | PRIMARY SEDIMENTATION TANK | RAIN 0.9"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-12-01 | 12:35A - 8:00A | 5500000 | PRIMARY SEDIMENTATION TANKS | RAIN 1.95" | REVIEWING BYPASS & OVERFLOW CONTROL
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-12-12 | 2:07P - 7:25P | 2700000 | PRIMARY SEDIMENTATION TANK | RAIN 1.55" | GOING THROUGH FEASIBILITY STUDY RE: NEW PLANT
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-12-12 | 3:30P - 4:27P | 1000 | SEELYVILLE LIFT STATION # 022 | RAIN, DUKE ENERGY POWER FAILURE
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-12-22 | 6:30A - 1:10P | 3400000 | PRIMARY SEDIMENTATION TANKS | RAIN 0.75" | FEASIBILITY STUDY REGARDING WWTP
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2006-12-31 | 2:30P - 3:30P |  | WOODGATE SOUTH LIFT STATION #039 | RAIN 0.08" - HEAVY RAIN FOR TWO DAYS
IN0055085 | WEST TERRE HAUTE MUNICIPAL STP | VIGO | 2006-04-03 | 7:00P - 10:45P | 1800 | 5472 W SMITH MEYERS FORCE MAIN | EQUIPMENT FAILURE | REPLACE BLOW OUT VALVE, PRESSURE TEST
IN0055085 | WEST TERRE HAUTE MUNICIPAL STP | VIGO | 2006-05-26 | 9:00A - 10:00A | 500 | 148 WINDEMERE ROAD FORCE MAIN | BROKEN LATERAL CONNECTION | VACTOR UP EXCESS WASTEWATER
IN0055085 | WEST TERRE HAUTE MUNICIPAL STP | VIGO | 2006-09-01 | 3:00P - 8:00P | 250 | RESIDENTAL GRINDER | EQUIPMENT FAILURE - REPLACED FAULTY CHECK VALVE
IN0055085 | WEST TERRE HAUTE MUNICIPAL STP | VIGO | 2006-11-18 | 20:00 - 21:00 | 200 | 479 KENWOOD - RESIDENTIAL GRINDER | PUMP FAILURE IN RESIDENTIAL GRINDER STATION | REPLACE PUMP, CONTINUED MONITORING
IN0020371 | LAFONTAINE MUNICIPAL STP | WABASH | 2006-09-25 | 10:00A - 12:30P | 7000 | MANHOLE AT LIFT STATION # 3 | OVERFLOW DURING SWITCH OVER TO LIFT STATION REPLACEMENT | NEW PUMPS & PANEL OPERATIONAL
IN0022420 | BOONVILLE MUNICIPAL STP | WARRICK | 2006-01-24 | 4:00A - 07:30 | 100 | WASSON LIFT STATION | POWER FAILURE | INSPECTION OF LIFT STATION
IN0022420 | BOONVILLE MUNICIPAL STP | WARRICK | 2006-02-16 | 10:00P - 3:00A (2/17) | 100 | SHANEE MEADOWS LIFT STATION | RAIN 0.7", POWER FAILURE (VECTREN)
IN0022420 | BOONVILLE MUNICIPAL STP | WARRICK | 2006-05-25 | 12:00A - 1:00A |  | TAYLOR LIFT STATION | RAIN 1.65", POWER FAILURE (STORM) | TRYING TO ACQUIRE PORTABLE GENTRATOR
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-03-09 | 3/9 |  | MANHOLE 7-198, 4-1 | RAIN 2.76"
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-05-15 | 11:30A - 2:45P | 5000 | SEWER MAIN BETWEEN MANHOLE 7-162 & 7-150 - COAL MINE RD | WARRICK CO HIGHWAY DEPT DAMAGED SEWER DURING CONST | REPAIRED
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-06-08 | 6/8 |  | 17 WYANDOTTE, PUEBLO TRAILER PARK | SEWER LATERAL DAMAGED BY VECTRON WHILE RESETTING LIGHT POLE
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-06-09 | 6/9 |  | LIFT STATION # 5 - W MANCHESTER BLVD | FLOAT FAILURE IN LIFT STATION
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-06-12 | 6/12 - 6/13 |  | OVERFLOW UNDER A MOBILE HOME - 706 BERKSHIRE | BLOCKAGE IN A LATERAL (PRIVATE COLLECTION SYSTEM)
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-07-12 | 10:30A - 2:45P |  | MANHOLE # 7-198 7 # 4-1 | RAIN
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-08-30 | ? - 07:05 |  | MANHOLE1-15 INDERREDEN & LEE DR | EMPLOYEE FAILED TO TURN PUMPS ON AFTER MAINTTNANCE
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-09-03 | 10:00A - 11:00A |  | GREEN VALLEY LIFT STATION # 1 - 15 MANHOLE | FLOAT FAILED IN LIFT STATION | REPLACED FLOAT
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-09-12 | 9/12 |  | MANHOLE # 7-198 | RAIN 2.35"
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-09-22 | 8:30P - ? |  | MANHOLES # 7-198, 7-199 | RAIN 5.7" | I&I REDUCTION
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-09-22 | 8:30P - ? |  | #2 LIFT STATION (4TH STREET) WET WELL, #2-1, 2-2 MANHOLES | RAIN 5.7" | PLAN TO REPLACE LIFT STATION
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2006-11-04 | 11/4 |  | MANHOLE # 1-15 INTERSECTION OF LES DRIVE & INDERIEDEN RD | EQUIPMENT FAILURE AT LIFT STATION
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-03-09 | 9:30A - 9:50P |  | MANHOLE 0 | RAIN 1.4" | I&I STUDY
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-03-10 | 4:15A - 10:30A | 25000 | MANHOLE 0 | RAIN 2.5" | I&I STUDY
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-03-11 | 8:00A - 5:34P | 45000 | MANHOLE 0 | RAIN 2.5" | I&I STUDY
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-03-12 | 2:30A - 4:15P | 50000 | MANHOLE 0 | RAIN 3.25" | I&I STUDY
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-05-02 | 4:00A - 4:00P | 4500 | MANHOLE AT PLANT OFF SEVEN HILLS RD | RAIN 1.8" | WORKING ON I & I IDENTIFICATION & REPAIR
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-07-12 | 10:15A - 11:50A | 7500 | MANHOLE # 0 - 11511 SEVEN HILLS RD | RAIN 5.4" | TOWN WORKING ON I&I STUDY
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-09-22 | 9/22 - 9/23 | 9000 | # 1 | RAIN 5" | COMMONWEALTH IS WORKING ON I&I STUDY
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-11-16 | 9:10A - 9:30A | 400 | MANHOLE # 1 | RAIN 2.5" | CLEAN UP DEBRIS TREATED AREA
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-12-12 | 12/12 |  | MANHOLE # 0 | RAIN 1.6" | CLEAN UP DEBRIS, COMMINWEALTH WORKING ON I&I STUDY
IN0020788 | ELBERFELD MUNICIPAL STP | WARRICK | 2006-12-22 | 4:45A - 6:00A | 2200 | MANHOLE # 0 | RAIN 1.6" | CONDUCTING I&I STUDY
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-01-13 | 1:00P - 9:30P | 4000 | MANHOLE AT VINE & HWY 68 | RAIN 1.4" | INCREASE FORCE MAIN FROM LS, REPAIR, ELIMINATE I&I
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-01-23 | 7:00A - 12:30P | 1500 | MANHOLE WEST OF VINE & HWY 68 | RAIN | REPAIR SEWER ENLARGING FORCE MAIN FROM MAIN LIFT STATION
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-03-09 | 3/9 - 3/10 | 25000 | MANHOLE VINE & HWY 68 | RAIN 4.1" | INCREASING DIAMETER OF FORCE MAIN
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-03-10 | 3/10 - 3/13 | 86000 | MANHOLE VINE & HWY 68 | RAIN 5.7" | REPAIRED DAMAGED SEWER LINES
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-03-13 | 10:00A - 1:00P | 1500 | MANHOLE AT VINE & HWY 68 | RAIN 0.3" | INCREASING SIZE OF FORCE MAIN
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-04-06 | 7:00P - 9:00P | 5000 | MANHOLE AT HWY 68 & VINE | RAIN 0.9" | REPLACE FORCE MAIN TO PLANT, 4" TO 6" LINE
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-04-21 | 4/21 - 4/22 | 7500 | VINE ST & HWY 68 | RAIN 1.6" | IMPROVEMENTS TO MAIN LIFT STATION & FORCE MAIN
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-05-02 | 4:00A - 5:00P | 4000 | MANHOLE AT VINE ST & HWY 68 | RAIN 1.5" | WORKING ON MAIN LIFT STATION REPAIR
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-05-27 | ? - 10:00A | 5000 | MAIN LIFT STATION | RAIN 0.9", LIFT STATION FLOAT MALFUNCTION | TO INSTALL PHONE DIALER ON MAIN LIFT STATION
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-06-02 | 6/2 - 6/3 | 7500 | MANHOLE AT INTERSECTION OF VINE & HWY 68 | RAIN 1.7", SEWER COLLAPSED | NEW FORCE MAIN AT MAIN LIFT STATION PENDING
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-07-12 | 7:00A - 7:00P | 7000 | MANHOLE AT VINE AND HWY 68 | RAIN 4.9" | WORKING ON I & I REDUCTION, INCREASING FORCE MAIN PIPE SIZE
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-09-12 | 9:00A - 12:00P | 2500 | MANHOLE AT VINE & HWY 68 | RAIN 3.6" | DESIGNING NEW LIFT STATION & REPAIR TO SEWER LINES
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-09-22 | 9/22 - 9/24 | 150000 | MANHOLE @ VINE & HWY 68 | RAIN 3.6" | NEW LIFT STATION BEING DESIGNED & REPAIRS TO SEWERS
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-10-27 | 10/27 - 10/28 | 7500 | MANHOLE AT VINE ST & HWY 68 | RAIN 2.5" | PLANS TO REPAIR SEWER LINES & LIFT STATION
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-11-07 | 9:00A - 3:00P | 4000 | MANHOLE AT VINE & HWY 68 | RAIN 1" | ENGENEERING PLANS FOR NEW LIFT STATION & SEWER REPAIRS
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-11-16 | 5:30A - 12:00 | 500000 | MANHOLE AT VINE & HWY 68 | RAIN 2.4" | REPAIRS TO MAIN LIFT STATION & SEWERS TO START SPRING 2007
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-12-12 | 9:00A - 10:00P | 10000 | MANHOLE VINE & HWY 68 | RAIN 1.7" | TOWN SEEKING GRANT TO REPAIR SEWERS
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2006-12-21 | 12:00 - 12:00 (12/22) | 7500 | MANHOLE AT VINE & HWY 68 | RAIN 1.4" | WORKING ON REPAIR OF SEWER LINES & ENLARGING LIFT STATION
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-05-20 | 9:30A - 1:00P | 3500 | MANHOLE 4500 BELL ROAD | DEBRIS IN MANHOLE CREATING SEWER BLOCKAGE | SUSPECT MANHOLE FRAME HAS BEEN DAMAGED - TO REPAIR
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-06-01 | 6/1 - 6/3 | 87500 | MANHOLE NO 12-17 @ 8255 COBBLESTONE CT | EMPLOYEE FAILED TO TURN PUMPS & DIALER ON AFTER MAINTENANCE | TOWN REVIEWING DISCIPLINARY ACTION
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-06-02 | 10:30A - 11:15A | 7000 | BROKEN FORCE MAIN @ POLLACK AVE & LISA LN | POLLACK AVE LIFT STATION EXPERIENCED A FORCE MAIN BREAK | FORCE MAIN SCHEDULED FOR REPLACEMENT THIS YEAR
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-07-12 | 11:00A - 11:45A | 5000 | MANHOLE # 23-120 (2422 BRIARCLIFF DRIVE) | RAIN 2.5" | PROBLEM BLUE LAKE LIFT STATION TO BE CORRECTED
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-09-12 | 3:30P - 4:30P | 1000 | MANHOLE # 23-120 (2422 BRIARCLIFF DR) | RAIN 5" | PER SUBMITTED TO TOWN COUNCIL FOR LIFT STATION
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-09-23 | 6:00A - 4:30P | 5000 | MANHOLES 09-45, 23-120, 09-130 | RAIN 6" | REMEDIATION OF BLUE LAKE LIFT STATION, EVAL COLLECTION SYSTEM
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-09-23 | 3:00A - 8:00A | 5000 | MANHOLE 02-56 IN COLONIAL HILLS SUBDIVISION | RAIN 5" | SEWER AREA TO BE JET CLEANED & TV INSPECTED
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-09-28 | 4:00P - 4:10P | 200 | RESIDENTIAL CLEANOUT @ 7899 MEADOW LANE | SEWER MAIN CLOGGED | SEWER TO BE TELEVISED VIDEO INSPECTED FOR PROBLEMS
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-10-27 | 1:30P - 4:30P | 18000 | MANHOLE 13-204 | RAIN 2.35" - PUMP STATION # 2 OVERLOADED | TOWN TO UPGRADE LIFT STATION
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2006-12-20 | 2:00P - 2:10P | 500 | ITT LIFT STATION FORCE MAIN | CONTRACTOR DAMAGED FORCE MAIN WHILE WORKING IN AREA | REFERRED TO UTILITY COMM & TOWN COUNCIL
IN0002259 | SIGECO, F. B. CULLEY STATION | WARRICK | 2006-01-16 | 1/15 - 1/16 | 600000 | BROKEN UNDERGROUND LINE ALLOWED DISCHARGE TO RIVER | BROKEN LINE DIVERTED CLARIFIED RIVER WATER FROM ASH POND | DISCHARGE PIPE CLEANED, LINE REPAIRED, POND LEVEL RAISED
IN0021059 | NEW PEKIN MUNICIPAL STP | WASHINGTON | 2006-03-10 | 3/10 - 3/13 | 500000 | MAIL LIFT STATION | RAIN 7.8"
IN0021059 | NEW PEKIN MUNICIPAL STP | WASHINGTON | 2006-09-22 | 11:00P - 9:30P (9/23) |  | LIFT STATION | RAIN 5.6"
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-01-02 | 5:30P - 700P |  | WATER & EMMA LIFT STATION | POWER FAILURE, CINERGY
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-01-02 | 5:30P - 7:00P |  | WATER & EMMA LIFT STATION | POWER FAILURE (CINERGY)
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-01-27 | 1/27 | 500 | CLEANOUT | BLOCKAGE
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-02-17 | ? - 7:30A |  | MANHOLE 32 JACKSON ST | RAIN 0.59", BLOCKAGE IN MAIN
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-03-09 | 3/9 |  | MANHOLES 32, 613, 614, 354 | RAIN 2.16"
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-03-09 | 2:30P - 3:00P | 300 | SOUTHWAY VILLA LIFT STATION | POWER FAILURE
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-03-11 | 3/11 |  | MANHOLES 97, 360, 576, 16, 458, 450 & 613 | RAIN 2.56"
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-03-12 | 3/12 |  | MANHOLES 97, 613, 360, 458, LAGOON OVERFLOW | RAIN 2.66", SEWER BLOCKAGE
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-03-13 | 8:00A |  | LAGOON OVERFLOW | RAIN 7.5"
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-04-02 | 11:00P - 12:00P |  | SMALL ST, HOBBS & JEANS PUMP STATIONS | RAIN 0.35", POWER FAILURE (STORM)
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-10-17 | 9:00A - 9:30A | 5000 | MANHOLE | RAIN 2.14", ROOTS IN 8" CLAY LINE | TV LINE & DEROOT
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-11-15 | 1:30P - 2:17P |  | LIFT STATION - PINE MEADOW | RAIN 0.93", CONTRACTOR HIT 8" MAIN WHILE LAYING CABLE | REPAIRING PIPE
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-12-01 | 1:00A - 1:20P |  | MANHOLE 438, 290 | RAIN 2.21", MANHOLES BLOCKAGE - GREASE | TO TELEVISE AND MAKE REPAIRS
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2006-12-01 | 7:00A - 1:20P |  | NEW STANDISH STATION MANHOLE 290 | RAIN 2.21" - ADJUSTING NEW STATION - GREASE IN MANHOLE | WILL TELEVISE AND ASSESS REPAIRS
IN0040029 | FOUNTAIN CITY MUNICIPAL STP | WAYNE | 2006-02-28 | 2/28 - 3/1 |  | OUTFALL 001, DISCHARGE ABOVE 1/10 STREAM FLOW RATE | UNIT VANDALIZED FORCING OPEN DISCHARGE VALVE | CHAIN & PADLOCK INSTALLED ON DISCHARGE WHEEL
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-02-24 | 1:30A - 7:45A | 300000 | SHORT CREEK LIFT STATION | PUMP / POWER FAILURE, RICHMOND P & L WORKING ON POWER GRID | CONSIDERING REDUNDANT POWER SUPPLY FOR LIFT STATION
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-03-12 | 3/12 | 300000 | SO 11TH & G | RAIN 3", BYPASS TO RELIEVE RESIDENTIAL FLOODING
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-03-12 | 3/12 | 400000 | 2011 BOSTON PIKE | RAIN 3", BYPASS TO RELIEVE RESIDENTIAL FLOODING
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-03-12 | 3/12 | 480000 | SW 5TH & E | RAIN 3", BYPASS TO RELIEVE RESIDENTIAL FLOODING
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-03-12 | 3/12 | 180000 | 440 SW 4TH | RAIN 3", BYPASS TO RELIEVE RESIDENTIAL FLOODING
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-03-12 | 3/12 | 480000 | SE PARKWAY & GLEN MILLER CT | RAIN 3", BYPASS TO RELIEVE RESIDENTIAL FLOODING
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-03-12 | 3/12 |  | SHORT CREEK LIFT STATION | RAIN 3", OVER CAPACITY, POSSIBLE FAILURE
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-10 | 11:30P - 7:00A (5/11) | 450000 | SW 5 & E | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-10 | 8:00A - 12:30P | 270000 | SW 5 & E | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-10 | 11:30P - 6:50A (5/11) | 380000 | SOUTH 5TH & E ALLEY | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-10 | 8:00A - 12:30P | 270000 | SOUTH 5TH & E ALLEY | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-11 | 12:30A - 6:30A | 360000 | SW 4TH & E | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-11 | 2:50A - 11:00A | 470000 | SOUTH 11TH & G | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-11 | 7:30A - 12:30P | 300000 | SE PARKWAY & GLEN MILLER | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-11 | 12:10A - 6:20A | 370000 | SE PARKWAY & GLEN MILLER | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-05-11 | 12:30A - 1:05P | 1505000 | 2011 BOSTON PIKE | RAIN 3.4", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-06-13 | 4 - 5 HRS |  | SEVERLEY LEAKING FIRE HYDRANT AT THE WWTP | LOSS OF CHLORINATION & DE-CHLORINATION WHILE PLANT WATER IS DOWN
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-11 | 2:00P - 2:30P | 30000 | SE PARKWAY & GLEN MILLER CT | RAIN 1.5", BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUING PROJECTS TO SEWER SYSTEM & WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-11 | 1:45P - 2:15P | 30000 | SW 5TH & E | RAIN 1.5", BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | STORAGE TANK BEING INSTALLED TO MINIMIZE PUMPING
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-22 | 12:20A - 5:45A | 300000 | SE PARKWAY & GLEN MILLER CT | RAIN 4.6", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-22 | 2:25A - 4:00A | 90000 | 2011 BOSTON PIKE | RAIN 4.6", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-22 | 12:05A - 5:45A | 540000 | SW 5TH & E | RAIN 4.6", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-22 | 12:05A - 5:00A | 380000 | 400 BLOCK SW 4TH | RAIN 4.6", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-27 | 9:00A - 3:30P | 390000 | SE PARKWAY & GLEN MILLER CT | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-27 | 9:10A - 9:50A | 30000 | SW 5TH & E IN ALLEY | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-27 | 9:10A - 12:20P | 180000 | SW 5TH & E | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-28 | 9:00 - 1:30 | 80000 | S 11TH & G | RAIN 2.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-28 | 4:40A - 12:20 | 360000 | SE PARKWAY & GLEN MILLER | RAIN 2.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-28 | 4:15A - 11:00P | 420000 | SW 5TH & E | RAIN 2.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-28 | 4:30A - 8:00A | 420000 | 450 SW 4TH | RAIN 2.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-28 | 4:45A - 10:50A | 360000 | 2011 BOSTON PIKE | RAIN 2.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-28 | 4:15A - 10:00A | 360000 | SW 5TH & E IN ALLEY | RAIN 2.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-07-28 | 7:45 - 11:00 | 240000 | SW G | RAIN 2.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-08-28 | 11:00P - 12:30A (8/29) | 80000 | SW 5TH & E | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-08-28 | 11:05P - 12:30A (8/29) | 70000 | 3200 AVON LANE | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-08-28 | 11:10P - 1:00A (8/29) | 120000 | SE PARKWAY & GLEN MILLER CT | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-08-28 | 10:00P - 1:15A (8/29) | 180000 | EARLHAM FOOTBALL FIELD | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-08-29 | 12:00A - 1:00A | 60000 | SW 5TH & E (ALLEY) | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-08-29 | 12:30A - 1:00A | 60000 | 450 SW 4TH | RAIN 1", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-10-04 | 2:00A - 4:00A | 120000 | SE PARKWAY & GLEN MILLER CT | RAIN 1.5", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH PROJECTS IN SEWER SYSTEM AND AT WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-10-17 | 6:45A - 9:00A | 120000 | SW 5TH & E | RAIN 2", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | STORAGE UNIT INSTALLED, PLANS TO ELIMINATE BYPASS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-10-17 | 7:35A - 1:00P | 300000 | SE PARKWAY & GLEN MILLER CT | RAIN 2", BYPASS PUMPED TO RELIEVE RESIDENTIAL FLOODING | CONTINUE WITH WWTP & SEWER PROJECTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-11-30 | 9:30P - 10:30A (12/1) | 780000 | SE PARKWAY & GLEN MILLER CT | RAIN 3.2" - BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUE PROJECTS IN SEWER SYSTEM & WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-12-01 | 2:00A - 9:00A | 420000 | EARLHAM FOOTBALL FIELD | RAIN 3.2" - BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUE PROJECTS IN SEWER SYSTEM & WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-12-01 | 4:00A - 10:30A | 390000 | SW 5TH & E | RAIN 3.2" - BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUE PROJECTS IN SEWER SYSTEM & WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-12-01 | 4:15A - 7:50A | 215000 | 450 SW 4TH | RAIN 3.2" - BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUE PROJECTS IN SEWER SYSTEM & WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-12-01 | 3:45A - 10:30A | 375000 | 3200 AVON LANE | RAIN 3.2" - BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUE PROJECTS IN SEWER SYSTEM & WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-12-01 | 2:00A - 7:50A | 350000 | SW 5TH & E ALLEY | RAIN 3.2" - BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUE PROJECTS IN SEWER SYSTEM & WWTP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2006-12-01 | 2:00A - 12:40P | 640000 | 2011 BOSTON PIKE | RAIN 3.2" - BYPASS PUMPING TO RELIEVE RESIDENTIAL FLOODING | CONTINUE PROJECTS IN SEWER SYSTEM & WWTP
IN0054402 | WESTERN WAYNE RSD | WAYNE | 2006-08-29 | 8/29 - 8/30 | 1000000 | PLANT BYPASS | RAIN 4.75", FLASH FLOODING | PARTIALLY CLOSED INFLUENT GATE TO PREVENT PLANT FLOODING
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-03-04 | 9:00P - 7:00A (3/5) |  | BIOSOLIDS IN RECEIVING STREAM | EQUIPMENT FAILURE, VACTOR TRUCK TO REMOVE SLUDGE
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-05-15 | 06:30 - 19:00 | 8250 | OLD CSO 007 - 411 HICKORY LA | RAIN 2" | SEWER PLANT EXPANSION, LOOKING FOR STORM WATER I&I
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-06-10 | 9:30A - 5:00P | 1500 | SSO 007 | SUSPECT RAIN EVENT CAUSED SSO | PLANT EXPANSION & SSO ELIMIATION
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-06-22 | 3:00P - 5:00P | 500 | SSO # 007 | RAIN 1" | PLANT EXPANSION WITH EQ BASIN
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-07-11 | 3:45P - 9:00P | 12000 | SSO # 007 | RAIN 1.5" | PLANT EXPANSION WITH EQ BASIN - TO BLOCK OFF SSO'S
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-07-12 | 7:00P - 10:45P | 6000 | SSO # 007 | RAIN 1", RAW SEWAGE PUMP TRIPPING OUT DURING HIGH FLOW | PLANT EXPANSION WITH EQ BASIN
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-10-17 | 05:00 - 09:00 | 40000 | SSO # 007 | RAIN 2" | NEW PLANT UNDERWAY WITH EQ BASIN
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2006-12-31 | 12/31 | 300000 | EQ TANKS FULL, OUTFALL 001 | RAIN 2.5" | WORKING ON I & I REDUCTION
IN0020974 | BROOKSTON MUNICIPAL STP | WHITE | 2006-03-12 | 3/12 - 3/13 | 500000 | MANHOLE # 1 AT PLANT | RAIN 2.5" | PLANT UNDER EXPANSION
IN0030571 | CHALMERS MUNICIPAL STP | WHITE | 2006-04-17 | 4/17 | 1000 | MANHOLE # 18 | RAIN 3.25" | LOOKING FOR INFLOW SOURCES
IN0021580 | MONON MUNICIPAL STP | WHITE | 2006-10-23 | 10/23 | 500 | MANHOLE ON WEST SIDE OF CLARIFIER | RETURN LINE PLUGGED | LINE FLUSHED WITH VACUUM TRUCK
IN0020176 | MONTICELLO MUNICIPAL STP | WHITE | 2006-02-04 | 12:30 - 13:20 | 500 | MANHOLE N SIDE OF CARTER DITCH / MAIN ST | SEWER LINE PLUG, JETTED WITH VACTOR | CONTINUED LINE MAINTENANCE
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2006-11-02 | 4:30P - 5:15P |  | 2" LOW PRESSURE SEWER | TELEPHONE CONTRACTOR BORED INTO 2" SEWER | CONTRACTOR NEEDS TO WAIT FOR LOCATES
IN0021113 | CHURUBUSCO MUNICIPAL STP | WHITLEY | 2006-01-30 | 6:00A - 7:15A | 21000 | CLARIFIER WASHOUT | RAIN 0.9", EQUIPMENT FAILURE (# 1 RAS PUMP PLUGGING UP) | FLUSHED BOTH RAS PUMPS
IN0021113 | CHURUBUSCO MUNICIPAL STP | WHITLEY | 2006-03-14 | 7:00A - 2:00P | 31500 | OUTFALL 002 | RAIN 3.2" | I&I & PLANT UPGRADE SCHEDULED THIS YEAR
IN0021113 | CHURUBUSCO MUNICIPAL STP | WHITLEY | 2006-08-22 | 6:30P - 9:00P | 10000 | RAW WET WELL FORCE MAIN | FORCE MAIN COLLAPSED DURING CONSTRUCTION | REINFORCED FORCE MAIN
IN0022624 | COLUMBIA CITY MUNICIPAL STP | WHITLEY | 2006-05-11 | 10:00A - 10:30A | 1000 | DIGESTER (OVER THE TOP) | WASTING VALVE WAS LEFT CRACKED (POSSIBLE DEBRIS) | HAULERS WERE CALLED TO LOWER LEVEL
IN0022624 | COLUMBIA CITY MUNICIPAL STP | WHITLEY | 2006-11-13 | 9:00A - 3:00P | 72000 | #012 | EMPLOYEE NEGLEGENCE / FAILURE TO CLEAN BAR SCREEN | EMPLOYEE TERMINATED
IN0022624 | COLUMBIA CITY MUNICIPAL STP | WHITLEY | 2006-12-26 | 10:00P - 7:00A (12/27) |  | OUTFALL # 012 | PUMPS PLUGGED WITH DEBRIS | TELEMETRY NOTIFIED RIGHT AWAY