## 2010 annual summary
PERMIT # | FACILITY NAME | COUNTY | BYPDATE | DURATION | GALLONS | LOCATION | RECEIVING AREA | REASON | ACTIONS
IN0000094 | ARCELOR MITTAL IND HARBOR E |  | 2010-05-11 |  |  | PLANT 4 12" MILL COOLING TOWER |  | UNKNOWN STILL INVESTIGATING
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2010-03-13 | 5:00P - 9:00P | 1200 | LIFT STATION AND PARR ROAD | GROUND | RAIN 1.42" | LTCP
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2010-03-13 | 5:00P - 9:00P | 1200 | LS AT PARR ROAD AND 000 CR | GROUND | RAIN 1.42" | LTCP
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2010-06-11 | 9A - 10:30A | 200 | PARR ROAD AND CR 000 MANHOLE | GROUND | RAIN RECEIVED 1.10" IN SHORT TIME | LTCP HAS BEEN APPROVED
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2010-06-19 | 4:00P - 4:00P (6/20) | 2880000 | POND 2 | HABEGGER DITCH | RAIN | LTCP
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2010-06-21 | 7:00A - 7:00A (6/23) | 4320000 | POND 2 | HEBEGGER DITCH | RAIN; PONDS ARE FULL
IN0039357 | GENEVA MUNICIPAL STP | ADAMS | 2010-02-01 | 12:06A - 12:20A | 500 | FORD ST AND 116 | NONE | RAIN | CLEANED FROZEN BUILD UP AROUND GATE
IN0039357 | GENEVA MUNICIPAL STP | ADAMS | 2010-05-27 | 9:20P |  | FORD ST AND 116 |  | RAIN
| ALLEN CNTY REGNAL SWR DIS. | ALLEN | 2010-10-17 | ? - 5:45P | 3000 | LS AT BRUICK RD | HOAK DITCH | PUMP #1 BLEW FUSE WHICH STOPPED ALARM FROM OPERATING | FUSE REPLACED. PUMP #2 PUMP DOWN LS. DITCH CLEANED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-01-08 | 2:30P - 5:55P | 1025 | S14 017 4737 HEATHERWIND DR | STORM SEWER TO ST. MARYS RIVER | PLUG CAUSED BY GREASE | WILL INVESTIGATE UPSTREAM AND DOWNSTREAM CONTINUE TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-01-11 | 12P - 1:30P | 450 | S14 017 4737 HEATHERWIND DRIVE | STORM SEWER TO ST MARYS RIVER | PLUG CAUSED BY GREASE | INVESTIGATE FURTHER UP AND DOWN STREAM TO ENSURE OTHER SEGMENTS NOT AFFECTED BY GREASE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-02-04 | 4:15P - 6:15P | 220 | R23 034 6108 BUNT DRIVE | GROUND | BLOCKAGE IN SEPARATE SANITARY SEWER LINE | LINE WAS FLUSHED AND BLOCKAGE REMOVED CITY CONTINUES TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-02-05 | 1P - 9A (2/8) | 68 | L23 009 | ST MARY RIVER | SMALL CRACK IN SIPHON STRUCTURE | SIPHON STRUCTURE WAS REPAIRED AND LINES FLUSHED CITY CONTINUES TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-02-22 | 6:45P - 8:15P | 450 | J46 097 | SPY RUN CREEK | SEPARATE SANITARY SEWER LINE WAS OBSTRUCTED | LINE WAS FLUSHED AND WILL TELEVISE AND DO FURTHER INVESTIGATION CONTINUE WITH CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-03-01 | 7:00A - 8:45A | 100 | 7914 CHINCHILLA P31 018 | GROUND | LINE PLUGGED WITH GREASE | BLOCKAGE REMOVED AND LINE FLUSHED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-03-09 | 2:45P - 3P | 50 | 7603 VERONA DRIVE R31 020 | TRIER DITCH | BLOCKAGE IN SEPARATE SANITARY SEWER AND .07 RAIN | BLOCKAGE REMOVED AND LINE FLUSHED CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-03-10 | 6P - 10:15P | 255 | 5236 HEWITT LANE T26 046 | BULLERMAN DRAIN | BLOCKAGE IN SEPARATE SANITARY SEWER AND .07 RAIN | BLOCKAGE REMOVED AND LINE FLUSHED CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-03-13 | 8:00P - 10:00P | 21600 | Q23 003, 004, 005 | ST. MARY RIVER | RAIN .63" GREASE BLOCKAGE IN LINE | LINE FLUSHED TO REMEDIATE OVERFLOW, IMPLEMENTING CMOM AND CSSOP PLANS
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-03-28 | 12:00P - 6:00P | 135000 | N23 125 | ST. MARYS RIVER | RAIN .96" OVERFLOW FROM SIPHON LINE IN SSO | IMPLEMENTING CMOM AND SSSOP PROGRAMS
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-04-08 | 7:00P (4/7) - 10:03A |  | V06 001 | MAUMEE RIVER | RAIN 2.87"
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-04-18 | 8P - 9:30A (4/20) | 230000 | P22 001 CSO | ST MARY RIVER | FLOATABLES CONTROL STRUCTURE MALFUNCTION TELEMETRY WAS NOT READING AND SUMP PUMP WAS THEREFORE NOT OPERATING | POWER ISSUE HAS BEEN CORRECTED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-04-21 | 11:00A - 12:30P | 250 | I02 I20 2439 WEST JEFFERSON | JUNK DITCH | GREASE | FLUSHED LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-04-25 | 6:44P - 10:25A |  | V06 001 | MAUMEE RIVER | RAIN 1.84" | WORKING TO ELIMINATE SSO'S
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-10 | 8:45A - 10:43A | 2950 | T34 028 | KRUNCKENBERG DITCH | RAIN 1.06
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-10 | 10:15P - 10:30A(5/11) | 32600 | OUTFALL #002 | MAUMEE RIVER | UNINTENDED OPENING OF SLUICE GATE | INVESTIGATION OF HOW IT OPENED IS ONGOING CITY CONTINUES TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-11 | 9:27A - 12:00P | 10050 | N23 120 & N23 125 | ST. MARY'S RIVER | RAIN 1.06" | CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-14 | 3P - 2P (5/15) | 50000 | L.S. G15 010 | GROUND TO JUNK DITCH | BROKEN 8" SANITARY SEWER FORCE MAIN | PUMP STATION SHUT OFF PUMPED OUT AND LINE REPAIRED AND SITE REMEDIATED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-21 | 10:48P - 5:40A (5/22) | 329600 | W30 047 PINE VALLEY | DELEGRANGE DITCH | RAIN 2.51" | CMOM AND CSSOP PROGRAMS
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-21 | 8:00P - 9:10P | 1050 | H27 036 | FAIRFIELD DITCH | RAIN 2.51" | CMOM AND CSSOP PROGRAMS
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-21 | 11:02A - 10:49A (5/24) | 100000 | NEBRASKA PUMP STATION OUTFALL 012 & 011 | ST. MARYS RIVER | RAIN 2.51"
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-22 | 1:00A - 4:05A | 925 | S30 023 | GROUND | RAIN 2.51" | CMOM AND CSSOP PROGRAMS
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-05-30 | 6:30P - 9:30P | 69600 | MANHOLE P66 037 | DELEGRANGE DITCH | HEAVY RAIN 1.38" IN 6 HOURS, TO ALLEVIATE BACKUPS PUMPED INTO DITCH | PUMPING WAS INTERMITTENT RELIEF SEWER IS UNDER DESIGN CITY CONTINUES TO IMPLEMENT ITS CMOM CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-06-10 |  | 30 | W18 016 | GROUND | GREASE IN SEWER LINE | LINE WAS FLUSHED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-07-12 | 11:45P - 2A (7/13) | 135 | T26 047 HEWITT | STORM SEWER | LINE BLOCKED WITH ROOTS | CITY FLUSHED LINE AND WILL FURTHER INVESTIGATE CONTINUES CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-07-21 | 4:47P - 7:30P | 163 | 1716 CINNAMON ROAD MH O42 046 | ST JOSEPH RIVER | BLOCKAGE OF ROOTS AND GREASE | LINE ROOT SAWED AND FLUSHED AND CLEANED UP CITY CONTINUES TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-07-26 | 10:18A - 2P | 555 | CC87019 CC87029 | UNKNOWN DITCH TO WABASH RIVER | BLOCKAGE THESE MH ARE PART OF THE RECENTLY ACQUIRED ZANESVILLE AREA | LINE WAS FLUSHED AND OVERFLOW CLEANED UP, CITY CONTINUES TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-08-02 | 11A - 1P | 150 | CC75004 L.S. | GROUND | MOTOR STARTER TRIPPED B/C THERMAL OVERLOAD | REPLACED HIGH TEMPERATURE SWITCH AND CLEANED UP OVERFLOW
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-08-07 | 4:25P - 4:26P | 30415 | THIRD STREET PUMP STATION M10 353 | ST MARYS RIVER | RAIN COUPLED WITH RIVER INFILTRATION RIVER WATER ENTERING UNDER SLUICE GATE | REWIRED FLOAT AT DEWATERING PUMP TURN ON AUTOMATICALLY INTO SANITARY SEWER
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-08-12 | 8:58P - 9:45P | 20 | 3835 OAKHURST U26 023 | GROUND | SMALL BLOCKED IN SEPARATE SANITARY SEWER LINE | LINE WAS FLUSHED OVERFLOW CLEANED UP AND WILL BE TV'D
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-08-14 | 2P - 6P | 6000 | 5810 ARAPAHO TRAIL U58 135 | NEIGHBORHOOD DENTION POND ST JOSEPH RIVER | 8-INCH SEPARATE SANITARY LINE PLUGGED WITH GREASE | LINE WAS FLUSHED OVERFLOW CLEANED UP AND WILL BE TV'D
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-10-08 | 7:15A - 8:15A | 500 | D43 006 (COVERDALE LS) 9661 COVERDALE RD. | GROUND | LOW VOLTAGE AT LS CAUSED PUMP TO TRIP | RESTORED VOLTAGE AND AREA CLEANED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-11-09 | 8:00A - 10:00A (11/17) | 20800 | PARKERDALE PUMP STATION | GROUND | VALVE FOR 6" STAND PIPE WAS NEVER CLOSED AFTER INSTALLATION | OVERFLOW CLEANED UP. CHECKING OTHER PUMP STATIONS.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-11-10 | 4:30A - 6:00A | 50000 | O19 009 SMITH & BELMONT | NATURAL DRAIN #4 | WATER MAIN BREAK ENTERED CSO | WATER MAIN REPAIRED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-11-12 | 2A - 11:15A | 100000 | SMITH & BELMONT O19 009 | NATURAL DRAIN #4 | WATERMAIN BREAK ENTER THE COMBINED SEWER SYSTEM | WATER WAS REPAIRED CITY CONTINUES TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-11-22 | 7:00P - 8:30P | 20 | V18 109 & V18 016 2228 FORESTVIEW DR | GROUND | GREASE IN LINE | LINE FLUSHED AND OVERFLOW CLEANED UP. WILL TV
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-11-30 | 5:20P -7:20P | 600 | K62 035 1604 WILLISTEAD PL | TILDEN DITCH | PRECIPITATION .31" AND ROOT BLOCKAGE | LINE FLUSHED OVERFLOW CLEANED UP CITY CONTINUES TO IMPLEMENT CMOM CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-12-02 | 10:48P - 2:45A (12/3) | 390000 | J03-268 BROWN ST LIFT STATION | ST. MARYS RIVER | 12 INCH WATER MAIN BREAK | WATER MAIN BREAK REPAIRED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-12-11 | 12:45P - 1:45P | 60 | T26 043 4040 STANTON | BULLERMAN DRAIN | GREASE BLOCKAGE IN SANITARY SEWER | LINE FLUSHED OVERFLOW CLEANED UP AND CONTINUE CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-12-14 | 11:28A - 1P | 10 | J19 019 2021 WOODHAVEN ROAD | GROUND | PLUG CAUSED BY GREASE | CONTINUE TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-12-14 | 3:53P - 6P | 127 | R23 026 6022 BUNT DRIVE | STORM SEWER TO TRIER DITCH | PLUG CAUSED BY GREASE | CONTINUE TO IMPLEMENT CMOM AND CSSOP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2010-12-17 | 7:46A - 9:24A (12/20) | 100000 | L19 018 OUTFALL #021 | ST. MARY'S RIVER @ OUTFALL K19 044 | FAULTY FLOAT CAUSED GATE TO STAY IN OPEN POSITION | GATE CLOSED AND FLOAT REPLACED
| GRABILL COLLECTION SYSTEM | ALLEN | 2010-05-21 | 11:30P - 5:30P | 1000 | MANHOLE 2-4 | WITMEN DITCH | RAIN 2" | PUMPS AT FULL DISCHARGE
| LEO-CEDARVILLE RSD | ALLEN | 2010-03-30 | 9:00A - 2:30P |  | SR 1 120' SOUTH OF EAGLE RIVER RUN | GROUND | LATERAL CRACK AT BELL IN PVC FORCE MAIN | SHUT DOWN UPSTREAM FACILITIES AND REPAIRED
IN0035378 | UTILITY CENTER MAIN ABOITE | ALLEN | 2010-05-21 | 10:30P - 2:00A (5/22) | 2000 | MH D31-5 ABOITE MEADOWS | GROUND | RAIN 2.1"
IN0035378 | UTILITY CENTER MAIN ABOITE | ALLEN | 2010-05-21 | 11:30P - 1:00A (5/22) | 1000 | MH D31-120 | GROUND | RAIN 2.1"
IN0035378 | UTILITY CENTER MAIN ABOITE | ALLEN | 2010-05-21 | 9:20P - 1:15A (5/23) | 20000 | SYCAMORE HILLS LS | GROUND | RAIN 2.24" | CHECKING UPSTREAM MANHOLES
IN0035378 | UTILITY CENTER MAIN ABOITE | ALLEN | 2010-05-22 |  | 2000 | C35-12 | GROUND AND CREEK | RAIN 2.24" | TELEVISING LINES UPSTREAM
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2010-01-14 | 6:45A - 7:30A | 5000 | CHESTNUT WTP L.S. | GROUND | BREAKER TRIPPED AIR COMPRESSOR LOST AIR FOR VALVE CONTROL FILTERS
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2010-04-08 | 11:45A - 2:30P | 1500 | SYCAMORE HILLS LS | GROUND | RAIN 1.7" | INSTALLING UP TO DATE CONTROL PANEL AND REPAIRING PUMPS
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2010-04-08 | 11:45A - ONGOING |  | SYCAMORE L.S. | GROUND | HEAVY RAIN 1.7 INCHES | CONTRACTING TO REHAB STATION WITH LARGER PUMPS AND CONTROL PANEL
IN0035378 | UTILITY CENTER, MAIN ABOIT | ALLEN | 2010-04-26 | 12:00P - 2:45P | 1500 | SYCAMORE LS | BEAL TAYLOR CREEK AND GROUND | RAIN 1.7" | AREA CLEANED IMMEDIATELY
IN0042391 | UTILITY CENTER, MIDWEST | ALLEN | 2010-12-27 | 1:55P - 2:30P | 100 | F32 - 23 MH | GROUND | GREASE PLUGGING LINE | JETTED LINE CLEANED GROUND AND T.V.ING TO DETERMINE DAMAGE
IN0035378 | UTILITY CENTER/AQUA INDIANA | ALLEN | 2010-05-11 | 3:25A - 11:15P | 8000 | SYCAMORE HILL LS | GROUND | RAIN 1.3" | WORKING ON PUMPS AND CHECKING MANHOLES
IN0021407 | WOODBURN MUNICIPAL STP | ALLEN | 2010-08-20 | 11A - | 1050 | FORCE MAIN NEAR HAVENWOOD LS | TRENCH | CREW BORING FIBER OPTIC HIT FORCE MAIN | CREW ON MONDAY WILL BORE NE LINE UNDER DITCH
IN0032573 | COLUMBUS MUNICIPAL STP | BARTHOLOMEW | 2010-04-18 | 12A - 1P | 31000 | WWTP DIGESTER | GROUND | OPERATOR ERROR IN ALLOWING DIGESTER TO OVERFLOW | REMOVED ALL SLUDGE FROM ROADWAY AND VACANT LOT WILL COVER REMAINING SLUDGE WITH SOIL
IN0032573 | COLUMBUS MUNICIPAL STP | BARTHOLOMEW | 2010-09-13 |  |  | LIFT STATION #1 | CLIFTY CREEK | 6" FORCE MAIN LEAKING UNDER CLIFTY CREEK. DISCHARGE IS FROM SEPTIC TANKS IN JEWELL VILLAGE | REPLACE OLD LINE RUNNING UNDER CREEK
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2010-05-12 | 10:40A | 5000 | LS L10 | GROUND | RAIN 2" | APPLICATION FOR GRANT TO BUILD EQ BASIN
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2010-06-12 | ? - 13:40 | 40000 | WET WELL | GROUND & STREAM | PRECIPITATION 2.22" | EQ BASIN BEING BUILT AS SOON AS WE GET BUILDING PERMIT ALREADY FUNDED
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2010-11-30 | ? - 1P | 2000 | LIFT STATION | GROUND | PRECIPITATION 4" IN TWO DAYS | HAS GRANT AND EQUALIZATION BASIN IN PRE-PHASE
IN0021253 | HOPE UTILITIES WWTP | BARTHOLOMEW | 2010-06-19 | 6:45A - 9:15A | 6960 | MH'S 3, 4, AND 35 | HAWCREEK | RAIN 1.3" | CLEANED UP SOLIDS
IN0021253 | HOPE WWTP | BARTHOLOMEW | 2010-05-12 | 10:30A - 1:00P | 7920 | MH'S 3A, 4 AND 35 | HAW CREEK | RAIN 1.4" | CLEANED UP SOLIDS
IN0050253 | FOWLER MUNICIPAL STP | BENTON | 2010-06-22 | 7A - 2P |  | ALL PUMP STATIONS HAD 1 OR 2 MH | GROUND FARM FIELD | 5" RAIN IN 8 HOURS LIGHTENING DAMAGE LEVEL ONE EMERGENCY DECLARED BY COUNTY | STORING EXTRA FLOW IN SURGE BASINS MASTER PLAN IS COMPLETE 1M GRANT TO INSTALL NEW SEWERS AND MAKE REPAIRS AT WWTP
IN0023990 | OTTERBEIN MUNICIPAL STP | BENTON | 2010-06-22 | AM - AM (6/23) |  | SOUTH INDIANA STREET MANHOLE | GROUND TO STORM CRAIN | 6" PRECIPITATION
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2010-01-28 | 11:15A - 11:20A | 100 | MANHOLE SC-4 96TH AND MONO TRAIL | GROUND | CONSTRUCTION PLUG WAS IN PLACE TO REROUTE SANITARY SEWER AND PLUG WAS NOT REMOVED QUICK ENOUGH CTRWD INSPECTOR DIRECTED CONTRACTOR TO REMOVE PLUG | SHORTER TIMES FOR SEWER PLUGS AND BYPASS PUMPING CAPABILITIES
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2010-06-14 | 10A - 1P | 2000 | MH SV-204 | GROUND | GREASE IN LINE FROM STONE CREEK DINER | LINES JETTED AND MANHOLES PRETREATMENT SPECIALIST WILL CONTACT OWNER
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2010-07-12 | 09:00 - 12:30 | 250 | ORBAL'S WEST GEAR BOX SUMP PIT | GROUND | PLUG CAME LOOSE PARTIALLY TREATED WATER | NEW PLUGS HAVE BEEN PURCHASED AND NEW METHOD OF REMOVING WATER PIPING THE OVERFLOW TO AN EXISTING MH
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2010-06-16 |  | 1552000 | PLANT | FINAL PLANT EFFLUENT | RAIN, SEWER LINES INFILTRATION
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2010-06-19 |  | 1089000 | PLANT | FINAL PLANT EFFLUENT | RAIN 1.52" ON TOP OF SATURATED SOILS | RELINING SEWERS
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2010-06-20 |  | 1089000 | PLANT | FINAL PLANT EFFLUENT | RAIN, SEWER LINES INFILTRATION
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2010-06-22 |  | 1974000 | PLANT | FINAL PLANT EFFLUENT | 1.6" RAIN ON ALREADY SATURATED GROUNDS | SPENDING $200,000 A YEAR TO RELINE SEWER LINES
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2010-06-23 |  | 13000 | PLANT | EFFLUENT | RAIN, I & I
IN0020796 | WHITESTOWN MUNICIPAL STP | BOONE | 2010-06-22 | 8:30A - 1:30P | 6500 | 601 EAST PIERCE MH | JACKSON RUN CREEK | PRECIPITATION 1.6" IN SHORT TIME | STAFF MONITORED OVERFLOW ALL EQUIPMENT AT PLANT WAS RUNNING AT CAPACITY SRF & OCRA GRANTS FOR SUMMER/FALL 2010 PROJECTS
| WHITESTOWN MUNICIPAL STP | BOONE | 2010-11-08 | ? - 9:30A | 4000 | ST. RD. & WEST STONEGATE DR. MH | GROUND | PLUG CAUSED BLOCKAGE | PLUG REMOVED, AREA CLEANED
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2010-04-08 | 7:00A - 4:00P | 216000 | OUTFALL 101 (EQUALIZATION) | OUTFALL 001 SALT CREEK | RAIN 2.5" RAIN OCCURRED WHILE WEST CLARIFIER WAS BEING REPAIRED | SET EQUALIZATION PLATES TO ALLOW HIGHEST REASONABLE FLOW TO BE SENT TO EAST CLARIFIER
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2010-09-12 | 7:55P - 8:30A (9/13) |  | MANHOLE #2 | STORM DITCH | FAULTY CONTACT ON #1 | AREA TREATED WITH LIME
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-05-23 | 7:00A - 7:00A (5/25) | 1500000 | EQ TANK EMERGENCY RELEASE POINT | 2-2DAY TERTIARY PONDS | RAIN 1.6" | COMPILING DATE FOR FUTURE REHAB PROJECT
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-09 | 8:00A - 7:00A (6/10) |  | EQ TANK EMERGENCY RELEASE POINT | 2-2 DAY TERTIARY PONDS | RAIN 1.25" | ADDITIONAL FLOW BLENDED WITH FINAL EFFLUENT AND RECEIVED CHLORINATION TREATMENT
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-10 | 7:00A - 7:00A (6/11) | 738000 | EQ TANK EMERGENCY RELEASE POINT | 2-2 DAY TERTIARY PONDS | RAIN .54" | ADDITIONAL FLOW BLENDED WITH FINAL EFFLUENT AND RECEIVED CHLORINATION TREATMENT
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-11 | 7A - 7A (6/12) | 537000 | EQ TANK EMERGENCY RELEASE POINT | 2-2 DAY TERTIARY PONDS | HEAVY RAINS 1.79" + .15" ALREADY FULL BASINS | WORKING ON COLLECTION SYSTEM T-BIRD DESIGNS WORKING ON SOLUTIONS
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-12 | 7A - 7A (6/13) | 306000 | EQ TANK EMERGENCY RELEASE POINT | 2-2 DAY TERTIARY PONDS | HEAVY RAINS 1.94" + .42" ALREADY FULL BASINS | WORKING ON COLLECTION SYSTEM T-BIRD DESIGNS WORKING ON SOLUTIONS
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-13 | 7A - 7A (6/14) | 237000 | EQ TANK EMERGENCY RELEASE POINT | 2-2 DAY TERTIARY PONDS | HEAVY RAINS 2.36" + .15" ALREADY FULL BASINS | WORKING ON COLLECTION SYSTEM T-BIRD DESIGNS WORKING ON SOLUTIONS
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-14 | 7A - 7A (6/15) | 762000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | HEAVY RAINS 1.4" ON ADDITIONAL 2.51" | ON GOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-15 | 7A - 7A (6/16) | 1800000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | HEAVY RAINS .18" ON ADDITIONAL 3.91" | ON GOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-16 | 7A - 7A (6/17) | 1320000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | PLANT CATCHING UP AFTER 4.09" | ON GOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-17 | 7A - 7A (6/18) | 468000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | PLANT CATCHING UP AFTER 4.09" | ON GOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-18 | 7:00A - 7:00A (6/19) | 360000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | RAIN 1.85" | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-19 | 7:00A - 7:00A (6/20) | 1584000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | RAIN | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-20 | 7:00A - 7:00A (6/21) | 768000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | RAIN .17" | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-21 | 7:00A - 7:00A (6/22) | 1380000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | RAIN 3.35" | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-22 | 7:00A - 7:00A (6/23) | 1800000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | TOTAL 9.46" RAIN | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-23 | 7:00A - 7:00A (6/24) | 1320000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | TOTAL 9.46" RAIN | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-24 | 7:00A - 7:00A (6/25) | 1032000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | RAIN
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-25 | 7:00A - 7:00A (6/26) | 792000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | PRECIPITATION | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-26 | 7:00A - 7:00A (6/27) | 198000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | PRECIPITATION PLANT AND COLLECTIONS SYSTEM CATCHING UP | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-27 | 7:00A - 7:00A (6/28) | 102000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | PRECIPITATION PLANT AND COLLECTIONS SYSTEM CATCHING UP | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2010-06-28 | 7:00A - 6:00A (6/29) | 138000 | EQ TANK EMERGENCY RELEASE POINT | 2 - 2 DAY TERTIARY PONDS | PRECIPITATION PLANT AND COLLECTIONS SYSTEM CATCHING UP | ONGOING IN HOUSE COLLECTION SYSTEM MAINTENANCE
IN0054445 | WHITE OAKS ON THE LAKE | CARROLL | 2010-09-07 | 7P - 7:30P | 300 | UPPER PARK LS | DRAINAGE DITCH DRY TO LAKE FREEMAN | SMALL LEAK IN LS | LS PUMPED DOWN AND KEEP PUMPED DOWN CONTRACTOR SEALING LEAK AND DURING OFF SEASON WILL LOOK INTO PERMANENT FIX
IN0023604 | LOGANSPORT MUNICIPAL STP | CASS | 2010-06-21 | 11:00A - 10:30P | 471000 | SCHULTZ AND KLOENNE STREETS | GOOSE CREEK | RAIN 1.87" | MINIMIZED UNCONTROLLED LEAKAGE, MAINTAIN MAX FLOW
IN0023604 | LOGANSPORT MUNICIPAL STP | CASS | 2010-06-22 | 8:30A - 2:30P | 180000 | INTERSECTION OF SCHULTZ AND KLOENNE ST. | GOOSE CREEK | RAIN .32"
IN0020354 | WALTON MUNICIPAL STP | CASS | 2010-03-13 | 12:15A - 6:18A | 27000 | LIFT STATION | PHILLIPS DITCH | RAIN 1.83"
IN0020354 | WALTON MUNICIPAL STP | CASS | 2010-06-14 | 7:12P - 11:33P | 14000 | LIFT STATION | PHILLIPS DITCH | RAIN 1.3" IN SHORT PERIOD OF TIME | PLANT WAS RUNNING AT DESIRED CAPACITY
IN0020354 | WALTON WWTP | CASS | 2010-06-19 | 2:48A - 1:44P | 109000 | LIFT STATION | PHILLIPS DITCH | RAIN 1.9"
IN0020354 | WALTON WWTP | CASS | 2010-06-21 | 10:51A - 9:42P | 123000 | LIFT STATION | PHILLIPS DITCH | RAIN 1.61"
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-01-24 |  | 3500 | MANHOLE 3-82A | PLEASANT RUN CREEK | RAIN .8 PLUS ADDITIONAL RAIN DAYS LEADING UP TO | CLEAN UP MESS AND WORKING ON SYSTEM POINT REPAIRS
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-01-25 |  | 50 | VALLEY DRIVE FORCE MAIN | GROUND | SPLIT IN PIPE | REPAIRED PIPE WITH CLAMP AND CLEANED UP MESS
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-04-08 | ? - ONGOING |  | MANHOLE 3-82A | PLEASANT RUN CREEK | RAIN 1.1 AND ONE PUMP DOWN FOR REPAIRS | WILL CLEAN UP MESS AND WORKING ON I/I ISSUES
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-04-12 | 1:00A - 1:30A | 200 | MH 3-310 | DITCH | GREASE IN LINE | FLUSHED LINE AND REMOVED GREASE, WILL TV
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-04-15 | ? - 1P | 500 | HUNT STATION FORCE MAIN | DITCH | SMALL HOLE IN FORCE MAIN | CLAMPED PIPE CLEANED UP MESS WITH VAC TRUCK
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-05-01 | ? - (5/3) |  | MANHOLE 3-82a | PLEASANT RUN CREEK | PRECIPITATION 3.5" IN PAST 3 DAYS | ALL PUMPS AND CONTROLS IN OPERATION WORKING ON POINT REPAIRS
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-05-01 | ? - 11:00 | 5000 | MANHOLE 3-55 AND 3-82a | PLEASANT RUN CREEK | 1.1" RAIN | WILL CLEAN UP WILL STOPPED AND WORKING ON POINT REPAIRS IN SYSTEM
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-05-02 | ? |  | MANHOLE 3-151 | PLEASANT RUN CREEK | ADDITIONAL RAIN TOTALLY 3.2" | WILL CLEAN UP WILL STOPPED AND WORKING ON POINT REPAIRS IN SYSTEM
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-05-05 | 5/10/10 | 250000 | 10" LINE IN GLENDALE SUBDIVISION | PLEASANT RUN CREEK | BROKEN 10" GRAVITY SEWER PIPE | CLEANED AREA AND REPAIRED LINE
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-06-09 | 8:00A - 9:00A | 2500 | MANHOLE 3-82A | PLEASANT RUN CREEK | RAIN 1.3" | OPENED RELIEF VALVE AND OVERFLOW STOPPED
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-06-19 |  | 5000 | MH 3-82A | PLEASANT RUN CREEK | RAIN 1.6" | ALL PUMPS AND CONTROLS IN OPERATION
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-11-25 | 10:00P - 4:00A | 50000 | MH 3-82A | PLEASANT RUN CREEK | RAIN 4" | CLEANED AREA AND LIMED
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-11-26 | 12:00 - 14:00 | 100 | CLEANOUT 336 HIGHLAND | YARD | MAIN STOPPED UP WITH GREASE | LINE FLUSHED AND CLEANED WITH VAC TRUCK CLEANED UP MESS COVERED WITH LIME AND STRAW
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2010-12-21 | ? - 11:30P | 300 | MH 1-13 | STORM DRAIN | SHOP RAGS IN LINE | CLEANED LINE WITH VACTOR AND FLUSHED STORM DRAIN
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2010-05-02 | 6A - 1:30P | 3000 | 321 NEWMAN AVENUE | STREAM | PRECIPITATION 5" POWER FAILURE HAD TO WAIT ON DUKE | SET UP PUMP TO MINIMIZE BYPASS UNTIL POWER WAS RESTORED DOING STUDY TO REPLACE STATION
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2010-05-02 | 8:30A - 12:30 A | 2000 | 747 WEST HARRISON AVENUE | STORM SEWER AND STREAM | PRECIPITATION 5" SUMP PUMP FAILED AND FLOODED DRYWELL INCLUDING MOTORS AND CONTROLS | REPAIRED SUMP PUMP AND STUDY TO REPLACE THIS STATION
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2010-05-02 | 9A - 9P | 5000 | NORTH CLARK BLVD & WASHINGTON AND MCKINLEY & CARTER | STORM SEWER | PRECIPITATION 5" | STUDY POSSIBLE UPGRADES TO OUR PLANT TO HANDLE HEAVY RAINS
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2010-08-14 | 7:45P - 8:30P | 2000 | N. CLARK AND PRIMARY CLARIFIERS | STORM SEWER | RAIN 1"
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2010-12-03 | 9:00A - 9:30A | 15 | ELOISE & CLARK PKWY | GROUND | GREASE IN MAIN LINE | CLEANED LINE AND VACTORED MANHOLES
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2010-05-02 | 13:35 - ? |  | MANHOLE RAILROAD STREET | DITCH TO MILLER FORK CREEK | HEAVY RAIN SHORT TIME 4.24"
IN0035521 | HENRYVILLE MEMBERSHIP SAN CORP | CLARK | 2010-05-21 | 8:25P - 9:25P |  | MH IN RAILROAD ST | GROUND TO ROAD DITCH TO MILLER FORK CREEK | RAIN 1"
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-01-21 | 8:07P - 8:52P | 27720 | CRUMS LANE LIFT STATION | STORM SEWER | RAIN .85" HIGH LEVEL IN WET WELL PUMPED INTO STORM DRAIN TO PREVENT PROPERTY DAMAGE | EVALUATING ALTERNATIVES TO INCREASE MAIN LINE SIZE OR BUILD NEW LIFT STATION
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-01-22 | 3:00A - 3:40A | 10150 | SPRING STREET LIFT STATION | MILL CREEK | PUMP 3 KICKED OUT | OPERATORS FIXED PROBLEM
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-02-19 | 8A - 9:15A | 75 | MANHOLE PERIMETER DRIVE | GROUND | PUMPS AND ALARMS TURNED OFF FOR WET WELL CLEANING AND OPERATORS FAILED TO RETURN TO ON AFTER COMPLETING CLEANING | LIME USED TO CLEAN AREA VACTORING WITH COMBO TRUCK, OPERATORS WRITTEN UP FOR CARELESSNESS
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-03-06 | 10A - 12P | 500 | SCOTT ROAD MANHOLE | GROUND CREEK | LEFT BRICKS IN MANHOLE CAUSED A RESTRICTION IN LINE | VACTORING LINE
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-03-15 | 6:00P - 10:00A (3/16) | 24000 | FORCE MAIN ALLISON LANE | GROUND | CONTRACTOR BORING FIBER OPTIC CABLE HIT FORCE MAIN | DUG UP AND REPAIRED FORCE MAIN. MORE ATTENTION TO BE PAID TO LOCATION OF CONTRACTORS
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-05-02 | 5A - 11P | 666000 | CRUMS 1 L.S. | DITCH TO LICK RUN CREEK | HEAVY RAINS 4.0" | TO PREVENT PROPERTY DAMAGE PUMPED WITH 6" INTO DITCH
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-05-02 | 9A - 11:30A | 60000 | EASTBROOK L.S. | DITCH TO LICK RUN CREEK | HEAVY RAINS 4.0" | TO PREVENT PROPERTY DAMAGE PUMPED WITH 6" INTO DITCH
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-05-02 | 7A - 1A (5/3) | 955000 | SPRING STREET L.S. | MILL CREEK | HEAVY RAINS 4.0"
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-05-02 | 5A - 11A (5/3) | 728000 | RIVERPORT II L.S. | DITCH TO LANCASSAGE CREEK | HEAVY RAINS 4.0" | TO PREVENT PROPERTY DAMAGE PUMPED INTO DITCH
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-05-05 | 8A - 1A (5/6) | 100 | LITERS L.S. | GROUND | AIR RELEASE VALVE FAILED | REPLACE AIR RELEASE VALVE VACTORED UP SEWAGE
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-05-18 | ? - 10:30A |  | MANHOLE BRISCOE DRIVE PARKVIEW MIDDLE SCHOOL | GROUND |  | NOTIFIED SCHOOL MAINTENANCE OF PROBLEM AND OVERFLOW WAS CLEANED UP
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-05-28 |  |  | UTICA SELLERSBURG RD | GROUND | FORCE MAIN HIT WHILE INSTALLING CABLE | LS SHUT DOWN AND REPAIR MADE
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-06-21 | 7:00A - 11:00P |  | POWERHOUSE FORCE MAIN | GROUND | CONTRACTOR BROKE FORCE MAIN GOING TO LS | REPAIRED FORCE MAIN, PUMPER TRUCK CONTAINED FLOW
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-06-28 | 11:30 - 12:15P | 30 | MH NEAR 1446 RIDGEWAY DRIVE | GROUND TO STORM SEWER | BLOCKAGE IN DOWN STREAM SEWER LINE ROOTS AND DEBRIS | CLEANED WITH CLEANING TRUCK AND FLUSHED AREA CLEANED ON A BI-MONTHLY BASIS WILL INCREASE CLEANING FREQUENCY
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-07-08 | 11:15A - |  | MH LS FRENCH QUARTER LAS CASITAS APARTMENT | LANCASSANGE CREEK PARKING LOT | EQUIPMENT FAILURE CITY WAS NOTIFIED BY HEALTH DEPARTMENT IT IS PRIVATELY OWNED LS | RESEARCHING AGREEMENT REGARDING WHO IS RESPONSIBLE FOR LS MAINTENANCE AND CLEANING
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-08-15 | 11:30P - 11:45P | 12120 | CRUMS LANE 1 - LIFT STATION | DRAINAGE DITCH | RAIN .66"
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-10-02 |  |  | VETERANS PARKWAY L.S. | GROUND STORMWATER | POWER FAILURE CREW STILL ON LOCATION | AMENDED REPORT WILL BE FILED
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-10-05 | ? - 3:30P | 3400 | VETERANS PKWY L.S. MANHOLE | GROUND TRIB. TO SILVER CREEK | POWER SUPPLY BURNT OUT NO SCADA ALARMS | VACTORED AND SPRAYED DOWN AND LIME APPLIED ADDED TO TWO WEEK ROTATION
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-11-09 | 10:00A - 11:15A | 5600 | FORCE MAIN FROM POWERHOUSE LS | GROUND | CONTRACTOR BORED THROUGH FORCE MAIN | REPAIRED FORCE MAIN AND CLEANED DEBRIS FROM AREA
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-11-20 | 11:00A - 12:00P |  | MH @ 178 GREENWOOD ST. | GROUND | MAIN LINE BLOCKED BY DEBRIS | CLEANED SEWER AND LIMED AREA
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2010-12-15 | 3A - 6:20A | 30000 | POWERHOUSE L.S. | GROUND STORM SEWER | FORCE MAIN INSIDE DRYWELL BROKE SUBMERGED PUMPS RENDERING PUMPS INOPERABLE | PUMPER TRUCK ON SITE TO VACUUM SEWAGE 6" PUMP HELPED KEEP UP WITH FLOW DURING REPAIR
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2010-04-06 | 10:15P - 11:45P | 40 | 316 CATALPA DRIVE | BASEMENT | BLOCKAGE IN MAIN SEWER LINE | LINE CLEARED IMMEDIATELY WITH JET PRESSURE SECTION WAS JUST TREATED AND CALLED TO HAVE WARRANTY TREATED
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2010-04-06 | 10:15P - 11:45P | 40 | 320 PAWPAW | BASEMENT | BLOCKAGE IN MAIN SEWER LINE | LINE CLEARED IMMEDIATELY WITH JET PRESSURE SECTION WAS JUST TREATED AND CALLED TO HAVE WARRANTY TREATED
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2010-05-07 | 12:48P - 3:20P | 5000 | MH BEHIND 2014 ALLISON LANE | GROUND | BLOCKAGE IN MAIN SEWER LINE | CLEANED LINE
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2010-10-05 | 10:00A - 10:35A | 5 | BASEMENT DRAIN 708 SARATOGA | BASEMENT | BLOCKAGE IN SEWER LINE | SEWER LINE CLEANED AND BLOCKAGE REMOVED
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2010-02-06 | 9A - 11:30A | 75 | 648 OHIO AVENUE | BASEMENT | SMALL BLOCKAGE ROOTS CAUSING SEWER MAIN TO SLOWLY BACK UP AND SUMP PUMP WAS ILLEGALLY TIED INTO SEWER LINE | HOME OWNER HAD CLEANING CO. CLEANING UP MESS ADVISED HOME OWNER TO TAKE SUMP PUMP OFF SEWER LINE AND WILL TV SEWER MAIN AND FIX ANY PROBLEM AREAS
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2010-05-02 | 8A - 8P | 25000 | M.H. # 4 442 NORTH INDIANA AVENUE | STREAM TO SILVER CREEK | 3.5" RAIN AND UNBOLTED LID | CLEANED UP MESS AND LOOKING INTO UPGRADE AND BOLTED LID BACK DOWN
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2010-05-02 | 12P - 8P | 4000 | M.H. # 7 PARADISE AVENUE | GROUND TO STORM DRAIN | 3.5" RAIN | CLEANED UP MESS AND LOOKING INTO UPGRADE
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2010-07-28 | 4A - 7A | 5000 | PERRY CROSSING ROAD | STORM DITCH TO CREEK | FORCE MAIN SLIPPED APART IN AREA WHERE CONTRACTOR RELOCATING ROAD | VAC TRUCK COMPANY CLEANED DITCH AND LIMED AREA
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2010-09-19 | ? - 10:00A |  | 1308 FRONTIER MH | DRY STORM DITCH | STICKS AND GREASE IN MH | WILL CLEAN LINE MORE OFTEN
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2010-12-05 | 12:25P - 12:26P | 25 | 1905 WASHINGTON DR MOBILE HOME | TWO TOILETS IN MOBILE HOME | BLOCKAGE IN SEWER MAIN | CLEANED AREA
IN0109533 | WASHINGTON TOWNSHIP RSD | CLARK | 2010-01-15 | 5:00P - 6:00P | 500 | LIFT STATION | DITCH | ELECTRIC RELAY THAT CONTROLS FLOATS FAILED | REPLACED RELAY
IN0109533 | WASHINGTON TOWNSHIP RSD | CLARK | 2010-09-23 | 8:00P - 8:30P | 200 | MH AT HWY 63 LS | DITCH | FLOATS DID NOT WORK | CLEANED AREA, REPLACE FLOATS
IN0039292 | CENTER POINT TOWN OF | CLAY | 2010-04-05 | 7P - 10:15P | 40000 | FINAL PUMP STATION | GROUND | VERY HARD STORM OVERLOADED PUMPING STATION
IN0039292 | CENTER POINT TOWN OF | CLAY | 2010-04-07 | 9P - 1A (4/8) | 5000 | FINAL L.S. | GROUND | 1.5 INCHES RAIN | FOR MORE INFORMATION CONTACT ROY, PRESIDENT OF TOWN BOARD, 812 835-3818
IN0039292 | CENTER POINT TOWN OF | CLAY | 2010-06-13 | 7:15P - 9P | 9000 | MAIN LIFT STATION | GROUND | PRECIPITATION 2"
IN0030228 | SHAKAMAK STATE PARK | CLAY | 2010-07-20 | 8:30A - 9:30P | 500 | CAMP MESS HALL LS | GROUND | POWER OUTAGE 4:30P 7/19 - 12:30P 7/20 | SEWAGE PUMP AND PUMPED LS INTO BYPASS APPLIED LIME
IN0020443 | COLFAX MUNICIPAL STP | CLINTON | 2010-06-14 | 11P - 9A(6/15) |  | MH SOUTH MERIDIAN STREET | STORM SEWER FARM FIELD | 5" RAIN AND 1.5" OVERNIGHT POWER FAILURE | NEW TELEPHONE CALL SYSTEM BEING INSTALLED
IN0020443 | COLFAX MUNICIPAL STP | CLINTON | 2010-06-22 | 4:00A - 9:00P |  | MH SOUTH MERIDIAN ST | STORM SEWER | RAN 2.75"
IN0020630 | KIRKLIN MUNICIPAL STP | CLINTON | 2010-06-14 | 7:30P - 12P (6/16) | 450000 | MH 2, 3, 6, 7, 26, 27, 27A, 44, 61 & PLANT | GROUND AND STORM DRAIN | 6 +" RAIN AREAS OF TOWN FLOODED | REDUCING I & I CASE NO. 2003-12643-W
IN0020630 | KIRKLIN MUNICIPAL STP | CLINTON | 2010-06-22 | 5:45A - 10:00P |  | MH'S 2, 3, 6, 8, 27A, 61, 81, 26, 27. | GROUND AND STORM DRAIN | RAIN 5" | REDUCING I & I
IN0031976 | MULBERRY WWTP | CLINTON | 2010-06-22 | 4:10A - 2:00P | 30000 | MH #130 | YARD | RAIN 3" | APPLIED LME TO AREA
IN0020672 | AUBURN MUNICIPAL STP | DE KALB | 2010-12-11 | 8:45P - 10:50P | 1008000 | CSO 002 2010 SOUTH WAYNE STREET | CEDAR CREEK | MAIN HEADWORKS UNDER CONSTRUCTION RUNNING ALL PUMPS IN HAND MODE RAIN HEAVY THAN EXPECTED | ENGINEERING FIRM IS WORKING ON COMPLETING CONTROLS SHUT OFF CSO PUMPS TO PREVENT FROM RUNNING IN FUTURE
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2010-01-24 | 7:05 - 7:10 | 500 | OUTFALL 3 | BIG RUN | PRECIPITATION AND SNOW MELT | ALL INFLUENT PUMPS RUNNING AND FILLED EQ BASIN AND CONTINUE TO OPERATE USING WET WEATHER OPERATING PROCEDURES
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2010-11-25 | 02:45 - 05:00 | 108000 | OUTFALL 003 | BIG RUN | 1.43 INCHES RAIN | WWTP AND STORM WATER PUMP STATION WERE OPERATED AS DESIGNED
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2010-04-07 | 20:00 - 24:00 | 72000 | SSO #2 PRIOR TO HEADWORKS | GARRETT CITY DITCH | RAIN 1.57" RECEIVED IN 12 HOURS | STAFF IMPLEMENTED WET WEATHER OPERATING PROCEDURES
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2010-05-21 | 6:00P - 5:00P (5/22) | 414000 | SSO #002 | GARRETT CITY DITCH | RAIN 1.68" | STAFF IMPLEMENTED WET WEATHER OPERATING PROCEDURES
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2010-05-31 | 16:15 - 03:30 (6/1) | 205000 | SSO #2 M.H. PRIOR TO HEADWORKS | GARRETT CITY DITCH | RAIN 2.84" | STAFF IMPLEMENTED WET WEATHER OPERATING PROCEDURE
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2010-06-27 | 15:15 - 20:00 | 6000 | MH PRIOR HEADWORKS SSO#2 | GARRETT CITY DITCH | TOTAL .95" RAIN 45 MINUTE PERIOD | WET WEATHER OPERATING PROCEDURE
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2010-01-21 | 6:00A - 11:00A | 500 | COMB CATCH BASIN WASHINGTON AND MARYLAND | ROADSIDE AND GRASS | PLUG IN LINE COMING OUT OF YARD DRAIN | CONTRACTOR FIXED PLUG AND TOOK YARD DRAIN OFF SANITARY SEWER
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2010-03-11 | 09:00- |  | 375 NORTH CENTER CLEANOUT AT HOUSE | GROUND | PLUG IN HOME OWNERS LINE | TALKED TO HOME OWNER TO HAVE THEM FIX LINE
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2010-05-22 | 8:00A - 9:00P (5/23) |  | COMP SEWER 675 N WAYNE | CEDAR CREEK | RAIN 1.91" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2010-05-22 | 8:00A - 9:00P (5/23) |  | MH BY US 6 LS, 320 WALNUT CLEANOUT | CEDAR CREEK | RAIN 1.91" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2010-06-18 | 6:00A - 5:30P | 210000 | MH AT US 6 LS; MH AT 675 N. WAYNE | GROUND TO CEDAR CREEK | RAIN 1.46" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2010-06-18 | 6 - 17:30 |  | COMB MH SOUTHLAND DRIVE | GROUND | I & I 1.48" RAIN 6 HOURS | MAXIMIZING FLOW WWTP AND ACTIVELY INVESTIGATING I & I
IN0020711 | WATERLOO MUNICIPAL STP | DE KALB | 2010-06-27 | 18:00 - 7 (6/28) | 100000 | MH 675 NORTH WAYNE | GROUND TO CEDAR CREEK | I & I FROM 1.5" RAIN IN 2 HOURS | MAXIMIZING FLOW TO WWTP TOWN ACTIVELY INVESTIGATING WWTP IS RUNNING AT CAPACITY & ALL EFFORTS BEING MADE TO TRANSPORT FLOWS TO WWTP
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-01-13 | 10A - 3P | 200 | 531 GREEN BLVD | GROUND | EQUIPMENT FAILURE CHECK VALVE FAILED | WASH DOWN SOLIDS QUIT USING BRASS CHECK VALVES AND GATE VALVES
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-01-19 | 1:00P - ONGOING | 100 | MH 9-7 133 W. 4TH ST. | GROUND | 8" MAIN PLUGGED | WILL UNPLUG LINE WITH JET MACHINE AND REPLACE 1000' OF CLAY TILE IN MAIN, WASH DOWN AND CLEAN SOLIDS.
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-01-26 | 8A - ONGOING | 50000 | SSO #001 DECATUR LIFT STATION | OHIO RIVER | BACK PRESSURE BLEW OUT INFLATABLE BALL ALLOWING RIVER WATER TO FLOOD STATION | WASH DOWN ANY SOLIDS REINFLATE AND RESET INFLATABLE BALL
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-01-27 | 8A - ONGOING | 50000 | SSO #005 WEST SIDE LIFT STATION | SOUTH HOGAN CREEK | BACK PRESSURE BLEW OUT INFLATABLE BALL ALLOWING RIVER WATER TO FLOOD STATION | WASH DOWN ANY SOLIDS REINFLATE AND RESET INFLATABLE BALL
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-02-03 | 6:00P - 1:00A (2/4) | 2000 | US 50 FORCE MAIN @ BILLINGSLY DR. | GROUND TO STREAM | 8" CAST IRON FORCE BROKE AT PREVIOUS REPAIR | WASHED DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-03-15 |  | 50000 | WEST SIDE DECATUR LIFT STATIONS | OHIO RIVER | OHIO RIVER AT 50.5' COMING BACK THROUGH OUTFALLS | WASH DOWN SOLIDS; BOTH STATIONS TO BE REHABBED
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-03-26 | 8A - ONGOING | 10000 | DECATUR ST #001 WEST SIDE #005 | SOUTH HOGAN CREEK | 10000 GPD RIVER AND CREEKS SWOLLEN BCK FLOWING THROUGH OUTFALLS | WASH DOWN SOLIDS REHAB STATIONS AND PLUG OVERFLOWS GOES OUT TO BID APRIL
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-04-07 |  | 1000 | 104 VELMA DRIVE | GROUND | UNSURE EQUIPMENT FAILURE AND INCREASED FLOWS .25 INCH RAIN | WASH DOWN SOLIDS KEEP A CLOSER EYE ON L.S.
| AURORA, CITY OF | DEARBORN | 2010-04-10 | 9:00P - 1:00P | 20000 | 148 LIFT STATION 822 SUNNY | OTHER PUMP STATIONS | EQUIPMENT FAILURE | PUMPS GOING NOW AND CLEANED AREA
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-04-22 | ONGOING | 1000 | 820 BUENA VISTA DR. | GROUND | EQUIPMENT FAILURE | STILL INVESTIGATING WILL PROBABLY REHAB ENTIRE STATION
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-05-05 | 3:15P - ONGOING | 10000 | SSO #1 DECATUR ST AND SSO #5 WEST SIDE | OHIO RIVER | RIVER UP OVER L.S. TOO MUCH INFILTRATION | WASH DOWN SOLIDS AND BIDS TO REHAB THESE TWO L.S. ACCEPTED WORK SHOULD START THIS SUMMER
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-05-08 | 7:00A - 10:30A | 200 | 822 SUNNYSIDE | GROUND | PUMP HAS DEAD SHORT TO IT; REPLACED | WASHED DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-05-12 | 5:00P - 5:30P | 100 | 822 SUNNYSIDE DR | GROUND | PUMP BROKE | WASHED DOWN SOLIDS. REPLACING PUMP
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-05-24 | 9:00A - 3:00P | 500 | 822 SUNNYSIDE | GROUND | PUMPS NOT PUMPING LIQUID. MAYBE AN AIRLOCK PROBLEM | WASH DOWN SOLIDS
| AURORA, CITY OF | DEARBORN | 2010-06-09 | 2:00P - | 500 | BURGER KING LS AND UPSTREAM MH | GROUND TO STORM DRAIN | RAIN 2.91" | WASHED DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-06-17 | 7P - 7:15P | 5000 | US 50 8" FORCE MAIN | GROUND TO STORM DRAIN | 12" CRACK | SHUT OFF AND QUICKLY CLAMPED LTCP… EITHER NEW PLANT OR NEW FORCE MAIN TO SDRSD
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-07-05 | 8:00P - 8:00A (7/6) | 50 | SSO #005 WEST SIDE | GROUND | BAD OFF FLOAT | WASH DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-08-04 | 4P - 8A (8/5) | 1000 | MILESTONE DR FORCE MAIN | GROUND | 3" FORCE MAIN PLUGGED SOLID | OPENED FLUSH VALVE WASH DOWN SOLIDS FLUSH MAIN ON REGULAR BASIS
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-11-02 | 10A - 10:30A | 100 | 822 SUNNYSIDE | GROUND | STARTER PUMP #1 SHORTED OUT KICKING BREAKER ALARM TAMPERED WITH AND DID NOT GO OFF | WASH DOWN SOLIDS REPLACE STARTER AND FIX ALARM
IN0050903 | AURORA, CITY OF | DEARBORN | 2010-12-27 | 3P - ONGOING | 100 | 10439 MILLSTONE DR | GROUND | BLOCKAGE ON 3" FORCE MAIN | WASH DOWN SOLIDS
IN0050903 | CITY OF AURORA | DEARBORN | 2010-09-01 | 7:00P - 7:30P | 50 | 601 BUENA VISTA CT. | GROUND | ELECTRIC CONTROL TIMER FAILED | WASHED DOWN SOLIDS, REPLACING PART
INJ063321 | GREENDALE MUNICIPAL STP | DEARBORN | 2010-04-07 | AM | 300 | MANHOLE # 295 | GROUND | HEAVY FLOWS | TOLD VRVC TO READJUST PUMPS DOWN TO REDUCE FLOW TO GREENDALE SYSTEM
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-01-21 | 3:05P - 12:00A |  |  |  | RAIN .75 | BUILDING NEW PLANT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-01-24 | 8:31P - 8:15A (1/25) | 110694 | PLANT PARTIAL TREATED | WHITAKER CREEK | PRECIPITATION .5 INCHES | TURNED OFF BLOWER TO PREVENT SOLIDS FROM ENTERING FINAL EFFLUENT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-01-24 | 9:51A - 6:24P | 82764 | PLANT PARTIAL TREATED | WHITAKER CREEK | PRECIPITATION .5 INCHES | TURNED OFF BLOWER TO PREVENT SOLIDS FROM ENTERING FINAL EFFLUENT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-03-25 | 7:08P - 4:52 (3/26) |  | AT PLANT | BYPASS OF A TREATMENT PROCESS | RAIN .8 AND .6 | BUILDING NEW PLANT BIDDING ON PROJECT NOW
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-04-25 | 9:34P - 7:22A (4/26) | 13675 | PLANT | WITAKER'S BRANCH | RAIN 1.0" | TURNED AIR OFF, BUILDING NEW PLANT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-05-02 | 2:22P - 11:59P |  | PLANT ONLY | WITAKER CREEK | PRECIPITATION 1.8" | BUILDING NEW PLANT CLOSING 5/27/10
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-05-03 | 1:17A - 6:56A |  | PLANT ONLY | WITAKER CREEK | PRECIPITATION 1.8" | BUILDING NEW PLANT CLOSING 5/27/10
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-06-09 | 2:53P - 7:45P |  | PLANT | WITAKER CREEK | RAIN 1.8" | BUILDING NEW PLANT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-06-12 | 9:53A - 4:36P |  | PLANT AND MAIN LIFT STATION | WITAKERS CREEK | PRECIPITATION 2" | NEW PLANT JULY 2011
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-06-14 | 9:58P - 5:16A (6/15) | 95000 | PLANT | WHITAKER CREEK | PRECIPITATION .8" | TURNED OFF BLOWERS & NEW PLANT JULY 2011
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-06-27 | 11:50P - 8A (6/28) | 54149 | PLANT | WITAKER CREEK | PRECIPITATION 1.7" | TURNED OFF AIR BUILDING NEW PLANT JULY 2011
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-10-06 | 4:00P - 8:09A (10/7) |  | LIFT STATION | CREEK | ELECTRIC COMPANY TURNED OF POWER TO LS | TURNED POWER ON
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-11-24 | 8:04P - 4:19A (11/25) | 35272 | PLANT |  | RAIN .55" | TURNED OFF AIR TO PLANT FOR BYPASS. BUILDING NEW PLANT
IN0023817 | MOORES HILL MUNICIPAL STP | DEARBORN | 2010-12-31 | 12:00A - 8:27A |  | PLANT |  | TURN OFF AIR TO PLANT FOR BYPASS | BUILDING NEW PLANT MAY 2011
IN0043168 | VALLEY RURAL UTILITY | DEARBORN | 2010-01-25 | 7:00A - 6:30P | 13000 | 002 | DOUBLE LICK CREEK | CONSTRUCTION AND PRECIPITATION | TESTED FOR AMMONIA WORKING ON LIFT STATIONS CALLED THE ENGINEER FOR SEWER SYSTEM EVALUATION
IN0043168 | VALLEY RURAL UTILITY | DEARBORN | 2010-06-12 | 1:30P - 3P | 2250 | 003 | HIDDEN VALLEY LAKE | RAIN MORE THAN 3" IN ONE HOUR | WORKING ON LIFT STATIONS HIRED ENGINEER FOR SEWER SYSTEM EVALUATION
IN0043168 | VALLEY RURAL UTILITY | DEARBORN | 2010-06-15 | 5:30P - 5:45P | 375 | L.S. #2 | HIDDEN VALLEY LAKE | STRUCK BY LIGHTENING BURNT OUT FUSES | REPLACED FUSES IMMEDIATELY hired ENGINEER FOR SEWER SYSTEM EVALUATION
IN0043168 | VALLEY RURAL UTILITY | DEARBORN | 2010-11-26 | 10A - 2:45A (11/28) |  | MH | HIDDEN VALLEY LAKE | ROOT AND GREASE | HIRED ENGINEER FOR SEWER EVALUATION APPROVED BUT WAITING ON FUNDING TO REPLACE 2/3 OF L.S. THIS LINE IS ON PRIORITY LIST TO BE REPAIRED
IN0020842 | SAINT PAUL MUNICIPAL STP | DECATUR | 2010-06-13 | 1A - 8A | 30000 | RIVERBEND L.S. | FLAT ROCK RIVER | PRECIPITATION 4"
IN0020842 | SAINT PAUL MUNICIPAL STP | DECATUR | 2010-06-13 | 2A - 5A | 15000 | MH CONGER & WASHINGTON | STORM SEWER | PRECIPITATION 4"
IN0020842 | SAINT PAUL MUNICIPAL STP | DECATUR | 2010-06-20 | 2A - 10A |  | RIVERBEND L.S & CONGER WASHINGTON ST MH | FLATROCK RIVER & STORM SEWER | PRECIPITATION 2.5"
IN0020842 | SAINT PAUL MUNICIPAL STP | DECATUR | 2010-06-22 | 9A - 11A |  | RIVERBEND L.S & CONGER WASHINGTON ST MH | FLATROCK RIVER & STORM SEWER | PRECIPITATION 2.5"
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-01-22 |  |  | LIFT STATION SOUTH WEST STREET | MILLSTONE CREEK | .85 INCHES RAIN OVERNIGHT | CLEAN AREA AS NEEDED AND AG 2003-130-94w
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-01-24 | 8A - 8A (1/25) |  | LIFT STATION SOUTH WEST STREET | MILLSTONE CREEK | .5 INCHES RAIN OVERNIGHT AND ANOTHER .4 DURING DAY | CLEAN AREA AS NEEDED AND AG 2003-130-94w
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-02-22 | AM - AM (2/23) |  | LIFT STATION ON WEST STREET MANHOLES 3 AND 73 | MILLSTONE CREEK | RAIN .4 INCHES AND SNOW MELT 8 INCHES | AG 2003-130-94W
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-03-26 |  |  | LS AT S. WEST ST | MILLSTONE CREEK | RAIN .9" | CLEANED AREAS
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-04-08 |  |  | MH 73 LS ON S. WEST ST. | MILLSTONE CREEK | RAIN 1.25" | CLEAN AREAS
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-05-02 | A - 2P |  | L.S. ON SOUTH WEST STREET | MILLSTONE CREEK | RECEIVED 1.1" RAIN ON SATURDAY (5/1) | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-05-12 |  |  | S. WEST ST LS | MILLSTONE CREEK | RAIN .85 | CLEANED AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-05-17 | ? - A (5/18) |  | L.S. SOUTH WEST STREET | MILLSTONE CREEK | RAIN 1.2" | CLEAN AREAS AS NEEDED AG 2003-13094W
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-09 | 3:00P |  | S. WEST ST. LS AND SEVERAL MH'S | MILLSTONE CREEK | RAIN 1.85" | CLEANED AREAS
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-12 | AM - PM |  | MH 73, 75, 76, 80, 81, 83, 96, 96A, 3, 4B, 6, 7, 8, 13 | MILLSTONE CREEK | HEAVY RAIN 2.5 - 4 INCHES | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-12 | AM - AM (6/13) |  | LIFT STATION ON S WEST ST | MILLSTONE CREEK | HEAVY RAIN 2.5 - 4 INCHES | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-14 | A - A (6/15) |  | L.S. S WEST STREET & MH 73, 76 | MILLSTONE CREEK | 1.65" TOTAL 6.4" IN LAST 7 DAYS | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-15 | A - A (6/16) |  | L.S. S WEST STREET & MH 73, 76 | MILLSTONE CREEK | 1.65" TOTAL 6.4" IN LAST 7 DAYS | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-19 |  |  | LS ON S. WEST ST. | MILLSTOWN | RAIN | CLEANED AREA AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-21 | 11:00A - 11:00P (6/22) |  | LS ON S. WEST ST., MH 73 AND 76 | MILLSTONE CREEK | RAIN 1.5" | CLEANED AREA AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-06-28 | ? - 2P |  | LS SOUTH WEST STREET | MILLSTONE CREEK | 1.25" RAIN OVERNIGHT | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-11-25 | 11/26 |  | LS ON S. WEST ST. | MILLSTONE CREEK | RAIN 3" | CLEANED AND DISINFECTED AREA
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2010-11-30 |  |  | L.S. ON WEST STREET | MILLSTONE CREEK | PRECIPITATION 1.65" | CLEAN AREA AS NEEDED
IN0020672 | AUBURN MUNICIPAL STP | DEKALB | 2010-07-28 | 5:45P - 8P | 1534000 | 2010 SOUTH WAYNE STREET CSO #2 | CEDAR CREEK | .55" HAD POWER BLURB DUE TO LIGHTING STRIKE ONE PUMP FAILED TO RESTART | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT SCHEDULED TO HAVE PUMP REPAIRED
IN0022462 | BUTLER MUNICIPAL STP | DEKALB | 2010-05-21 | 6:00P - 3:00A (5/22) | 5900000 | OUTFALL 003 | BIG RUN | RAIN 4" | FLOW MAXIMIZED THRU WWTP
IN0022969 | GARRETT MUNICIPAL STP | DEKALB | 2010-04-25 | 8:30P - 6:15A | 90000 | SSO #2 | GARRET CITY DITCH | RAIN 1.19" | IMPLEMENTED WET WEATHER OPERATING PROCEDURE
IN0062669 | ALBANY MUNICIPAL STP | DELAWARE | 2010-03-02 | 10:00A - 1:00P | 45000 | GRAVITY MANHOLE TO LIFT STATION WHICH GOES TO WETLAND (OUTFALL 001) | GROUND THAT IS BLENDED WITH OUTFALLS 001, 002, 003 | DISCHARGE PIPING @ LIFT STATION BLEW APART. PUMPS COULD NOT GET PRESSURE | STOPPED FLOW TO LIFT STATION TO MINIMIZE BYPASSING, REPAIR ON THE WAY AND SAMPLES SENT TO LAB
IN0062669 | BELL AQUACULTURE, LLC | DELAWARE | 2010-04-15 | 3:30P | 200 | LIFT STATION | RILEY STAFFORD DITCH | PIPING BLEW APART IN L.S. EFFLUENT | SHUT DOWN ALL WATER GOING TO FISH TANKS TO REPAIR LINE AND SAMPLES COLLECTED
IN0021652 | EATON MUNICIPAL STP | DELAWARE | 2010-05-20 | 8:20 - 2P |  | CSO #2 | HOLDREN DITCH | EQUIPMENT FAILURE OVERFLOW FLOODED PUMPS AND ELECTRIC PANEL | EMERGENCY PUMPS REPLACE ALL PIPING, SUMP PUMP, AND INSTALL BACK FLOW DEVICE
IN0020338 | GASTON MUNICIPAL STP | DELAWARE | 2010-03-13 | 8:53A - 9:00A (3/14) | 781000 | OUTFALL #1 GASTON WWTP | PIPE CREEK | RAIN 2.4" | TERTIARY TREATMENT POND BYPASSED TO PREVENT OVERFLOW AND RUNNING OFF SITE; TRYING TO REDUCE I & I
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-03-13 | 12:10A - 4:25A |  | BENSON HOUSE | JAKES CREEK | RAIN 1.25" | STORAGE TANK UNDER CONTRACTION FOR WET WEATHER EVENTS
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-03-13 | 12:25A - 12:25A (3/14) | 156955 | BENSON MANHOLE | JAKES CREEK | RAIN 2.49" | FLOW MAXIMIZED TO SHORTEN THE DURATION OF EVENT
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-03-25 | 2P - 12P (4/5) | 100 | MORRISON RD AND JACKSON STREET | HIAT DITCH | BROKEN 10" SANITARY LINE | MUNCIE SD SPECIFYING PROJECT REPAIR SHOULD BEGIN 3/29/10 PROJECT COMPLETED 4/5/10
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-03-31 | 2:00P - 5:15P | 440662 | CSO #18 | WHITE RIVER | PIPE PLUG UPSTREAM OF PLANT BROKE FREE | LOCATE AND REMOVE PLUG
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-06-04 | 7:25A - 7:40P | 29188 | CSO 18 | WHITE RIVER | OVERFLOW STRUCTURE AND PUMP FAILED | REPAIR PUMP
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-06-14 | 10:18P - 5:10A (6/15) | 492862 | BENSON L.S. | GROUND | HIGH RAINFALLS 2.2" | NOTIFIED BY PAGER ACTION IN BUILDING STAGES
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-06-21 | 10:37A - 3:00P | 6275 | BENSON | JAKE CREEK | RAIN
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-07-07 | 7:51A - 8:50A | 82696 | BEECH GROVE CSO | WHITE RIVER | WATER MAIN BREAK MADISON AND KIRBY AVENUE | MONITORED WATER AND NO EFFECT ON AQUATIC LIFE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-09-13 | 1:00P - 1:10P | 327 | CSO #28 | WHITE RIVER | INDIANA AMERICAN WATER FLUSHING FIRE HYDRANTS CAUSED OVERFLOW AND ALARM | HYDRANT RUN OFF ONLY
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-09-21 | 6:50A - 6:55A | 1694 | CSO #28 | WHITE RIVER | HYDRANT FLUSHING BY INDIANA AMERICAN WATER
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2010-09-24 | 10:01A - 11A | 2194 | THOMAS DRIVE CSO 26 | BUCK CREEK | OBSTRUCTION IN COLLECTION SYSTEM | REMOVAL OF OBSTRUCTION AND PREVENTATIVE MAINTENANCE ON COLLECTION SYSTEM
IN0020150 | YORKTOWN MUNICIPAL STP | DELAWARE | 2010-01-15 | 10:00A | 100 | LIFT STATION (YORKTOWN SPORTS COMPLEX) | GROUND | SEWAGE SPILL AROUND LIFT STATION | PUMPED DOWN TO NORMAL, CLEANED AND LIMED, CONTRACTOR FIXED BROKEN PIPE
IN0020150 | YORKTOWN MUNICIPAL STP | DELAWARE | 2010-03-13 | 9:00P - 9:00A(3/14) |  | MANHOLE | GROUND AT WWTP | RAIN 2.52" | PUMPS PUMPING MAX FLOW; I & I REDUCTION IN PLACE
IN0023124 | HUNTINGBURG MUNICIPAL STP | DUBOIS | 2010-04-10 | 1:00P - 4:00P | 2000 | VAN BUREN ST LIFT STATION FORCE MAIN | STORM SEWER | BROKEN FORCE MAIN | FORCE MAIN REPAIRED
IN0023124 | HUNTINGBURG MUNICIPAL STP | DUBOIS | 2010-07-18 | 11P - 6A (7/19) | 5000 | VAN BUREN STREET LS | STREAM | ELECTRICAL OVERLOADS TRIPPED DUE TO LIGHTNING STRIKE | OVERLOADS REPAIRED
IN0023124 | HUNTINGBURG MUNICIPAL STP | DUBOIS | 2010-08-12 | 6:00A - 7:30A | 1000 | 200 WEST LS | STREAM | OPERATOR ERROR, PUMPS NOT TURNED OFF AFTER MAINTENANCE
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2010-07-04 | 4:00P - 10:00A (7/6) | 20000 | SUNRISE LS | GROUND | LEAKING VALVE | CAPPED LINE, CLEANED AREA WITH VACTOR
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2010-07-19 | 7:30P - 8:30P | 10000 | HOCHGESANG AVENUE MH | CREEK | LS HIT BY LIGHTNING | PUT PUMPS CONTROLS ON BACK UP FLOATS REPAIR DAMAGED PARTS
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2010-04-29 | 11:30A - 2:00P |  | SERVICE LINE TO FORCE MAIN | GROUND | ADAPTOR ON 2" CURB STOP ASSEMBLY BROKE | REPLACED ASSEMBLY WITH NEW ONE
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2010-07-29 | 7:30A - 11A |  |  | GROUND | 8" PVC FORCE MAIN CRACKED | REPLACED SECTION OF LINE AND PUT BACK IN SERVICE
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2010-10-10 | 10:00P - 7:00A (10/11) |  | LIFT STATION | GROUND | HIGH LEVEL LIGHT BLOWN; SCATA DID NOT PAGE OUT | REPLACED HIGH LEVEL LIGHT; WORKED ON SCATA
IN0038989 | BROADMORE ESTATES | ELKHART | 2010-08-25 | 8:30A - 9:15A | 100 | LOT 183, 2ND MANHOLE FROM WWTP EASTSIDE | GROUND | PLUG IN PUMP | REPAIRED PUMP, LIMED AREA
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-02-01 | 8:00A - 9:00P | 585 | CSO 40 MCNAUGHTON PARK | ST. JOE RIVER | LARGE MASS OF CLOTH PLUGGED EFFLUENT LINE BEFORE BAR SCREEN CHAMBER | TRUCK PUMPED OUT MATERIAL AND RETURNED FLOW TO NORMAL. INVESTIGATING A CUSTOMER
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-05-21 | 3:00P |  | 525 MAPLE ROW, 1321 LOCUST ST., 1142 BEARDSLEY AVE., 321 W. DINEHART AVE. | BASEMENT BACK-UP | RAIN 2.28" | LOOKING AT LONG TERM OPTIONS FOR SEWER SEPARATIONS
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-06-18 | 7:45A - 9:49A | 1088 | CSO 30, CHARLES AND PRINCETON | ELKHART RIVER | FAILURE OF BYPASS PUMP | MOVING FORWARD WITH CSO LTCP PROJECTS
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-21 | 6:33A - 6:59A | 259 | CSO 20 BRIDGE AND HUDSON | ST JOSEPH RIVER | WORK INTERRUPTED BY AN EMERGENCY AND LEFT IN A HASTE PUMPS WERE LEFT IN OFF MODE DURING CLEANING | SOP WILL BE REVISED TO ASSIGN A POINT PERSON TO DO FINAL INSPECTION UPON LEAVING A SITE
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-28 | 4:30 - ? |  | 1630 FRANCIS | BASEMENT | 1.1" IN 30 MINUTES HYDRAULICALLY OVERLOADING SYSTEM | CONTINUING EVALUATE LONG-TERM OPTIONS FOR SEWER SEPARATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-28 | 4:30 - ? |  | 247 DINEHART | BASEMENT | 1.1" IN 30 MINUTES HYDRAULICALLY OVERLOADING SYSTEM | CONTINUING EVALUATE LONG-TERM OPTIONS FOR SEWER SEPARATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-28 | 4:30 - ? |  | 215 EAST INDIANA AVE | BASEMENT | 1.1" IN 30 MINUTES HYDRAULICALLY OVERLOADING SYSTEM | CONTINUING EVALUATE LONG-TERM OPTIONS FOR SEWER SEPARATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-28 | 4:30 - ? |  | 1829 FRANCIS | BASEMENT | 1.1" IN 30 MINUTES HYDRAULICALLY OVERLOADING SYSTEM | CONTINUING EVALUATE LONG-TERM OPTIONS FOR SEWER SEPARATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-28 | 4:30 - ? |  | 222 THORNDALE | BASEMENT | 1.1" IN 30 MINUTES HYDRAULICALLY OVERLOADING SYSTEM | CONTINUING EVALUATE LONG-TERM OPTIONS FOR SEWER SEPARATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-28 | 4:30 - ? |  | 1701 FRANCIS | BASEMENT | 1.1" IN 30 MINUTES HYDRAULICALLY OVERLOADING SYSTEM | CONTINUING EVALUATE LONG-TERM OPTIONS FOR SEWER SEPARATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-07-28 | 4:30 - ? |  | 2015 MORTON | BASEMENT | 1.1" IN 30 MINUTES HYDRAULICALLY OVERLOADING SYSTEM | CONTINUING EVALUATE LONG-TERM OPTIONS FOR SEWER SEPARATION
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2010-11-18 | 2:30P -3:30P | 500 | 1600 BROOKWOOD | BASEMENT | GREASE
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-01-21 | 7:00P - 8:00P | 50 | SEWER MAIN 201 CHICAGO AVE. | BASEMENT | SEWER BLOCKAGE CAUSED BACKUP | REMOVED BLOCKAGE
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-01-25 | 2:00P - 3:00P | 10 | SEWER MAIN 1905 WOODWARD PL | BASEMENT | SEWER BLOCKAGE CAUSED BACKUP | REMOVED BLOCKAGE
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-03-01 | 2:30P - 3:30P | 40 | MANHOLE AT 115 SILVERWOOD LANE | STREET | BLOCKAGE IN LINE | CLEARED BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-05-29 | 10:00A - 11:00A | 5 | SEWER MAIN 404 RIVER AVE. | TUB | LATERAL DAMAGED DURING CONSTRUCTION OF NEW SEWER LINE
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-06-16 | 2P - 2:30P | 50 | 1219 WEST CLINTON | BASEMENT | ROOTS IN SEWER MAIN | CLEANED SEWER MAIN AND REMOVED ROOTS ROUTINE CLEANING
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-06-18 | 7:15P - 8:00A (6/19) | 5750000 | CSO'S 002, 004, 007 | ELKHART RIVER | LOST POWER AT WWTP
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-06-18 |  |  | 1613 WEST AVENUE | BASEMENT | EXCESSIVE RAIN TREE ROOTS | MAIN WAS CLEANED AND ADDED TO 6 MONTH CLEANING INSPECTION SCHEDULE POSSIBLE SLIP LINING SECTION
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-06-23 | 10:00P - 12:00A (6/24) | 315000 | CSO 002, 007 | ELKHART RIVER | POWER FAILURE | MANUALLY SWITCHED POWER FEEDS
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-06-23 |  |  | 1613 WEST AVENUE | BASEMENT | EXCESSIVE RAIN TREE ROOTS | MAIN WAS CLEANED AND ADDED TO 6 MONTH CLEANING INSPECTION SCHEDULE POSSIBLE SLIP LINING SECTION
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-06-27 |  |  | 1613 WEST AVENUE | BASEMENT | EXCESSIVE RAIN TREE ROOTS | MAIN WAS CLEANED SAND ADDED TO 6 MONTH CLEANING INSPECTION SCHEDULE POSSIBLE SLIP LINING SECTION
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-07-06 | 12:00P - 2:00P | 200 | FORCE MAIN FROM CARTER LS | GROUND | BROKEN FORCE MAIN | REPAIRED FORCE MAIN AND CLEANED WITH VACTOR
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2010-09-08 | 2A - 12P | 125950 | CSO 004 | ELKHART RIVER | SET UP BYPASS PUMPING TO WORK ON 30" AND BYPASS PUMPING EQUIPMENT FAILED | RAISED OVERFLOW WEIR AND CSO LEVEL WILL BE WATCHED OR NIBLOCK WILL HAVE SOMEONE MONITORING PUMPS 24 HOURS
IN00761 | JOHNSON CONTROLS, INC. | ELKHART | 2010-06-23 | 21:07 - 0 (6/24) |  | GROUND REMEDIATION SYSTEM 1301 E MONROE STREET GOSHEN | ROCK RUN CREEK | STORM CAUSED POWER FLUXUATIONS PUT TWO OFF-SITE WELLS CONTINUED TO RUN | STEPS ARE BEING TAKEN TO PROVIDE AN ALARM
IN0021466 | NAPPANEE MUNICIPAL STP | ELKHART | 2010-05-11 | 10:00A - 11:00A |  | 503 N. MADISON ST | BASEMENT | ROOT BALL | CUT ROOT BALL
IN0021466 | NAPPANEE MUNICIPAL STP | ELKHART | 2010-11-19 | 1:00P - 2:00P | 400 | MH INSIDE PLANT | WALKING PATH OUTSIDE PLANT | AIR RELIEF VALVE STUCK ON SLUDGE TRANSFER LINE | VACTORED UP RESIDUAL OFF GROUND
IN0021466 | NAPPANEE MUNICIPAL STP | ELKHART | 2010-12-21 | 3:00P - 3:30P |  | 358 E. JOHN ST. | BASEMENT | SEWER BLOCKAGE | JETTED SEWER
IN0058025 | NEW PARIS CONSERVANCY DISTRICT | ELKHART | 2010-03-25 | 1P - 1:10P | 1000 | MEADOW FLOWER DRIVE AND RED CEDAR | STORM SEWER AND RETENTION POND | SEWER CLEANING PROJECT JET VAC TRUCK DECANTED INTO STORM SEWER | SEPTIC PUMPER PUMPED OUT EFFECTED STORM SEWER AND 10,000 FROM THE EFFECTED AREA OF RETENTION POND IN FUTURE NEW PARIS CD WILL INSPECT BEFORE DECANTING IN MANHOLES
IN0032336 | CONNERSVILLE MUNICIPAL STP | FAYETTE | 2010-03-12 | 8:58P - 7:34A (3/13) |  | MH AT 302 EAST DRIVE | STORM SEWER CATCH BASIN | RAIN .71" | CREW RAN LINE
| EVERTON RSD | FAYETTE | 2010-12-09 | 6A - 9:30A |  | 5499 SOUTH STATE RD 1 LS 14 | GROUND PRIVATE POND | EQUIPMENT FAILURE | CALLED ELECTRICIAN TO CHECK CONTROLS
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2010-04-19 |  | 5000 | 12 " FORCE MAIN | GROUND | NEW CONSTRUCTION BORING HIT 12 " FORCE MAIN | FORCE MAIN INCORRECTLY MARKED ON MAPS REROUTE 100 FOOT OF FORCE MAIN LIME AREA
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2010-05-02 |  | 350 | L.S. | AROUND L.S. | RAIN | SPREAD LIME IN AFFECTED AREA
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2010-05-02 |  | 450 | MANHOLE | AROUND MANHOLE | L.S. WAS OVERLOADED FROM RAINFALL | SPREAD LIME IN AFFECTED AREA
| GEORGETOWN COLLECTION SYSTEM | FLOYD | 2010-11-04 |  | 100 | CORYDON RIDGE ROAD | DITCH | COMPANY BORING UNDER ROAD HIT 4" MAIN | SHUTDOWN L.S. AND REPAIRED LINE CLEANED ROAD OFF AND ANY DEBRIS IN THE AREA
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-02-23 | 2:45P - 4P | 1350 | 1315 E SPRING ST | BOILER ROOM FLOOR | BLOCKAGE IN SEWER MAIN | CLEANED BLOCKAGE IN SEWER MAIN AND BACKFLOW PREVENTION DEVICE WAS ADVISED FOR PROPERTY OWNER
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-02-26 | 9:15A - 10:30A | 1000 | NW CORNER OF CHERRY ST. AND BONO RD. COMMON LATERAL TO B13 TRUNK FROM B-13-C1 | GROUND SURFACE | UTILITY POLE WAS REPLACED DUE TO TRAFFIC ACCIDENT AND DAMAGED COMMON SERVICE LATERAL | STRUCTURE UPSTREAM BEING PUMPED AND TRUCK TO SANITARY STATION AT WWTP FOR TREATMENT. PIPE LINE TO BE REPAIRED NEXT WEEK
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-03-09 | 2P - 10:30A (3/10) |  | ALLEY OF EKIN & CULBERTSON MH | STORM SEWER | BLOCKED SANITARY LINE | RELIEVE BLOCKAGE DOWNSTREAM GETTING QUOTE TO POLY LINE DEFECTIVE BRICK MANHOLE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-03-16 | 1:20P - 2:30P |  | 305 AMBURGHY DR. MH# 4-61 | GROUND | BLOCKAGE CAUSED BY SMALL ROOTS CATCHING DEBRIS | CUT ROOTS AND CLEANED LINE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-03-16 | 8:15A - 9:30A | 375 | MH 25-R17EE 4115 PROFIT CT. | GROUND AND FLAT RUN CREEK | BLOCKAGE IN MH | RELIEVED BLOCKAGE AND CUT ROOTS, SOLIDS REMOVED AND LIME APPLIED
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-04-27 | 5:30P - 10:30A (4/28) | 22500 | BASIN 1A MH C53 | STORM SEWER | BLOCKAGE IN MAIN LINE | UNPLUGGED LINE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-05-02 | 7:20A - 9:20A | 120 | BASIN 27-2 MH 49A | STORM SEWER | MORE THAN 3" RAIN IN 24 HRS | CONDUCTING A PRELIMINARY ENGINEERING STUDY TO DETERMINE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-05-02 | 7:30A - 9:30A | 800 | PRIVATE CLEAN OUT BASIN 16 & MH 16-38 | UNNAMED TRIB TO SILVER CREEK | MORE THAN 3" RAIN IN 24 HRS | BASIN #16 SCHEDULED FOR PILOT LINING IN 2011
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-05-02 | 8A - 12P | 9960 | MH 13-C46 & 13-C47 | FALLING RUN CREEK | MORE THAN 3" RAIN IN 24 HRS | UPGRADE OF #14 WILL HELP PROVIDE RELIEF DURING RAIN EVENTS ALSO IN NEXT 5 YRS BASIN #13 SCHEDULED FOR LINING
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-05-02 | 6P - 9P | 5520 | MH 14-123A & MH 14-101 | FALLING RUN CREEK | MORE THAN 3" RAIN IN 24 HRS | BASIN #14 L.S. WILL BE UPGRADED FROM 7800GPM TO 10500GPM IN 2011
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-07-30 | 1:30P - 2:30P | 300 | 3941 DUNBAR AVE MH | GROUND TO KNOB CREEK | F.O.G. SOFT PLUG BLOCKAGE | JETTER TRUCK CLEANED LINE THOROUGHLY CCTV
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-09-29 | 2P - 2:30P |  | 148 EAST MARKET STREET LATERAL FROM 6-18A | BASEMENT | F.O.G. SOFT PLUG BLOCKAGE | RELIEVED BLOCKAGE AND CLEANED LINE THOROUGHLY
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2010-11-25 | 1P - 11A (11/26) | 10000 | 220 MAEVI DR. 2 M.H. | BASEMENT AND GROUND | RESTRICTION IN PIPE AND PRECIPITATION 2" | LINE FLUSHED AND ROOTS CUT AND CCTV INVESTIGATION
IN0043923 | WYMBERLY WOODS UTLS. | FLOYD | 2010-11-08 | 8:55A - 10:50A | 100 | MH BEHIND 4053 TANGLEWOOD LANE | GROUND AROUND MANHOLE | SQUIRREL CAUSED POWER FUSE TO BLOW CAUSING LS POWER TO SINGLE PHASE | FUSE RESET, PUMPING RESUMED, AREA CLEANED
IN0039390 | KINGMAN MUNICIPAL STP | FOUNTAIN | 2010-06-22 | 6:00A - 9:00A | 1500 | 2ND LIFT STATION | MILL CREEK | RAIN 3"
IN0024716 | VEEDERSBURG MUNICIPAL STP | FOUNTAIN | 2010-02-25 | 2:49P - 3:05P | 25000 | 200 SOUTH PERRY STREET MH #26 & 53 | GROUND | SEWER COLLECTION SYSTEM HAD BLOCKAGE | JET EQUIPMENT USED TO CLEAN LINE AND RECHECK MANHOLE
IN0039268 | BATESVILLE MUNICIPAL STP | FRANKLIN | 2010-03-29 | 9:30P - 10:15P |  | AEROBIC DIGESTER | LITTLE LAUGHERY CREEK | VALVE MALFUNCTIONED ALLOWING SLUDGE STORAGE TANK TO BACK FEED TO DIGESTER | PUT AIR PLUG IN STORM SEWER THEN PUMPED AND LIMED
| METAMORA REGIONAL SEWER DIST | FRANKLIN | 2010-01-30 | 1:12P |  | 18149 US 52 | GROUND | SEWAGE RELEASE DUE TO FAILED GRINDER STATION
IN0023973 | OLDENBURG MUNICIPAL STP | FRANKLIN | 2010-06-12 | 7 - 14:00 | 80000 | LIFT STATION | CREEN HAVEY BRANCH | PRECIPITATION 3.02" | WILL APPLY OCRA GRANT JULY AND IF FUNDED LOOKING AT BUILDING EQ BASIN
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-02-03 | 9:04P - 10:00P | 2 | MANHOLE 18 TO 21 | BASEMENT | DISINFECTION WIPES IN SEWER LINE | CLEANED LINE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-02-16 | 6:38A - 7:30A | 5 | 1319 JACKSON BLVD LATERAL BACK UP | BASEMENT | SEWER LINE BACKUP | CLEANED LINE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-03-01 | 7:55A - 8:15A | 2 | 1012 JEFFERSON ST | BASEMENT | PROBLEM IN HOMEOWNER'S LATERAL | SENT HOMEOWNER COPY OF SEWER ORDINANCE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-03-17 | 11:44A - 12:10P | 10 | 300 EAST 18TH ST MH 99 TO 98 | BASEMENT | RESIDENCE LATERAL LINE PLUGGED | RAN SEWER LINE BUT DID NOT HELP, TOLD HOMEOWNER TO CALL A PLUMBER
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-04-10 | 12:56P - 2:15P | 10 | 2111 BOULEVARD ST | HOMEOWNERS BATH TUB AND DRAINS |  | REPLACED VACUUM CONTROL VALVE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-05-23 | 8:30A - 10:00A | 5 | 2420 WOLF POINT DR | YARD | BLOCKAGE IN LATERAL | PLUMBER CLEARED BLOCKAGE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-06-12 | 1:46P - 3:15P | 5 | MH 15TH & COLLEGE STREETS | GROUND | SEWER LINE PLUGGED WITH STICK AND GREASE | RAN SEWER LINE WITH VACTOR TRUCK AND MONITOR LINE MORE OFTEN
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-10-11 | 11:30A - 12:15P | 2 | 4284 DEERE TRAIL CT | GROUND | VACUUM CONTROL VALVE FAILED | REPLACED VALVE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-10-26 | 3:30P - 4:00P | 400 | 1ST STAGE CLARIFIER AT TREATMENT PLANT | STORM SEWER | PUMPS BECAME AIR LOCKED WHEN INSTALLING TRANSDUCER FOR NEW VFD SYSTEMS | DIVERTED FLOW TO MIXING TANK TO STOP OVERFLOW FROM CLARIFIER
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2010-12-10 | 8:30A - 9:15A | 50 | 514 E. 8TH | BASEMENT | BLOCKED WITH RAGES AND SANITARY WIPES | JETTED LINE
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2010-03-25 | 6:15P - 9:00A (3/26) |  | PLANT | STREAM SOUTH FORK | RAIN 2.2" | SHUT OFF OXIDATION DITCH MOTORS TO RETAIN SLUDGE FROM WASHING OUT AND DIVERTED WATER TO EQ BASIN
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2010-11-24 | 12:15P - ONGOING |  | WWTP | STREAM SOUTH FORK | 2" RAIN | TURNED OFF OXIDATION DITCH ROTORS TO ELIMINATE SLUDGE WASHOUT SEEKING GRANT MONEY
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2010-11-24 | 12:15P - 3:00A(11/26) | 1000000 | PLANT LOCATION | STREAM SOUTH FORK | RAIN 4.4" | TURNED OF OXIDATION DITCH ROTORS TO ELIMINATE SLUDGE WASH OUT
IN0038288 | OWENSVILLE MUNICIPAL STP | GIBSON | 2010-01-05 | 10:00P - 10:00A (1/6) | 50000 | HWY 168 LS | MONTGOMERY DITCH | BOTH PUMPS FAILED | CLEANED SOLIDS IN DITCH, RENTED PUMP, FIXING OTHER PUMPS
IN0038288 | OWENSVILLE MUNICIPAL STP | GIBSON | 2010-11-26 | ? - 4:45P | 1000 | 401 NORTH BENNITT | BASEMENT | SEWER MAIN BLOCKAGE | UNSTOPPED BLOCKAGE HOMEOWNER CONTACT CONTRACTOR CLEAN BASEMENT
| JONESBORO UTILITIES | GRANT | 2010-03-13 | 12:00P - 10:00P | 300000 | I-11 AND I-18 | GROUND | RAIN 2" | CLEAN MANHOLES; WASTEWATER IS SENT TO GAS CITY FOR TREATMENT
| JONESBORO UTILITIES | GRANT | 2010-03-13 | 12:00P - 10:00P |  | MH I-11 W.2ND AND RACE ST, MH I-18 N OF HWY 22/35 |  | GROUND SOAKED FROM THAWING | CLEAN UP WASTE AND SPREAD LIME
| JONESBORO UTILITIES | GRANT | 2010-03-28 | 10:00A - 4:00P | 375000 | I-11 to I-18 | FLASH FLOOD; CREEK | RAIN 1.6" | CLEANED MH AND LINES; WASTEWATER SENT TO GAS CITY FOR TREATMENT
IN0025585 | MARION MUNICIPAL STP | GRANT | 2010-01-23 | 8A - 6:30P | 2000 | MANHOLE 29-1754 2131 SOUTH FAIRFIELD | GROUND/STORM SEWER | PARTIAL BLOCKAGE | CLEARED BLOCKAGE AND STAFF CLEANED AREA
IN0025585 | MARION MUNICIPAL STP | GRANT | 2010-06-22 | 7:00A - 9:00A | 2000 | MH# 67-2628 | GROUND | RAIN, EMPLOYEE LEFT PUMPS IN OFF POSITION | AREA AROUND MANHOLE CLEANED
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2010-03-12 | 10:00P - 12:30A | 400 | NORTH LIFT STATION | SCHWARTZ DITCH | RAIN 1.5"
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2010-06-06 | 3:10A - 6:30A | 360 | NORTH LIFT STATION | SCHWARTZ DITCH | RAIN 2.1"
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2010-06-14 | 8:30P - 2:30P (6/15) | 720 | NORTH L.S. | SCHWARTZ DITCH | RAIN 2.5" IN SHORT AMOUNT OF TIME
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2010-06-14 | 9P - 2A (6/15) | 600 | WEST L.S. | JEFFERSON DITCH | RAIN 2.5" IN SHORT AMOUNT OF TIME
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2010-08-04 | 9:30P - 12:30P | 360 | NORTH LS | SCHWARTZ DITCH | 1.5" RAIN IN SHORT AMOUNT TIME
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2010-11-25 | 2:00A - 4:00A | 240 | NORTH LIFT STATION | SCHWARTZ DITCH | RAIN 2.3"
IN0040801 | WORTHINGTON MUNICIPAL STP | GREENE | 2010-07-18 | A - (7/30) |  | MAIN LS SSO OUTFALL #2 | OXBO WHITE RIVER | GROUND WATER INFILTRATION HEAVY RAIN POWER OUTAGE ACROSS TOWN | TOWN HAS RECEIVED GRANT TO REPAIR COLLECTION SYSTEM
IN0021334 | ARCADIA MUNICIPAL STP | HAMILTON | 2010-06-22 | 8A - 2P | 45000 | 25990 S.R. 19 MH | GROUND | 2.4" TOWN OF ARCADIA RECORDED 6.6" LAST 10 DAYS | WATER WAS PUMP OUT OF SANITARY MH TO PREVENT PROPERTY DAMAGE PUT BACK FLOW VALVE IN CUSTOMER LATERAL
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2010-06-22 | 9:15A - 6:00P | 78000 | SMOCK CREEK LS, ALLISONVILLE RD LS, HAGUE LS | WHITE RIVER, CHEENEY CREEK | RAIN 2" | ALL AFFECTED AREAS CLEANED OF DEBRIS
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2010-01-22 | ? - 1P |  | STILL WATER COVE LIFT STATION | GROUND | TRANSFORMER INSIDE CONTROL PANEL FAILED NOT ALLOWING FLOATS OR ALARM TO WORK | ROUTINE CHECKS AND ADD AN ALARM FLOAT THAT DOES NOT RELY ON 24V TRANSFORMER
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2010-01-29 | ? - 4:30P | 12000 | LIFT STATION AND MANHOLE BEHIND LOT 32 | GROUND | DISCONNECT SHORTED OUT RESULTING IN PUMPS NOT RUNNING AND ALARM NOT WORKING | LIFT STATION WORKING AGAIN, REPLACING DISCONNECT AND INSTALLING BATTERY POWERED BACK UP
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2010-03-14 | 7:00P - 7:45P | 16200 | QUIET BAY LIFT STATION | MORSE RESERVOIR | AIR LOCK IN FORCE MAIN | HAD TO PUMP LIFT STATION DOWN TO ALLOW BACK FLUSHING TO REMOVE AIR LOCK. WILL RE-BUILD CHECK VALVES
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2010-06-22 | 6:00A - 6:40A (6/23) | 750000 | SSO'S # 002, 003, 101 | MORSE RESERVOIR | RAIN 3.1" | PERSONNEL AT PLANT FOR DURATION OF BYPASS TO ENSURE MAXIMUM OPERATION
IN0022586 | CICERO MUNICIPAL STP | HAMILTON | 2010-06-22 | 6A - 6:40A (6/23) | 1500000 | MAIN ST LS & MH 369 IRA BRIDGE & HEADWORKS | MORSE RESERVOIR | PRECIPITATION 3.1" | PERSONAL AT PLANT FOR DURATION OF OVERFLOW TO ENSURE MAXIMUM OPERATION ENGINEER CURRENTLY WORKING ON I & I STUDY
IN0055760 | CLAY TOWNSHIP RWD | HAMILTON | 2010-05-28 | 5P - 9P (5/29) | 15000 | M.H. TD- 210D | STORM SEWER | GREASE BLOCKAGE | CLEANED UP AREA AND ADDED TO "TROUBLE SPOT" LIST TO BE CLEANED YEARLY
IN0055760 | CLAY TOWNSHIP RWD | HAMILTON | 2010-06-22 | 8:00A - 12:00P | 25000 | MH # SI-7 | GROUND | RAIN 3.5" | GROUND CLEANED WITH VACTOR TRUCKS
IN0055484 | FISHERS - CHEENEY CREEK STP | HAMILTON | 2010-03-09 | 9:30A - 9:35A | 11000 | 106TH & HAGUE L.S. MANHOLE | CHEENEY CREEK | BYPASSING L.S. WITH 3 6" PUMPS, INTAKES ON PUMPS CLOGGED | REMOVED PLUG IN LINE AND RESIZED PUMPS
| HAMILTON S.E. UTILITIES, INC. | HAMILTON | 2010-11-14 | 9P - 11P | 9667 | MH PRB1-211 SAND CREEK NORTH OF 126TH | GROUND | MALFUNCTION ON ALARM FLOAT | CLEAN STATION MAINTAIN WEEKLY INSPECTION OF L.S.
| HAMILTON S.E. UTILITIES, INC. | HAMILTON | 2010-11-27 | 9A - 10A | 2000 | MH HZ1-101 HORIZON SUBDIVISION | GROUND | BREAKER FAILURE IN L.S. | REPLACED BREAKER MAINTAIN BI-ANNUAL INSPECTIONS
| HAMILTON SOUTHEASTERN UTILITIES | HAMILTON | 2010-01-06 | 5:30P - 6:30P | 1200 | 8 MH'S IN SPYGLASS HILLS: 2-6, 11,14,17 | GROUND TO CURB TO INLET TO DET. POND | MALFUNCTION ON ALARM FLOAT | REPAIRED FLOAT
IN0030168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2010-01-30 | 9:00A - 2:30P |  | MH AT FM GRINDER LINE 116 WESLEY CT. | MORSE RESERVOIR | MECHANICAL COUPLER CAME LOOSE | PIPE REPLACED AND SECURED
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2010-06-22 | 9:30 - 11:10 |  | LS #1 ALLISONVILLE ROAD | WEST FORK WHITE RIVER | PRECIPITATION 3.5" CAUSED FLOW INTO LS ABOVE PEAK PUMP CAPACITY | SAMPLES TAKEN CITY ORDINANCE AGAINST SUMP PUMPS TIED INTO CITY SEWERS
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2010-06-22 | 8:45 - 15:30 |  | LS #5 WEST CHESTER BLVD | MORSE RESERVOIR | PRECIPITATION 3.5" CAUSED FLOW INTO LS ABOVE PEAK PUMP CAPACITY | SAMPLES TAKEN CITY ORDINANCE AGAINST SUMP PUMPS TIED INTO CITY SEWERS
IN0020168 | NOBLESVILLE MUNICIPAL STP | HAMILTON | 2010-06-22 | 8:30 - 9 |  | LS #8 LANDS END CIRCLE | MORSE RESERVOIR | PRECIPITATION 3.5" CAUSED FLOW INTO LS ABOVE PEAK PUMP CAPACITY | SAMPLES TAKEN CITY ORDINANCE AGAINST SUMP PUMPS TIED INTO CITY SEWERS
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2010-03-08 | 5A - 4P (3/9) | 0 | SECONDARIES | CONTACT TANK | CLEANING OF TERTIARY POND | CLEANING COMPLETE
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2010-03-31 | 3:30P - ? |  | SECONDARIES | CONTACT TANK | RAIN 2" | SHUTTING POND DOWN TO CLEAN SOLIDS
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2010-03-31 | 3:30P - 3:00P (4/2) |  | SECONDARIES | CONTACT TANK | END OF CLEANING SOLIDS OUT OF TERTIARY POND
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2010-06-22 | 8:50A - |  | INFLUENT MH | SIMON'S DITCH | RAIN 4.7"
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2010-06-22 | 8:50A - 2:30A | 600000 | INFLUENT MANHOLE | SIMON'S DITCH | RAIN 4.8"
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2010-08-30 | 6:00A - 4:30 | 800000 | SECONDARIES | CONTACT TANK | CLEANING SOLIDS OUT OF TERTIARY POND
IN0059544 | WESTFIELD MUNICIPAL STP | HAMILTON | 2010-10-28 | 1:30P - 2:30P | 11000 | LATERAL IN CRAWL SPACE | CRAWL SPACE | STICKS AND DEBRIS IN LINE | RELEASED BLOCKAGE AND ALLOWED SEWAGE TO FLOW BACK INTO DRAIN
IN0002925 | ELI LILLY AND CO., GREENFIELD | HANCOCK | 2010-07-28 | 12:21P - 12:26P | 0 | UV BUILDING BYPASS OF TREATMENT PROCESS | LEARY DITCH | NORTH UV UNIT (BACK TO THE SOUTH UV) HAS ELECTRICAL IMBALANCE CAUSING INSUFFICIENT DISINFECTION | SOUTH UV IS NOW FULLY OPERATIONAL AND CALL TO AQUIONICS TO INVESTIGATE AND FIX NORTH UV
IN0020109 | GREENFIELD MUNICIPAL STP | HANCOCK | 2010-06-21 | 9:00A - 5:00P | 700000 | HEADWORKS BUILDING | STORM SEWER. WOODED AREA | RAIN 2.7"
IN0060542 | MCCORDSVILLE WWTP | HANCOCK | 2010-12-16 | 10:00A - 3:00P | 22000 | DAMAGED VALVE ON SLUDGE PIPING | GROUND AT WWTP SITE | 6" PLUG VALVE ON SLUDGE PIPING BROKE. LIQUID SLUDGE LEAKED ONTO GROUND | SLUDGE ISOLATED AND CLEANED.
IN0059781 | CAESARS RIVERBOAT CASINO WWTP | HARRISON | 2010-09-14 | 12:30P - 3:30P | 200 | INFLUENT/GRINDER STRUCTURE AT WWTP | GROUND | HIGH RETURN SLUDGE RATE CAUSED EXCESS PRESSURE AND RETURN SLUDGE AND INFLUENT WATER SPLASHED OVER INFLUENT STRUCTURE | VACUUMING UP SLUDGE AND APPLYING LIME, WILL NOT ALLOW BOTH RETURN PUMPS TO RUN AT SAME TIME
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-03-03 | 10:45A - 11:15A | 25 | MANHOLE - LUCAS STREET | STREET | BLOCKED SEWER LINE | LIST STATION PUMPS SHUT OFF AND LINE CLEANED
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-03-10 | 10A - 10:40A | 150 | LUCAS STREET MH | STREET | PHONE UTILITY BORED THROUGH LINE CAUSING IT TO FAIL | LINE PLUGGED AND STATION OFF UNTIL LINE IS REPAIRED
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-04-12 | 11:30A - 1:15P | 50 | TWIN LIFT FORCE MAIN | GROUND | ELBOW ON FORCE MAIN CRACKED | ELBOW REPLACED, VAC TRUCK CLEANING MESS
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-06-09 | 10:10A - 10:30A | 500 | MAIN PUMPING STATION | DRIVE AREA | PRIMARY POWER AND TIE BREAKER FAILED TO AUTO CHARGE | MANUALLY RESET SYSTEM. SEWAGE PUMPED BACK INTO LIFT STATION
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-06-22 | 2:00A - 5:00A | 1000 | MH 410 ELIZABETH DR, 309 STADIUM DR | GROUND, BASEMENT BACKUP | RAIN 2" | ALL PUMPS RUNNING
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-06-24 | 11:30P - 2:00 (6/25) | 500 | MH 225 S. MARDALE, ELIZABETH LANE, JOHNSON AVE | PARKING LOT, GROUND | PUMP FAILED | VAC TRUCK CLEANED AREA, REPLACED PUMP
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-07-29 | 12:10A - 1:20A | 5000 | MAIN PUMPING STATION | GROUND AND DRIVE AREA | AUTOMATIC SLUICE GATE DID NOT LOWER PROPERLY | BACK UP SLUICE GATE PUT INTO OPERATION MANUALLY AND CALLED TO INVESTIGATE FAULTY SLUICE GATE
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2010-09-10 | 7:15P - 7:45P | 20 | 422 W. JANET DR. | BATHROOM. GROUND NEAR CLEANOUT | ROOTS IN SEWER LINE CAUSED BACK UP | LINE ON ROOT TREATMENT PROGRAM
IN0020079 | DANVILLE MUNICIPAL STP | HENDRICKS | 2010-03-15 | 7:00A - 10:30A (3/17) | 250 | MH @ 115 N JEFFERSON | GROUND | MH AT END OF GRAVITY LINE. TWO HOME LATERAL TIE IN | VAC/JET LINE
IN0020079 | DANVILLE MUNICIPAL STP | HENDRICKS | 2010-06-22 | 12:30A - 3:00A | 1500 | COUNTY HOME LIFT STATION | WEST FORK OF WHITE LICK CREEK | RAIN 3.7" | ALL PUMPS RUNNING
IN0020079 | DANVILLE MUNICIPAL STP | HENDRICKS | 2010-06-22 | ? | 250 | 402 WEST CLINTON 147 SOUTH TENNESSEE | BASEMENT | WAS NOT REPORTED UNTIL AFTER THE FACT | JET/VAC TRUCK TO CLEAN SANITARY SEWER POLICY TO SEPARATE SHARED LATERALS WAIVING ALL FEES AND ASSISTING WITH COST
IN0020079 | DANVILLE MUNICIPAL STP | HENDRICKS | 2010-07-26 |  |  | WWTP | N/A | 2 OF 5 CLARIFIERS BYPASSED FOR MAINTENANCE OF V-NOTCH WEIRS | VAC TRUCK AND PRESSURE WASHING
IN0020079 | DANVILLE MUNICIPAL STP | HENDRICKS | 2010-10-28 | 7:00P - 9:00A (10/29 | 660 | MANHOLE #377 | WEST FORK WHITE LICK CREEK | DEBRIS IN LINE | JETTED LINE, FLUSHED ST.
IN0057614 | HENDRICKS COUNTY RSD | HENDRICKS | 2010-06-19 | 4:00A - 9:00A |  | MH WEST OF MEIJER | STORM SEWER | MCC TRIPPED DUE TO POWER FAILURE | STARTED BACKUP GENERATOR; RESET EQUIPMENT
IN0057614 | HENDRICKS COUNTY RSD | HENDRICKS | 2010-06-22 | 2:00A - 4:30P |  | MH WEST OF MEIJER | STORM SEWER | RAIN 3.34" | USED DIESEL PUMP TO MAXIMIZE FLOW TO PLANT
| MARSH | HENDRICKS | 2010-11-15 | 4P - 8A (11/16) | 200 | MARSH PLAZA L.S. | GROUND | EQUIPMENT FAILURE | GORDON PLUMBING MADE REPAIRS AND CLEANED UP AREA
| MARSH SUPERMARKET | HENDRICKS | 2010-09-09 | 10:00A - 1:00P | 9000 | MH NORTH OF MARSH LIFT STATION | GROUND AND CLARKS CREEK | GREASE | UNCLOGGED SEWER AND CLEANED AREA
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2010-01-07 | 9:30A - 10:45 |  | MH AT CORNER OF SCAMAHORN & OSBORN | GROUND | LS PRESSURE SWITCH MALFUNCTION | INSTALLING NEW LIFT STATION. AREA AROUND MH BEING CLEANED AND LIMED
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2010-02-22 | UNKNOWN |  | WWTP SOLIDS FROM CLARIFIER PARTIALLY TREATED | WEST FORK WHITE LICK CREEK | RAIN .58 INCHES AND SNOW MELT | WATCH WEATHER AND MONITOR PLANT CLOSELY AND MAKE CHANGES TO STOP GATES AS NEEDED
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2010-06-19 | 4:00A - 2:00P |  | MH AT MAIN LIFT; CLARIFIERS AT WWTP | WHITE LICK CREEK | RAIN 2.3" | ALL SOLIDS PICKED UP, LIME
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2010-06-21 | 2A - 12:45P (6/22) |  | 2 MH BEHIND SCHOOL | GROUND GRASSY SWALE | HEAVY RAINS 4.5" IN SHORT TIME WIDESPREAD FLOODING | AREAS AROUND MH WILL BE CLEANED SOLIDS RAKED UP TOWN INVESTIGATING I & I AND LINING OLD LINES HOPE TO CAMERA AND SMOKE TEST LINES
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2010-11-29 | ? - ONGOING |  | WWTP CLARIFIERS | WEST FORK WHITE LICK CREEK | UNKNOWN CHEMICAL IN INFLUENT CAUSING FOAM | PARTIALLY TREATED WASTE IS BLENDED WITH EFFLUENT AND SAMPLED
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2010-12-12 | ? - 4 |  | BRIXTON SUBDIVISION | STORM POND DRAINS TO UNNAMED TRIB OF WHITE LICK | 8" FORCE MAIN BREAK | LS SHUTDOWN TWO PUMPERS TRUCKS HAULED WHILE BREAK WAS REPAIRED
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-01-02 | 5:30P - 7:30P | 200 | MANHOLE 1816 HEMLOCK LANE | STREET STORM INLET | BACK UP IN SEWER MAIN | JETTED SEWER LIMED GRASSY AREA AND ROUTINE MAINTENANCE CLEANING
IN0062456 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-04-12 | 2:30P- 5:30P | 100 | MH 1251 QUAKER BLVD | GRASS AND SIDEWALK | PIPE PLUG LEFT IN SEWER LINE | REMOVED PLUG AND JETTED CLEAN, SPREAD LIME ON GROUND
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-04-26 | ? - 2P(5/3) | 42000 | STORM DRAIN OUTLET AT FRANKLIN PARK | STORM SEWER TO WHITE LICK CREEK | SEWER BACKUP | UNCLOGGED SEWER AND TELEVISE REPAIRS WILL BE MADE IF NEEDED
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-05-03 | 3:30 - 2:30 (5/4) | 10000 | 1145 RAYMOND STREET | CRAWLSPACE | CLEANOUT IN CRAWL SPACE FAILED AND MAIN WAS CLOGGED | UNCLOGGED SEWER AND REPAIR PIPE JOINT THAT HAS SEPARATED
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-06-22 | 5:00A - 12:30P | 19000 | DEERFIELD PARK LS, SWINFORD PARK MH | GROUND, STORM SEWER | RAIN 2.7" | CLEANED OVERFLOW AREAS WITH VAC TRUCK
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-08-03 | ? - 15:00 | 30000 | STANLEY ROAD AND SR 267 FORCE MAIN | GROUND | FORCE MAIN SEPARATED | COLLECTION BASIN CONSTRUCTED UTILITIES BEING LOCATED AND PIPE WILL BE REPAIRED AND OBSERVED
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-09-01 | 2:30P - 3:30P | 4440 | FORCE MAIN | GROUND | FORCE MAIN DAMAGED BY BORING MACHINE | AREA LIMED; FORCE MAIN DIVERTED TO SECOND FORCE MAIN
IN0021202 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-09-22 | 9:30A - 10:00A | 4800 | FORCE MAIN AT CENTER ST. AND ENTRANCE TO CRYSTAL BAY CONDOS | GROUND | FORCE MAIN DAMAGED BY BORING MACHINE | CLEANED UP SPILL AREA AND WILL REPAIR FORCE MAIN
IN0062456 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2010-10-30 | 4P - 10A (10/31) | 200 | MAIN STREET AND MILL STREET | BASEMENT STORM SEWER | CLOG IN SEWER LINE | FIX CLOG
IN0062456 | PLAINFIELD SOUTH WWTP | HENDRICKS | 2010-05-25 | 10:00A - 11:00A | 100 | MH AT PAMELA CT. | STORM SEWER | GRAVEL IN LINE FROM CONSTRUCTION, GREASE, RAGS | LINE CLEANED TO REMOVE BLOCKAGE
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2010-03-07 | 3:30P - 7:30P | 50 | 8723 REDDITCH DRIVE MANHOLE | GROUND | BLOCKAGE | CREW CLEARED BLOCKAGE AND CONTINUED TO JET-ROD SANITARY SEWERS, TELEVISED LINES
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2010-03-11 | 2:30P - 2:45P | 150 | AVON COMMERCE PARK L.S. | GROUND | FAULTY AIR RELEASE VALVE ON FORCE MAIN | SHUT VALVE ON AIR RELEASE AND MADE REPAIR, DO BETTER JOB ON INSPECTION
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2010-04-27 | 6:00P - 6:30P | 15 | 4466 LONDONDERRY CT | GROUND | AIR RELEASE VALVE ON FORCE MAIN WENT BAD. | CLEANED SPILL AND LIME AREA, REPLACED VALVE
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2010-06-22 | 6:00A - 6:30A | 5000 | 625 EAST AND US 36, MH, LINGERMAN LS | GROUND | RAIN 4.5" LS LOST POWER | USED GENERATOR FOR BACK UP POWER SUPPLY
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2010-12-04 | 6:00P - 6:10P |  | WOOD CREEK FARMS HOUSING ADDITION | GROUND | RAIN .18" BROKEN FORCE MAIN | REPAIRED FORCE MAIN AND LIMED AREA
IN0043966 | GAS AMERICA SERVICES | HENRY | 2010-06-22 | 10A - 8P | 86000 | POLISHING TANK TO OUTFALL 001 | MONTGOMERY CREEK | 3.5" RAIN IN 4.5 HOURS ON SATURATED GROUNDS | PLANT BLOWERS SHUT DOWN TO ALLOW SOLIDS TO SETTLE
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2010-03-12 | 6:00P - 5:30P (3/16) | 21410000 | 003 | BLUE RIVER | RAIN 1.74"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2010-06-13 | 9P - 11P | 1980000 | 003 | BIG BLUE RIVER | .66" RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2010-06-21 | 10:00A - 1:00P | 1980000 | 003 | BIG BLUE RIVER | RAIN
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2010-06-22 | 4:00A - 1:00P | 15860000 | 003 | BLUE RIVER | RAIN 1.61"
IN0023914 | NEW CASTLE MUNICIPAL STP | HENRY | 2010-11-30 | 12:45A - 4A | 90000 | 003 | BIG BLUE RIVER | PRECIPITATION .41"
IN0055131 | SOUTH HENRY REGIONAL SEWER DIS | HENRY | 2010-06-22 | 10:15A - 10:50A | 500 | MH 13 - 56 | GROUND | RAIN 2.5" | WILL REPLACE BOLT ON MH
IN0055131 | SOUTH HENRY REGIONAL SEWER DIS | HENRY | 2010-06-22 | 10:15
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-01-23 | 14:30 - 16:10 (1/25) |  | MANHOLE 200' UPSTREAM | WILDCAT CREEK | SNOW MELT AND GROUND THAW | NEW PLANT UNDER CONSTRUCTION
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-03-13 | 12:30A - 12:30P |  | MH 200' UPSTREAM | WILDCAT CREEK | RAIN
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-03-13 |  |  | MANHOLE 200' UPSTREAM | WILDCAT CREEK | HEAVY RAIN | NEW PLANT UNDER CONSTRUCTION
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-03-28 | 10:30A - 1:10P (3/31) |  | MH 200' UPSTREAM | WILDCAT CREEK | RAIN | NEW PLANT UNDER CONSTRUCTION
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-05-04 | 10:30 - 13:40 |  | MANHOLE 200' UPSTREAM | WILDCAT CREEK | TRANSFORMER BLOWN LOSS POWER DUKE NOTIFIED | PORTABLE GENERATOR BROUGHT TO SITE NEW PLANT UNDER CONSTRUCTION
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-05-11 | ?- 12:40P |  | MH 200' UPSTREAM | WILDCAT CREEK | RAIN | FLUSHED PUMP AND PUT BACK UP PUMP ON LINE
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-05-31 | 20:10 - 13:00 (6/1) |  | M.H. 200' UPSTREAM | WILDCAT CREEK | HEAVY LOCAL RAINFALL | NEW PLANT UNDER CONSTRUCTION
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-06-14 | 9:30A - 1:00P (6/18) |  | MH 200" UPSTREAM | WILDCAT CREEK | RAIN
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-06-14 | 09:30 - |  | MH 200' UPSTREAM | WILDCAT CREEK | LOCAL HEAVY RAINFALL | NEW PLANT UNDER CONSTRUCTION
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-06-22 |  |  | MH 200' UPSTREAM | WILDCAT CREEK | RAIN | PLANT SET UP TO TAKE MENTIONED FLOW UNTIL RAIN SUBSIDES
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-06-22 | 0 - 12:10 (6/25) |  | MH 200' UPSTREAM | WILDCAT CREEK | HEAVY LOCALIZED RAINS | PLANT SET-UP TO TAKE MENTIONED FLOW UNTIL RAIN/INFILTRATION SUBSIDES
IN0038768 | GREEN ACRES GOLF COURSE & SUBD | HOWARD | 2010-12-27 | 12:30 - 12:50 |  | MH 200' UPSTREAM | WILDCAT CREEK | DEBRIS IN PUMP | NEW PLANT UNDER CONSTRUCTION
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-03-09 | 3P - 3:40P | 30000 | WASTE HOLDING TANK | GROUND STORM SEWER WILDCAT CREEK | VALVE FOR THE FLOW OF WASTE ACTIVATED SLUDGE FROM AERATION BASIN DID NOT CLOSE | VALVES WILL BE MORE CLOSELY MONITORED, DECANT VALVES WILL BE LOWERED TO ALLOW OVER FLOW TO RUN INTO HEADWORKS
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-03-12 | 11:45P - 6:15A (3/13) | 200000 | OUTFALL 002 | BRUNK DITCH | RAIN 1.3" | WORKING TO FIND AND REPAIR SOURCES OF INFILTRATION IN PRIVATE SECTOR
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-03-13 | 2:15P - 3:10A (3/14) | 500000 | OUTFALL 002 | BRUNK DITCH | RAIN .6" | WORKING TO FIND AND REPAIR SOURCES OF INFILTRATION IN PRIVATE SECTOR
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-03-28 | 11:10A - 8:20P | 500000 | OUTFALL 2 | BRUNK DITCH | RAIN 1.18" | LOOKING FOR SOURCES OF I & I
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-05-21 | 1:00P - 9:00A (5/23) |  | SURGE TANK | POLISHING PONDS | RAIN .65" | PLANNED RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-06 | 6:30A - 6:30A (6/7) |  | SURGE TANK | POLISHING PONDS | RAIN 2"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-06 | 3:20A - 10:10A | 100000 | OUTFALL 002 | BRUNK DITCH | RAIN 2"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-09 | 10:00A - 7:00A (6/10) |  | SURGE TANK | POLISHING PONDS | RAIN .73"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-14 | 8:30P - 4:05A (6/15) | 50000 | OUTFALL 2 | BRUNK DITCH | PRECIPITATION .9" | REHAB OF COLLECTION SYSTEM AND PLANNED RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-15 | 7A - 7A (6/17) |  | SURGE TANK | POLISHING PONDS | PRECIPITATION 1.2" | REHAB OF COLLECTION SYSTEM AND RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-21 | 8:18A |  | SURGE TANK | POLISHING PONDS | RAIN 1.8"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-21 | 8:45A - 8:45P | 480000 | 002 | BRUNK DITCH | RAIN 1.8"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-22 | 2:45A |  | 002 | BRUNK DITCH | RAIN 3"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2010-06-22 | 2:45A - 3:50P | 800000 | 002 | BRUNK DITCH | PRECIPITATION 3"
| GREENTOWN MUNICIPAL STP | HOWARD | 2010-10-21 | 1:30P - 2:00P | 15000 | WASTE HOLDING TANK | GROUND, STORM SEWER | DIGESTER OVERFLOWED BECAUSE OF FAULTY VALVE | SPILLED MATERIAL BEING DILUTED AS MUCH AS POSSIBLE
IN0061310 | BIPPUS REGIONAL SEWER DISTRICT | HUNTINGTON | 2010-05-22 | 6:00P | 1000 | EFFLUENT LIFT STATION BEHIND TREATMENT PLANT | GROUND | RAIN 3" | APPLIED LIME TO AREA
IN0060674 | LAKE AND FOREST CLUB | JACKSON | 2010-11-30 | 9:00A - 1:00P | 2400 | TRASH TRAP | GROUND | PIPES FROM TRASH TRAP TO AERATION TANK PARTIALLY BLOCKED | PIPES JETTED CLEAN
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2010-03-19 | 12:00P - 12:20P | 500 | MANHOLE G07-W060 | STORM SEWER | DRIVES ON PUMPS OVERHEATED AND KICKED OUT SYSTEM DID NOT ALARM STATION WAS HIGH | RESTARTED DRIVES AND RESET SCADA TO ASSURE CALLOUTS WILL CHECK SYSTEM DAILY
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2010-06-28 | 12P - 12:20P | 50 | MH #E09-W009 | STORM SEWER | 3" + RAIN CAUSE LINE TO SURGE | USED VAC TRUCK TO SUCK DOWN MH LOOKING AT SLIP LINING TO DO AWAY WITH I & I
IN0053201 | NIPSCO, ROLLIN M. SCHAFER STA | JASPER | 2010-10-05 | 7:30A - 2:30P |  | LOCKER ROOM SANITARY FLOOR DRAINS | LOCKER ROOM AND HALLWAY | ROOT APPEARS TO BE BLOCKING DRAIN LINES | CONTAINMENT BOOM UTILIZED MAINTENANCE CREW BEGAN TRACING LINES AND CONTRACTOR CAME IN AND CLEANED AND SANITIZED
IN0053201 | NIPSCO, ROLLIN M. SCHAHFER STA | JASPER | 2010-12-15 | ? - ? |  | 2723 E 1500 N POND OVERFLOW TO 2 SURFACE WATER DRAINS | GROUND AND DAVIS DITCH | SUSTAINED FLOW FROM OVERFLOW CULVERTS FLOODING VEGETATED AREA 100-150 GPM | INVESTIGATION IS UNDER WAY
IN0024414 | RENSSELAER MUNICIPAL STP | JASPER | 2010-11-16 | 07:00 - 10 | 65000 | CSO #19 | IROQUOIS RIVER | EQUIPMENT FAILURE CUTTING KNIFE ON COMMINUTOR BROKE AND STOPPED UNIT | DIVERT FLOW AROUND COMMINUTOR TO REPAIR IT
IN0039101 | WATER SERVICE CO OF INDIANA | JASPER | 2010-06-27 | 8:30 - 14:30 | 50 | MH LOT 642 | GROUND | SEWER MAIN PARTIALLY PLUGGED | JETTED AND CLEANED OUT SEWER MAIN SPREAD LIME ON AFFECTED AREA
IN0039101 | WATER SERVICE CO OF INDIANA | JASPER | 2010-08-08 | 4:30 - 8 |  | COUNTY LINE ROAD MH | GROUND | SEWER MAIN PLUGGED | CONTINUE SEWER CLEANING AND MAINTENANCE PUT LIME DOWN
| PORTLAND MUNICIPAL STP | JAY | 2010-09-17 | 12:30P - 5:30P |  | INDUSTRIAL PARK LIFT STATION, CSO'S 15 AND 16 | SIPE DITCH | LIFT STATION CONTROLLER FAILED | VACUUMED AREA, STATION RUN ON MANUAL UNTIL REPAIRED
IN0060437 | SALAMONIA WWTP | JAY | 2010-09-22 | 12:00P |  | WWTP OUTFALL #1 | LITTLE SALAMONIA | LIGHT RAIN. NEED TO DISCHARGE TO KEEP LAGOONS FROM OVERFLOWING
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JEFFERSON | 2010-06-17 | ? - 5:00P | 100000 | LOT 1784; 8 INCH SEWER FORCE MAIN; JOINT LEAK | COUNTRY SQUIRE LAKE | 8 INCH SEWER FORCE MAIN; JOINT LEAK | SHUT DOWN ALL STATIONS SERVICED BY FORCE MAIN AND INSTALLED BYPASS PIPE
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-01-21 | 7:30P - 8:00P | 2000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | LTCP | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-01-24 | 11:30P - 6:10A (1/25) | 54000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAIN .82 INCHES | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-02-05 | 4P - 8:15P | 18000 | SECONDARY TREATMENT DIVERSION | OHIO RIVER | HEAVY RAIN .94" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-03-12 | 4:15P - 7:00P | 900 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN .47" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-03-25 | 6:15P - 9:30A (3/26) | 160000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAIN FALL 1.14" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-03-26 | 10:00A - 11:45A | 8000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN .04" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-03-28 | 8:00P - 1:00A (3/29) | 74000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN .24" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-04-08 | 6A - 1:15P | 13000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAINFALL 1.03" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-04-24 | 8:30A - 9:00A |  | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN .66" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-04-24 | 8:30A - 9A | 1350 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAIN .66" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-04-26 | 7:00P - 9:15P | 500 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | BROKEN LINE BESIDE EAST DIGESTER | CONTAINED SPILL, REPAIRING SLUDGE LINE
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-05-02 | 11A - 7:30P | 90000 | WELLS DR L.S. | DEAN BRANCH CREEK | HEAVY RAINFALL 3.62" | DIP OUT ALL DEBRIS AND HAULED OFFSITE BEFORE OVERFLOW LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-05-02 | 10A - 6:30P | 90000 | SEVERAL M.H. IN CITY | GROUND | HEAVY RAINFALL 3.62" | TRIED TO MAINTAIN M.H. LIDS TO PREVENT VEHICLE DAMAGE LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-05-02 | 6:30A - 6:30 (5/3) | 55000 | SECONDARY TREATMENT DIVERSION | BLENDED WITH EFFLUENT TO OHIO RIVER | HEAVY RAINFALL 3.62" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-05-12 | 11:30A - 1:30P | 15000 | WELLS DR LS | DEANS BRANCH CREEK | RAIN 1.9" | HAULED ALL DEBRIS OFFSITE BEFORE OVERFLOW
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-05-12 | 8:30A - 7:30P | 16000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN 1.9"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-05-12 | 10:30A - 1:30P | 10000 | SEVERAL MANHOLES | GROUND | RAIN 1.9"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-05-22 | 10:00P - 11:00P | 960 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN .79"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-09 | 6:45A - 2:30P | 294000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN 1.69" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-09 | 9:30A - 10:15A | 7000 | WELLS DR LS | DEANS BRANCH CREEK | RAIN 1.69" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-09 | 9:00A - 10:30A | 6000 | SEVERAL MHS IN CITY | GROUND | RAIN 1.69" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-13 | 11:40P - 12P (6/14) | 4000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAINFALL 1.3" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-14 | 12P - 4P | 400 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAINFALL IN SHORT TIME .47" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-15 | 9:30P - 1A (6/16) | 12920 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAIN SHORT AMOUNT OF TIME .39" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-19 | 7:00A - 2:00P | 150000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN 1.18" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-21 | 1:00P - 7:00P | 120000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN 1.54" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-21 | 2:30P - 3:30P | 8000 | WELLS DR. LIFT STATION | DEANS BRANCH CREEK | RAIN 2.1" | CLEANED UP AREA AROUND WET WELL
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-28 | 3A - 4:30 | 15000 | WELLS DRIVE LS | OHIO RIVER | HEAVY RAINFALL 1.7" | CLEANED DEBRIS FROM WET WELL
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-06-28 | 12A - 12:15P | 90000 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | HEAVY RAINFALL 1.7" | NONE LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-07-22 | 7:45P - 9P | 620 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RUNNING ONE CLARIFIER DUE TO CONSTRUCTION AND RAIN .24" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-08-13 | 5:45P - 7:30P | 12900 | SECONDARY TREATMENT DIVERSIONS | OHIO RIVER | RAIN 1.5"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-11-17 | 5:30P - 6:30P | 1500 | MH 1440 CRAIGMONT STREET | DITCH TO CROOKED CREEK | LINE OBSTRUCTED BY RAGS | LINE WAS JETTED CLEAN AND ADDED LINE TO PROBLEM AREA FOR WEEKLY CHECKS
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-11-22 | 9:00A - 10:00A | 1500 | MH | GROUND/CROOKED CREEK | BLOCKAGE OF CONSTRUCTION MATERIAL AND ROOTS | DUG UP AND REPLACED 20' OF SEWER LINE
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-11-29 | 10:30P - 2:15P (11/30) |  | SECONDARY TREATMENT DIVERSION | OHIO RIVER | HEAVY RAIN 1.84" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2010-12-30 | 8:45A - 2:30P | 73000 | SECONDARY TREATMENT DIVERSION | OHIO RIVER | .4" RAIN AND MELTING SNOW | LTCP
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-01-17 | ? - 4:00P | 420 | LOT 1417; CLEANOUT | GROUND | 3 INCH SEWER MAIN PLUGGED WITH DEBRIS | SNAKED SEWER, CLEANED DEBRIS AND LIMED AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-01-17 | ? - 3:00P | 420 | LOT 1839 AND 1872 | GROUND | STATION #2 HAD LOW VACUUM WHICH CAUSED SEWAGE TO BACK UP AND OVERFLOW THROUGH AIR INTAKE | REPAIRED LEAK, CLEANED DEBRIS AND LIMED AREA, CSERP TO BE IMPLEMENTED TO CORRECT SSO'S.
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-01-25 | 9:30A | 630 | LOT NO. 3924 CLEANOUT | GROUND | 4 INCH MAIN PLUGGED WITH DEBRIS | SNAKE SEWER LINE CLEANED UP DEBRIS AND PUT LIME ON AREA CSERPTO CORRECT SSOS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-02-16 | 11:30A - 12:01P | 10 | LOT 3925; CLEAN OUT | GROUND | DEBRIS IN GRAVITY LINE | SNAKED SEWER LINE AND PUT LIME ON AFFECTED AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-03-27 | 11:30A - 12:00P | 5 | LOT 3637; CLEAN OUT | GROUND | INOPERABLE VACUUM VALVE | CHANGED CONTROLLER ON VALVE, CLEANED AND LIMED AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-04-06 | 2P - 2:30P | 750 | LOT NO. 1972 FORCE MAIN | GROUND DRY LAKE BED | CONTRACTOR HIT FORCE MAIN WHILE DIGGING | CLOSED VALVES REPAIRED BROKEN PIPE CLEANED UP DEBRIS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-04-08 | ? - 2P | 105 | CLEAN OUTS AND AIR INTAKES | GROUND | RAIN STORM CAUSE MULTIPLE VACUUM FAILURES | CHANGED CONTROLLERS 2010 CONSTRUCTION OF NEW VACUUM SEWERS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-04-14 | 11A - 11:15P | 1500 | VACUUM STATION 1 FORCE MAIN | GROUND | CONTRACTOR HIT FORCE MAIN WHEN DIGGING TO INSTALL NEW SEWER SYSTEM | CLOSED VALVE TO ISOLATE BRAKE REPAIRED PIPE CLEANED UP DEBRIS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-05-17 | ? - 8:30P (5/18) | 210 | LOT NO. 315 | GROUND | VACUUM VALVE FAILED TO OPEN PROPERLY CAUSING SEWAGE TO BACKUP AND OVERFLOW AIR INTAKE | CHANGED CONTROLLER ON VACUUM VALVE, CLEANED UP DEBRIS, SPREAD LIME, AND 2010 CONSTRUCTION OF NEW VACUUM SEWERS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-05-17 | 3:40P - 3:45P | 30 | LOT NO. 447 FORCE MAIN | GROUND | CONTRACTOR INSTALLING NEW SEWER SYSTEM HIT FORCE MAIN CREATING A HOLE | REPAIR CLAMP WAS QUICKLY INSTALLED PIPE WAS NOT LOCATED BECAUSE IT DID NOT APPEAR ON SEWER SYSTEM DRAWINGS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-05-20 | 12P - 2:10P | 20 | LOT NO. 2638 AIR INTAKE | GROUND | VACUUM VALVE FAILED TO OPEN PROPERLY CAUSING SEWAGE BACK UP | CHANGED CONTROLLER ON VACUUM VALVE, CLEANED UP DEBRIS, SPREAD LIME, AND 2010 CONSTRUCTION OF NEW VACUUM SEWERS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-02 | 11A - 11:45A | 10 | LOT #3265 CLEAN OUT | GROUND | WASTE DEBRIS BLOCKED 3" GRAVITY LINE | SNAKED SEWER CLEARED BLOCKAGE CLEANED UP DEBRIS AND PUT LIME DOWN 2010 CONSTRUCTION OF NEW VACUUM SEWERS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-05 | (6/7) | 420 | LOT NO. 285; AIR INTAKE | GROUND | VACUUM VALVE FAILED TO OPEN PROPERLY CAUSING SEWAGE TO OVERFLOW THROUGH AIR INTAKE | EMPTIED VACUUM PIT INTO TRAILER MOUNTED TANK; FIXED VALVE, CLEANED SOLIDS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-08 | 11:00A - 11:30A | 15 | LOT NO. 2638 AIR INTAKE | GROUND | VACUUM VALVE FAILED | CLEANED UP AREA; UNKINKED SENSOR LINE
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-10 | 9:30P - 10P | 5 | LOT NO. 713 AIR INTAKE | GROUND | VACUUM VALVE FAILED TO OPEN | CHANGED CONTROLLER ON VACUUM VALVE, CLEANED UP WASTE DEBRIS AND SPREAD LIME ON AFFECTED AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-10 | 11:00A - 12:00P | 20 | LOT NO. 3267; AIR INTAKE | GROUND | WASTE DEBRIS BLOCKED 3 INCH GRAVITY LINE | CLEARED BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-22 | ? - 8:10A (6/27) | 15000 | MH LOT NO. 736 | GROUND | BLOCKAGE CAUSED BACKUP | REMOVED BLOCKAGE CLEANED UP WASTE DEBRIS WILL CONTINUE TO MONITOR THIS AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-24 | ? - 10:30A | 210 | LOT NO. 1622 | GROUND | VACUUM VALVE FAILED TO OPEN PROPERLY SEWAGE BACKED UP AND OUT THE AIR INTAKE LINE | CHANGED CONTROLLER ON VALVE CLEANED UP SPREAD LIME AND 2010 CONSTRUCTION OF NEW VACUUM SEWER
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-06-24 | ? - 3P | 1050 | LOT NO. 3316 | GROUND | 3 INCH SEWER LINE CAME APART & CAUSED A BLOCKAGE | DUG UP & REPAIRED LINE SPREAD LIME 2010 CONSTRUCTION OF NEW VACUUM SEWERS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-07-07 | ? - 5:30P | 420 | LOT NO. 285 AIR INTAKE | GROUND | VACUUM VALVE FAILED TO OPEN PROPERLY | ADJUSTED CONTROLLER ON VACUUM VALVE AND CLEANED UP WASTE 2010 CONSTRUCTION NEW VACUUM SEWERS
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-08-06 | ? - 3:P (8/9) | 420 | AIR INTAKES LOT No. 1932, 1935, 1942 | GROUND | CONTRACTOR DIRECTIONAL-DRILLED PARALLEL AND THRU A 3" VACUUM SEWER LINE | REPAIRED DAMAGE LINE (600' - 800') CLEANED UP WASTE
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-08-17 | ? - 1:30P | 7350 | LOTS 233 | GROUND | LEAKING FORCE MAIN | REPAIRED EQUIPMENT AND CLEANED DEBRIS FROM AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-08-25 | ? - 10:00A | 473 | LOT 2778, 3900 CLEAN OUT | GROUND | VACUUM STATION 4 LOST VACUUM PRESSURE | REPAIRED EQUIPMENT AND CLEANED DEBRIS FROM AREA
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-10-21 | ? - 4:00A | 630 | LOT NO. 3267 | GROUND | GRAVITY SEWER BLOCKAGE | SNAKED GRAVITY SEWER, CLEANED DEBRIS, SPREAD LIME
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-12-14 | ? - 4:30P | 630 | LOT NO. 1577 CLEAN OUT | GROUND | GRAVITY SEWAGE BLOCKAGE | SNAKED GRAVITY SEWER REMOVED BLOCKAGE CLEANED UP DEBRIS 2010 CONSTRUCTION
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-12-22 | ? - 4:00P | 210 | LOT 3072; CLEAN OUT | GROUND | VACUUM VALVE SURGE TANK FAILURE | CLEANED DEBRIS, LIMED AREA, REPLACED SURGE TANK
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-12-23 | ? - 2:30P | 630 | LOT NO. 1845 CLEAN OUT | GROUND | GRAVITY SEWER BLOCKAGE | REMOVED BLOCKAGE CLEANED UP WASTE DEBRIS APPLIED LIME
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2010-12-24 | ? - 9A | 1260 | STATION 1 AIR INTAKE | GROUND | PUMPS OFFLINE DUE TO HIGH LEVEL ALARM | PUMPS BACK INTO SERVICE CLEANED UP WASTE AND LIMED AREA 2010 NEW CONSTRUCTION
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-01-07 | 8:30A - 11:00A | 500 | SUMMIT ST LS | DRAINAGE SWALE | DISCHARGE FLANGE ON LS BROKE | PUMPED LS WITH SEPTIC TRUCK AND REPAIRED FLANGE
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-03-31 |  |  | LIFT STATION OWNED BY PIZZA HUT | PARKING LOT TO DRAINAGE DITCH | TWO BAD FLOATS | REPLACED FLOATS
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-05-12 | 10:50A - 12:30P |  | QUAKERS HILLS SOUTHWEST LS | DRAINAGE SWALE | RAIN 1.67"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-05-12 | 10:50A - 12:00P |  | 5TH ST NORTHEAST LS | DRAINAGE SWALE TO MUSCATATUCK RIVER | RAIN 1.67"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-06-02 | 7:30P - 7A (6/3) |  | SUMMIT STREET LIFT STATION | UNNAMED DRAINAGE SWALE | LIGHTING STORM KICKED BREAKER | RESET BREAKER REPAIR ONE PUMP AND ORDERED TWO NEW DISCHARGE FLANGES
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-06-27 | 11:30P - 1A (6/28) |  | SOUTHWEST LS | UNNAMED DRAINAGE SWALE | HIGH FLOW EVENT RAIN 2.0"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-09-02 |  |  | MH #L1A | GROUND | BLOCKAGE IN PIPING | JETTED LINE AND APPLIED LIME
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2010-11-13 | 10:51A - 11:59A |  | MH AD12D | UNNAMED DRAINAGE SWALE | SEWER BLOCKAGE IN LINE | REMOVED BLOCKAGE WILL TV LINE NEXT WEEK
| PIZZA HUT | JENNINGS | 2010-04-01 | (4/5) |  | LIFT STATION | GROUND | MECHANICAL AND CONTROL ISSUES | HAD TANK PUMPED DAILY TO REMOVE WASTEWATER UNTIL ISSUES WERE RESOLVED
IN0022314 | BARGERSVILLE MUNICIPAL STP | JOHNSON | 2010-06-12 | 9:15P - 9:30P |  | SHORT STREET | STORM DRAIN | HEAVY DOWN POUR 1.25" | LOWERED STORM PUMP LEVEL PROCESS PUMPS RUNNING AT FULL CAPACITY UTILITIES INSTALLED A SEPARATE BY-PASSING LINE TO DIVERT FLOW FROM MAIN L.S. TO 18" LINE GOING TO HEADWORKS RESEARCHING A 6" TRASH PUMP
INP000212 | CASTINGS TECHNOLOGIES | JOHNSON | 2010-08-24 | 9P - 8:30A (8/25) | 2400 | 1450 MUSIC LAND DRIVE | FRANKLIN POTW |  | DISCHARGED IMMEDIATELY HALTED EVALUATE WHAT CAUSED THE INTERFERENCE
| GREENWOOD, CITY OF | JOHNSON | 2010-11-05 | 12:25P - 3:30P |  | 1390 SUNBURY CT RUPTURED FORCE MAIN | GROUND | FORCE MAIN RUPTURE | FLOW DIVERTED TO OTHER FORCE MAIN, SPILL CLEANED
IN0020966 | NEW WHITELAND MUNICIPAL STP | JOHNSON | 2010-04-10 | 1:30P - 2:10 | 100 | 206 SOUTHLANE | YARD | LINE STOPPED UP | CLEANED WITH JETTER, FLUSHED AREA
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2010-03-15 | ? - 7:20A | 960000 | CLARIFIER AND EFFLUENT AT PLANT | BREWER DITCH | RAIN .83" | WILL PUMP OUT HOLDING TANKS; ENGINEERS LOOKING FOR SOLUTIONS
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2010-04-17 | 4P - 7:50P |  | 2672 500 NORTH EAST RD L.S. | GROUND | POWER FAILURE | GOT POWER UP AND L.S. RUNNING SPRAYED AREA DOWN WITH WATER
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2010-06-19 | ? - 10:00A |  | LOST SOLIDS FROM CLARIFIER | BREWER DITCH | RAIN 1.96"
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2010-06-22 | 7:15A - 7:30A |  | SOLIDS FROM CLARIFIERS | BREWER DITCH | RAIN 2"
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2010-03-25 | 10:05A - 5P | 25000 | LIFT STATION #1 | GROUND | PUMP FAILED AND PRECIPITATION 1" | NEW PUMP INSTALLED, DAMAGED TAKEN OFFLINE, AND CLOGGED PUMP CLEANED PRICING VAC TRUCK AND LS CLEANING
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2010-05-16 | ? - 9A (5/17) | 20000 | DIGESTER #4 | GROUND | DURING SHUTDOWN OF DEWATERING PROCESS VALVE WAS OVERLOOKED ASSUMING CHECK VALVES WOULD HOLD THEY DID NOT | OPERATIONAL AND DIGESTER OPERATIONAL PLAN WERE MODIFIED TO ENSURE CLOSING OF ALL ASSOCIATED VALVES AND LIMED AREA
IN0053783 | MEADOWS ACRES MOBILE HOME PARK | KOSCIUSKO | 2010-06-01 |  | 500 | LOT 17 | GROUND | CONSTRUCTION RELATED | ROOTS CUT OUT AND REPLACED CAP
IN0053783 | MEADOWS ACRES MOBILE HOME PARK | KOSCIUSKO | 2010-08-16 | 5:30P 6:45P |  | LOT 26 | GROUND | PLUG IN LINE | REMOVED PLUG AND CLEANED AREA
IN0036412 | MILLWOOD ACRES | KOSCIUSKO | 2010-02-03 |  | 16000 | RAW LIFT STATION | GROUND | RAW PUMP QUIT WORKING AROUND 7PM WAS NOT DISCOVERED UNTIL SATURDAY 9:30 | WILL BE CHECKED DAILY BY PARK MANAGER UNTIL WARNING LIGHT IS INSTALLED
IN0040444 | NORTH WEBSTER MUNICIPAL STP | KOSCIUSKO | 2010-02-22 | 9:30P - 11P | 500 | LIFT STATION #10 | GROUND | AIRLINES CONNECTED TO FLOAT SWITCHES BECOME PLUGGED AND NOT PUMPED | L.S. RAN MANUALLY THEN CLEARED AIR LINES IN FUTURE REPLACE OR CLEAN LINES AS NECESSARY
| SYRACUSE MUNICIPAL STP | KOSCIUSKO | 2010-12-21 | 12:00P - 12:05P | 300 | LIFT STATION |  | LS OVERFLOWED DURING BACKWASHING OF FILTERS | GATE ADJUSTED AT TANK TO REDUCE FLOW TO LS
IN0045802 | TURKEY CREEK REGIONAL SEWER DI | KOSCIUSKO | 2010-03-17 | 9:15A | 500 | PIXIE PARKWAY TRAILER PARK | GROUND | SEWER LATERAL BROKE AT CONNECTION POINT | SEWER LINE REPAIRED AT CONNECTION, LIME OUT DOWN
IN0024805 | WARSAW MUNICIPAL STP | KOSCIUSKO | 2010-09-07 | 10:15A - 11A | 3000 | FISHER AVE & BOYDSTON STREET | STORM BASIN TO WALNUT CREEK | SEWER LINE BLOCKED | CLEARED BLOCKAGE CLEANED ROAD AND STORM BASIN WITH VAC TRUCK WILL MONITOR LINE
IN0060917 | WARSAW WWTP # 2 | KOSCIUSKO | 2010-07-19 | 11:15 | 30 | 115 TAFT STREET | BASEMENT | WHILE JETTING SEWER JETTER FORCED WATER AND DEBRIS INTO LATERAL | STOPPED JETTING CONTACTED INSURANCE AND CLEANING COMPANY WILL REPAIR DROP IN LINE TO BE ABLE TO JET
IN0025577 | LA PORTE MUNICIPAL STP | LA PORTE | 2010-07-23 |  |  | 1008 GREENWAY STREET | BASEMENT | PRECIPITATION 2.95" | DISCUSSION WITH PROPERTY OWNER AND FLYER MAILED TO PREVENT BASEMENT BACK UPS
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-05-31 | 1:17P - 4P |  | COMBINED SEWER DRAIN AT LAWRENCE / E. JEFFERSON | ROAD AND LAWN | 2" RAIN | INTERSECTION BLOCKED OFF JUST COMPLETED DARLINGTON SEWER SEPARATION WAS DESIGNED TO PARTIALLY MITIGATE PROBLEM
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-05-31 |  |  | 912 MICHIGAN AVE | BASEMENT | 2" RAIN BACKED UP THROUGH SINK ON TO FLOOR SINK SHUT OFF VALVE WAS NOT CLOSED DURING THE STORM | SCHEDULED THE SEWER TO BE CLEANED HOMEOWNER WAS PROVIDED WITH HANDOUT PREVENTING BASEMENT BACKUPS
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-05-31 |  |  | 709 TIPTON STREET | BASEMENT | 2" RAIN SOURCE OF WATER IN BASEMENT IS UNKNOWN NO DRAINS OR FIXTURES IN BASEMENT | SCHEDULED THE SEWER TO BE CLEANED HOMEOWNER WAS PROVIDED WITH HANDOUT PREVENTING BASEMENT BACKUPS
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-05-31 |  |  | 608 PLAIN ST. | BASEMENT | RAIN 2"
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-05-31 |  |  | 514 E. LINCOLN HIGHWAY | BASEMENT | RAIN 2" | ON-GOING SEWER SEPARATION PROJECTS
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-06-15 |  |  | 1310 WRIGHT STREET | BASEMENT | .86" RAIN STORM | OWNER CLEANED BASEMENT AND REP OF WASTEWATER DEPT. SENT OWNER A FLYER
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-06-15 | 8:30P |  | 1613 MICHIGAN AVE | BASEMENT | .86" RAIN STORM | OWNER CLEANED BASEMENT AND REP OF WASTEWATER DEPT. MET WITH OWNER
IN0025577 | LAPORTE MUNICIPAL STP | LA PORTE | 2010-12-28 | 8:30A - 10:30A | 1000 | FORCE MAIN LANE STREET AND CLOSSER AVENUE | PINE LAKE | BROKEN FORCE MAIN | SHUT DOWN L.S. USED VACUUM TRUCK TO HAUL COLLECTED SAMPLES WILL EVALUATE CONDITION TO DETERMINE IF REPLACEMENT IS NECESSARY
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-01-07 | 2:45P - 3:45 | 20 | 627 DUPAGE ST. BASEMENT FLOOR DRAIN | BASEMENT FLOOR | BLOCKAGE IN SEWER MAIN | JET CLEANED SEWER LINE TO ENSURE FULL CAPACITY
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-01-23 | 7A - 8:23A | 50 | 502 OAK STREET | BASEMENT | BLOCKAGE | JETTED AND REMOVED BLOCKAGE AND CLEAN WITH ACCORDANCE TO CSOOP
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-02-07 | 8:30P - 3:15P (2/8) | 145 | 1904 TENNESSEE STREET | BASEMENT | BLOCKAGE IN SEWER MAIN | JETTING AND CLEANED PUBLIC SEWER MAIN WILL BE ADDITIONALLY INSPECTED ON 2/9/2010
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-02-09 | 1:30P - 1:55P | 20 | 2403 ELSTON STREET | GROUND | BLOCKAGE IN SEWER MAIN | JETTING AND CLEANED PUBLIC SEWER MAIN WILL BE ADDITIONALLY
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-02-16 | 8:00A - 8:10A | 200 | PRIMARY DIGESTER #2 | GROUND | LINE BETWEEN PRIMARY DIGESTER PLUGGED | UNPLUGGED LINE, WILL WATCH DIGESTER LEVEL MORE CLOSELY
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-03-16 | 10:55A - 11:30 | 200 | MH AT 113 TALL TIMBERS CT | STREET | WAD OF RAGS AND SAND IN PUBLIC SEWER | VAC/JET LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-05 | 10:48A - 10:56A |  | 607 PLEASANT AVENUE | BASEMENT | PLUG IN PUBLIC MAIN | ALLEVIATED PLUG RECHECK LINE 6/15 PROPER REPORTING
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-13 | 3:34A - 4:37A | 1000 | MH #C15 &C16 ON B&E MARINA DOCK | TRAIL CREEK STREAM | RAIN 2" | STUDY UNDERWAY TO RELOCATE SEWER
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-13 |  | 125 | 126 E. 5TH ST | BASEMENT FLOOR | RAIN 2" | PRIVATE CONTRACTOR CLEANED UP BASEMENT
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-13 | 7:46A - 1:08P |  | 435 N CARROLL AVE | BASEMENT | HEAVY RAIN 2" AND PLUG | JETTED PUBLIC MAIN AND ALLEVIATED PLUG
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-13 | 7:23A - 11A | 100 | 325 N CARROLL AVENUE | BASEMENT FLOOR | PLUG IN PUBLIC MAIN 2" RAIN | ALLEVIATED PLUG RECHECK LINE 6/15 PROPER REPORTING
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-23 | 1:08P - 1:45P | 15 | 125 LAKE SHORE DR MH | GROUND | PLUG IN SEWER BETWEEN MH CFE9 AND CFE8 | REMOVED PLUG AND VACUUMED MH
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-25 | 12:02P - 3:50P (5/26) |  | INTERNAL PLANT BYPASS TO STORM RETENTION BASIN | STORM RETENTION BASIN | REPLACE SECONDARY CLARIFIER DISTRIBUTION WEIR
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-05-31 | 6:20P - 8:00A (6/2) | 5 | 919 E. MICHIGAN | STREET | PRIVATE LATERAL LINE BLOCKED | HOMEOWNER HIRED PRIVATE CONTRACTOR TO REPAIR LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-06-23 | 10:00A - 10:30A | 125 | 126 E. FIFTH ST | BASEMENT | RAIN 1.04"
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-06-23 | 10:23A - 11:20A | 2000 | 339 LINCOLN AVE | BASEMENT | RAIN 1.04" PLUG IN MAIN | JETTED OUT PLUG
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-06-25 | 11:50P - 1:40A (6/26) | 686000 | WWTP FILTER BUILDING | TRAIL CREEK | EQUIPMENT FAILURE | SECONDARY EFFLUENT WAS DISINFECTED INSPECTION OF WIRING FOR WEAR AND OTHER POTENTIAL PROBLEMS
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-06-26 | 12P - 1:05A | 200 | 201 DEWEY STREET | BASEMENT | SURCHARGE IN THE COMBINED SEWER .13" | CREW CLEANED CATCH BASINS
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-07-12 | 1:29P - 2:04P | 10 | 201 SCHOOL STREET | BASEMENT | PLUG IN PUBLIC MAIN | CREW ALLEVIATED PLUG AND LINE WAS RUNNING AGAIN RECHECK LINE 7/13/10
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-07-21 | 9:41A - 10:20A | 50 | 1530 LAKESHORE DRIVE MH | GROUND CATCH BASIN DRYWELL | BLOCKAGE | VACUUMED MH JETTED SEWER LINE CLEAN CATCH BASIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-07-21 | 3:41P - 3:46P | 30000 | WWTP FILTER BLDG WAS CHLOR/DECHLOR | TRAIL CREEK | POWER DISRUPTION | POWER ADDRESSED IMMEDIATELY AND REACTIVATED ALL EQUIPMENT
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-07-22 | 12:29P -2:00P | 2 | 1539 LAKE SHORE DRIVE | GROUND | DAMAGE TO SEWERS DUE TO WATER LINE INSTALLATION | EXCAVATION AND REPAIR TO DISTRICT LINES TELEVISING LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-07-24 | 2A - 3:15A | 2000 | MH C15, C16, C17 | TRAIL CREEK | PRECIPITATION 2.08" | CLEANING UP OVERFLOWS AND PRELIMINARY ENGINEERING STUDY TO RELOCATE SEWER
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-07-24 | 7A - 10P | 6000000 | OUTFALL #2 | TRAIL CREEK | INTENSE RAINFALL HYDRAULIC OVERLOADING | MAXIMIZING FLOW
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-07-29 | 11:15A - 11:16A | 1 | 216 AUTUMN TRAIL | BATHROOM IN HOME | CLEANING SEWER MAIN HOMEOWNER REPORTED WATER SPRAYED FROM TOILET | CREW FOLLOWED PROPER PROCEDURES WILL MONITOR FUTURE CLEANING PROCEDURES IN THIS LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-08-05 | 1:25P - 1:32P | 73000 | WWTP FILTER BUILDING | TRAIL CREEK | BYPASS OF TREATMENT PROCESS CLEAR WELL PUMP MOTOR REMOVED FOR BEARING REPAIR | MAXIMUM FLOW LIMIT WAS REDUCED ADDITIONAL FLOW DIVERTED TO DIURNAL BASIN PREEMPTIVE ADJUSTMENT OF MAXIMUM FLOW IN FUTURE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-08-24 | 4:53P - 5:20P | 1 | 441 PLEASANT AVENUE CLEANOUT | GROUND | PLUG IN PUBLIC MAIN | PLUGGED IMMEDIATELY CLEARED
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-09-02 | 10:21A - 10:43A |  | 417 E. COOLSPRING | SINK/TUB/TOILET | PLUG IN LINE | JETTED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-09-06 | 10:50A - 11:35A | 20 | 201 SCHOOL STREET | BASEMENT | PLUG IN PUBLIC MAIN | JETTED AND CLEARED PLUG WILL SCHEDULE FOR RE-CHECK
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-09-20 | 8:30A - 9:17A | 5 | 904 E. COOLSPRING AVE. BASEMENT BACKUP | BASEMENT FLOOR | PLUG IN PUBLIC MAIN | JETTED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-10-08 | 9:35A - 10:30A | 50 | 502 YORK ST | BASEMENT | PLUG OF HEAVY GREASE IN SEWER | JETTED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-10-08 | 3:45P - 3:46P | 6944 | WWTP FILTER BUILDING | TRAIL CREEK | LOSS OF POWER TO TREATMENT PLANT | POWER RESTORED AND EQUIPMENT REACTIVATED
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-11-01 | 1:30P - 3P | 50 | 238 EAST 2ND STREET MH | GROUND | ROOT BLOCKAGE CONTRACTOR REMOVED LID AND 50 GALLONS SPILLED OUT | RESPONDED WITH JET/VAC TRUCK LINE SCHEDULED FOR RECHECK
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-11-12 | 11:21A - 12:54P | 20 | 134 GRACE STREET | BASEMENT | PLUG IN PUBLIC MAIN | DISTRICT CREW JETTED MAIN LINE WILL BE SCHEDULED FOR RECHECK
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-11-12 | 11:02A - 11:22A | 2 | 116 COMBS STREET | BASEMENT | PLUG IN PUBLIC MAIN | DISTRICT CREW JETTED MAIN AND LINE WILL BE SCHEDULED FOR RECHECK
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-11-16 | 9:20A - 9:59A | 15 | 329 SOUTH PORTER STREET | BASEMENT | PLUG IN PUBLIC MAIN | DISTRICT CREW JETTED MAIN AND LINE WILL BE SCHEDULED FOR RECHECK
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-11-18 | 11A - 11:30A | 400 | 6012 EAST HWY 20 35 - 20 L.S. FORCE MAIN | DITCH | NIPSCO WHILE BORING HIT THE FORCE MAIN | SHUT DOWN L.S. VAC'D SEWAGE FROM DITCH AND WET WELL DISTRICT STAFF WILL REVIEW UNDERGROUND LOCATE AND MARKINGS
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-12-03 | 10:44A - 11:20A |  | 304 JACKSON ST. | BASEMENT FLOOR | PUBLIC MAIN PLUGGED | CREW UNPLUGGED PUBLIC MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-12-10 | 10:40A - 11:20A | 15 | 325 SPRINGLAND AVENUE | BASEMENT | PUBLIC MAIN PLUGGED | JETTED LINE AND RELIEVED BACKUP ADVISED HOMEOWNER PROPER CLEAN AND DISINFECTION
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-12-13 | 10:35A - 11:30A | 100 | 435 NORTH CARROLL AVENUE | BASEMENT | PUBLIC MAIN PLUGGED | ALLEVIATED PLUG RELIEVED BACKUP ADVISED HOMEOWNER PROPER DISINFECTION
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-12-20 | 11:28A - 12:00P | 30 | 221 N. RIDGELAND AVE | BASEMENT | BLOCKAGE IN PUBLIC MAIN AND PLUG IN PRIVATE LINE | JETTED PUBLIC MAIN AND LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-12-22 | 1:18P - 1:50P | 20 | 218 W HOMER ST. | BASEMENT | PUBLIC MAIN PLUGGED | JETTED PUBLIC MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2010-12-22 | 12:50P - 1:50P | 25 | 217 CHARLES ST. | BASEMENT | PUBLIC MAIN PLUGGED | JETTED PUBLIC MAIN
IN0040622 | SHIPSHEWANA MUNICIPAL STP | LAGRANGE | 2010-02-25 | ? - 9:20A | 400 | L.S. SR 5 NORTH OF US 20 | GROUND | PUMPS NOT WORKING | GOT ONE PUMP WORKING AND DO WEEKLY CHECKS ON L.S.
IN0040622 | SHIPSHEWANNA MUNICIPAL STP | LAGRANGE | 2010-05-20 | 5:30P - 9:00P | 15000 | LIFT STATION ST .5/STRD 20 | GROUND | RAIN 2.5" | BROKEN LATERAL TAKING WATER FROM FIELD; FITTED PIPE OVER OLD ONE AND USED SANDBAGS
IN0000094 | ARCELOR MITTAL IND HARBOR E | LAKE | 2010-03-07 |  | 24000 | INTERNAL OUTFALL #602 | STORM SEWER TO EXTERNAL OUTFALL 001 | COOLING TOWER 1 DOWN WHEN RESTARTED OVERWHELMED COLDWELL CAPACITY | SAMPLES TAKEN AND DISCHARGE VALUES WELL BELOW PERMITTED CONDITIONS
| CITY OF HOBART | LAKE | 2010-12-31 | 9:15A - 1:10P |  | LS @ 705 N. WISCONSIN | CREEK TO DEEP RIVER | RAIN 2.59" AND SNOW MELT | LS RUNNING AT FALL CAPACITY BUT COULD NOT KEEP UP WITH I & I. TRYING TO CORRECT I & I PROBLEMS.
| DEER CREEK SUBDIVISION | LAKE | 2010-12-03 | ? |  | L.S 109 AVE. | GROUND TO UNKNOWN STREAM | PRIVATELY OWNED L.S. HAD ACTIVE ALARM THAT WET WELL SURCHARGING | TOWN CONTACTED OWNER TO INFORM HIM SITUATION
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-01-24 | 2:05A - 1:55A (1/25) | 339000 | PARTIAL BYPASS SECONDARY CLARIFIERS TO CHLORINE CONTACT CHAMBER |  | RAIN .38 | BYPASSED FLOW REMIXED WITH TERTIARY TREATED EFFLUENT
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-03-13 | 1:50A - 11:00P | 756000 | SECONDARY CLARIFIERS | CHLORINE CONTACT TANK | RAIN .76"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-04-07 | 12:45P - 2:30A (4/8) | 600000 | SECONDARY CLARIFIERS | CHLORINE CONTACT CHAMBER | PARTIAL BYPASS DUE TO HIGH FLOWS | REMIXED WITH TERTIARY TREATED EFFLUENT PRIOR TO FINAL EFFLUENT SAMPLER
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-05-11 | 3:45P - 4:00P | 130000 | SECONDARY CLARIFIERS | CHLORINE CONTACT TANK | RAIN .90" | BYPASSED FLOW REMIXED WITH TERTIARY TREATED EFFLUENT IN DECHLORINATION CHAMBER
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-05-13 | 12:05A - 10:20P | 1205000 | SECONDARY CLARIFIERS | CHLORINE CONTACT TANK | RAIN .97" | BYPASSED FLOW REMIXED WITH TERTIARY TREATED EFFLUENT IN DECHLORINATION CHAMBER
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-06-23 | 4:35P - 4:20A (6/24) | 1664000 | SECONDARY CLARIFIERS BEFORE TERT FILTERS | CHLORINE CONTACT TANK | PRECIPITATION 2.06" | PARTIAL BYPASS DUE TO HIGH FLOWS FLOW WAS REMIXED WITH TERTIARY TREATED EFFLUENT
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-07-24 | 10P - 4A (7/25) | 818700 | PARTIAL BYPASS OF TREATMENT SECONDARY CLARIFIERS | CHLORINE CONTACT CHAMBER | RAINFALL 2.98" | FINAL EFFLUENT AUTO SAMPLER
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-07-31 | 6:20A - 2:20P | 1150000 | WWTP BYPASS OF TERTIARY FILTERS | CHLORINE CONTACT CHAMBER | HIGH FLOWS RAINFALL 1.7"
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-08-03 | 5:50A - 7:20P (8/4) | 4930000 | SECONDARY CLARIFIERS PARTIALLY TREATED RELEASE | CHLORINE CONTACT CHAMBER | BYPASS OF TERTIARY FILTERS DUE TO HIGH FLOWS | REMIXED WITH TERTIARY TREATED PRIOR TO FINAL SAMPLER
IN0039331 | DYER MUNICIPAL STP | LAKE | 2010-12-31 | 7:30A - 7:30P | 2300000 | SECONDARY CLARIFIERS | CHLORINE CONTACT CHAMBER | RAIN .9" | BYPASSED FLOW REMIXED WITH TERTIARY TREATED EFFLUENT IN THE DECHLORINATION CHAMBER
IN0022977 | GARY SD LAKE STATION | LAKE | 2010-04-07 | 8P - 12:30A (4/8) | 24000 | 2548 DEARBORN STREET | DITCH LINE LEADS TO BURN DITCH | 1.7" RAIN | PUMPS PUMPING FULL SPEED CONTINUE INVESTIGATING AND ELIMINATING INFILTRATION
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-11 | 16:00 - 18:14 |  | 1017 ELSWORTH STREET | BASEMENT | BLOCKAGE IN SEWER MAIN | JETTED AND CLEANED SEWER MAIN REESTABLISHED FLOW ACTIVELY CLEANING COLLECTION SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-17 | 4:00P - 8:30A (1/19) | 226000 | 6001 WEST INDUSTRIAL | GARY SANITARY DISTRICT | POWER FAILURE AT AIRPORT LIFT STATION NOT NOTICED ON SCADA SYSTEM | STARTED PUMPS AND STOPPED OVERFLOW, WILL MONITOR SCADA SYSTEM MORE CLOSELY
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-24 | 10:01P - 10:45P |  | PRIVATE SEWER 2698 CALHOUN | BUILDING FLOOR | BLOCKAGE FORMED MAIN SEWER LINE | CLEANED TO REMOVE BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-24 | 12P- ONGOING |  | BYPASS TREATMENT PROCESS- WWTP | GRAND CALUMET RIVER | BYPASS TRASH RACK DUE TO DAMAGED CHAINS | GET MAINTENANCE TO REPAIR AND DAMAGES AND REPLACE PARTS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-24 | 10:45 - 12:45 |  | PRIVATE SEWER 5420 PIERCE STREET | BUILDING FLOOR | BLOCKAGE FORMED MAIN SEWER LINE | CLEANED TO REMOVE BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-24 | 7 - 11:30 | 22000000 | BYPASS TREATMENT PROCESS- WWTP | GRAND CALUMET RIVER | POWER FAILURE BACKED UP IN CLARIFIER OPENED 84" GATE TO LOWER LEVEL IN WEIRS | BACK IN SERVICE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-24 | 2:58P - 4:45P | 10 | PRIVATE SEWER 1719 HENDRICKS STREET | BASEMENT | BLOCKAGE FORMED MAIN SEWER LINE | CLEANED TO REMOVE BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-28 | 0 - ONGOING |  | BYPASS TREATMENT PROCESS- WWTP | GRAND CALUMET RIVER | BYPASS TRASH RACK DUE TO DAMAGED CHAINS | GET MAINTENANCE TO REPAIR AND DAMAGES AND REPLACE PARTS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-29 | 12:00A - 11:59P | 47500000 | 3600 WEST 3RD AVE (BYPASS OF TREATMENT PROCESS) | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-29 | 9:30A - 1:00P |  | 1338 E 50TH COURT | BUILDING FLOOR | PRIVATE SEWER BACKUP RESULTING FROM BLOCKAGE IN MAIN LINE | SEWER LINE CLEARED TO REMOVER BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-30 | 12:00A - 11:59P |  | 3600 WEST 3RD AVE (BYPASS OF TREATMENT PROCESS) |  | BAR RACK IN HEADWORK'S AT WWTP BYPASSED FOR MAINTENANCE | BAR SCREENS IN OPERATION FOLLOWING BAR RACK SO MINIMAL IMPACT TO PLANT
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-01-31 | 12:00A - 11:59P | 43400000 | 3600 WEST 3RD AVE (BYPASS OF TREATMENT PROCESS) | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-01 | 12:00A - 11:59P | 42400000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-02 | 1200A - 11:59P |  | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-03 | 1200A - 11:59P |  | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-03 | 10:00A - 12:15P | 100 | 9115 OAK AVE | BUILDING FLOOR | BLOCKAGE IN MAIN SEWER LINE | MAIN SEWER CLEANED TO REMOVE BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-04 | 1200A - 11:59P |  | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-04 | 17:00 - 17:45 | 25 | 300 ELSWORTH STREET | BASEMENT | GREASE BLOCKAGE IN MAIN SEWER LINE | JETTED AND CLEANED SEWER MAIN CLEARED BLOCKAGE AND ACTIVELY CLEANING COLLECTION SYSTEM AS WEATHER PERMITS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-05 | 1200A - 11:59P |  | 3600 WEST 3RD AVE BYPASS TREATMENT PROCESS | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-06 | 1200A - 11:59P |  | 3600 WEST 3RD AVE BYPASS TREATMENT PROCESS | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-07 | 1200A - 11:59P |  | 3600 WEST 3RD AVE BYPASS TREATMENT PROCESS | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-08 | 12:45 - 13:30 |  | 4864 GRANT STREET | BASEMENT | BLOCKAGE IN SEWER MAIN | JETTED AND CLEANED SEWER MAIN AND ACTIVELY CLEANING OUR COLLECTION SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-08 | 1200A - 11:59P |  | 3600 WEST 3RD AVE BYPASS TREATMENT PROCESS | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-09 | 1200A - 11:59P | 38000000 | 3600 WEST 3RD AVE BYPASS TREATMENT PROCESS | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | WORKING TO GET UNIT OPERATIONAL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-10 | 0:00 - 14:00 |  | 3600 WEST 3RD AVE BYPASS TREATMENT PROCESS | GRAND CALUMET RIVER | HAD TO OPEN THE BYPASS TO THE TRASH RACK DUE TO UNIT BEING JAMMED | TRASH RACK IS BACK IN SERVICE BYPASS GATE CLOSED 100%
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-02-20 | 20:04 - 21:51 | 10 | 1432 AETNA STREET | BASEMENT | BLOCKAGE IN SEWER MAIN | JETTED AND CLEANED SEWER MAIN AND ACTIVELY CLEANING OUR COLLECTION SYSTEM AS WEATHER PERMITS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-03-13 | 1:45A - 10:30A | 2000000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | EFFLUENT SAND FILTER BYPASSED DUE TO NOT HAVING WEIR OVERFLOW IN SECONDARY SAND FILTER BUILDING | 84" BYPASS GATE CLOSED AND SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-03-16 | 6:47P - 7:15 | 5 | 6356 E. 3RD AVE | GROUND | BLOCKAGE IN SEWER MAIN | JETTED AND CLEANED SEWER
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-03-17 | 8:06A - 1:30P |  | 8120 LAKEWOOD PRIVATE SEWER BACK UP | BUILDING FLOOR | BLOCKAGE IN MAIN SEWER LINE | LINE CLEANED AND BLOCKAGE REMOVED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-03-31 | 3:30P - 5:00P | 10 | 1001 N. WAYNE ST. | BASEMENT | BLOCKAGE IN SEWER MAIN | JETTED AND CLEANED SEWER MAIN, CLEARED BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-04-02 | 7:25A - 10:30A | 5 | 7834 INDIAN STREET | BUILDING FLOOR | BLOCKAGE FORMED IN MAIN SEWER | MAIN SEWER CLEARED TO REMOVE BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-04-07 | 19:28 - 20:08 | 5 | 1507 EAST 50TH COURT | BASEMENT | SEWER MAIN CHARGED DUE TO PRECIPITATION .67" | WWTP FLOW WAS MAXIMIZED AND ACTIVELY CLEANING COLLECTION SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-04-07 | 18:50 - 19:20 | 5 | 4655 DELAWARE STREET | BASEMENT | SEWER MAIN CHARGED DUE TO PRECIPITATION .67" | WWTP FLOW WAS MAXIMIZED AND ACTIVELY CLEANING COLLECTION SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-04-09 | 8:30A - 11:30A | 5000 | 236 MORNINGSIDE | BASEMENT | SEWER MAIN COLLAPSED | CLEANING AND TELEVISING SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-04-13 | 17:33 - 18:34 | 50 | 612 HOVEY STREET | BASEMENT | CLOG IN SEWER MAIN | JETTED SEWER MAIN AND CLEARED CLOG, ARE ACTIVELY CLEANING COLLECTION SYSTEM AS WEATHER PERMITS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-04-16 | 07:00 - 12:15 |  | 3600 WEST 3RD AVENUE | GRAND CALUMET RIVER | BYPASS TREATMENT PROCESS EFFLUENT SAND FILTER BUILDING BYPASSED DUE TO BLACK WATER FILLED THE FILTERS BLACK WATER WAS FROM A VALVE THAT WAS OPEN | WILL CAP OFF VALVE IN QUESTION
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-04-18 | 9:45A - 11:30 | 100 | 762 RANDOLPH STREET | BUILDING FLOOR | BLOCKAGE FORMED IN MAIN SEWER LINE | MAIN SEWER LINE CLEANED TO REMOVE BLOCKAGE CONTINUE PROGRAM TO CLEAN TELEVISE REHABILITATE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-02 | 11:55P - 1:35A (5/3) |  | 7858 MILLTIN ROAD | GRAND CALUMET RIVER | BLOCKAGE IN MAIN SEWER LINE | MAIN LINE CLEANED TO REMOVE BLOCKAGE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-09 | 3:00P - 7:26P |  | 23RD AND WISCONSIN LS | GROUND | SEWER LINE BROKE AT LS | VACUUMED SEWAGE AND SHUT DOWN LIFT STATION
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-11 | 8:13A - 9:50 | 250 | SEWER BACKUP 247 TAFT PLACE | FLOOR | BLOCKAGE IN MAIN LINE | SEWER CLEANED AND BLOCKAGE REMOVED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-11 | 8:50A - 10:00A |  | SEWER BACKUP 2330 W 2ND ST | FLOOR | BLOCKAGE IN MAIN LINE | SEWER CLEANED AND BLOCKAGE REMOVED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-11 | 1:44A - 2:30A |  | SEWER BACKUP 1216 HAMILTON | FLOOR | BLOCKAGE IN MAIN LINE | SEWER CLEANED AND BLOCKAGE REMOVED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-11 | 2:38P - 3:15P |  | SEWER BACKUP 5034 E 10TH AVE | FLOOR | BLOCKAGE IN MAIN LINE | SEWER CLEANED AND BLOCKAGE REMOVED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-11 | 8:20A - 10:00A |  | SEWER BACKUP 6627 HEMLOCK AVE | FLOOR | BLOCKAGE IN MAIN LINE | SEWER CLEANED AND BLOCKAGE REMOVED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-13 | 2:40P - 4:00P |  | 5101 PENNSYLVANIA | FLOOR | BLOCKAGE IN SEWER LINE | SEWER LINE CLEANED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-13 | 11:05A - 4:50P | 3000000 | 3600 W. 3RD AVE | GRAND CALUMET RIVER | RAIN. BYPASSED EFFLUENT FILTER BUILDING DUE TO HIGH FLOW. SECONDARY CLARIFIERS HAVE NO WEIR OVERFLOW | WILL GET OTHER TWO FILTER CELLS FIXED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-14 | 8:03A - 10A | 45 | 7175 ASH AVENUE | BASEMENT | BLOCKAGE IN LINE OF SANITARY SEWER | ALLEVIATE BACKUP AND CONTINUING THE CLEANING OF COLLECTION SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-18 | 8A - 9:45A | 20 | 774 MATTEWS STREET | BUILDING FLOOR | BLOCKAGE IN MAIN SEWER LINE | CLEANED TO REMOVE BLOCKAGE AND CONTINUE PROGRAM TO CLEAN, TELEVISE, REHABILITATE DETERIORATED SEWERS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-28 | 16:05 - 18:15 |  | 3461 RHODE ISLAND | BASEMENT | SEWER MAIN CLOGGED | JETTED SEWER MAIN AND RE-ESTABLISHED FLOW
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-05-31 | 14 -2:25 (6/1) | 49800000 | 3600 WEST 3RD AVENUE | GRAND CALUMET RIVER | RAIN EVENT HAD TO OPEN 84" BYPASS GATE 10% TO HELP LOWER LEVEL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-09 | 9:30A - 12:00P | 10 | 4140 E 13TH | BUILDING FLOOR | PRIVATE SEWER BACKUP | MAIN SEWER LINE CLEANED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-15 | 21:43 - 23:50 | 1400000 | 3600 WEST 3RD AVENUE | GRAND CALUMET RIVER | BYPASS OF TREATMENT FILTER BYPASSED DUE TO HIGH FLOWS PRECIPITATION .61" | CONTINUE TO IMPLEMENT WET WEATHER PLAN TO HANDLE HIGH FLOWS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-17 | 8:55A - 9:10A | 200 | 4600 EAST 15TH PLACE | GRAND CALUMET RIVER | LINE WAS BROKEN IN THE DRYWALL PIT THAT PUMPS PUMP INTO | PUMP DOWN THE WET WELL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-18 | 5:38P - 11:59P | 38500000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | RAIN 1.38" | BYPASS GATE OPENED 20%TO LOWER WEIR LEVELS.
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-19 | 11:59P - 9:09P (6/20) | 17100000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | RAIN .08" | BYPASS GATE OPENED 20%TO LOWER WEIR LEVELS.
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-21 | 10:41A - 3:56P | 2200000 | PLANT | LITTLE CALUMET RIVER | RAIN; OPEN BYPASS GATE 10% | FILTER CELLS BACK IN SERVICE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-23 | 14 - 16 | 5 | 2676 FILLMORE STREET | BASEMENT | SEWER MAIN CAVE IN AT 408 FILLMORE | REPLACED FAILED SECTION AND REESTABLISHED FLOW ACTIVELY CLEANING SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-23 | 9 - 17:00 | 40 | 333 PIERCE STREET | BASEMENT | SEWER MAIN CAVE IN AT 408 FILLMORE | REPLACED FAILED SECTION AND REESTABLISHED FLOW ACTIVELY CLEANING SYSTEM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-24 | 12:00A - 8:34P |  | 3600 WEST 3RD AVE BYPASS GATE | GRAND CALUMET RIVER | TRASH RACK OUT OF SERVICE, OPENED BYPASS GATE | PUT TRASH RACK BACK IN SERVICE, CLOSED BYPASS GATE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-24 | 12:00A - 11:59P | 11100000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | RAIN ; BYPASS GATE OPENED 10%
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-06-25 | 0 - 20:34 | 7600000 | 3600 WEST 3RD AVENUE | GRAND CALUMET RIVER | STILL UNDER HIGH FLOWS | OPENED 84" GATE 5 % TO KEEP FILTER BUILDING UNDER CONTROL
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-07-24 | 2:30 - 23:59 | 38300000 | 3600 WEST 3RD AVENUE | GRAND CALUMET RIVER | RAIN EVENT AND BREAKING DOWN OF WISEMAN SCREEN | PLANS TO GET WISEMAN SCREEN BACK UP AND RUNNING
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-07-25 | 0 - 20:38 | 23800000 | 3600 WEST 3RD AVENUE | GRAND CALUMET RIVER | RAIN EVENT AND BREAKING DOWN OF WISEMAN SCREEN | PLANS TO GET WISEMAN SCREEN BACK UP AND RUNNING
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-07-28 | 0 - 23:59 | 0 | WWTP BYPASS OF TREATMENT PROCESS |  | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-07-29 | 0 - 23:59 | 83000000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-07-30 | 0 - 23:59 | 85500000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-07-31 | 0 - 23:59 | 84700000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-07-31 | 8:30 - 20:58 | 26800000 | WWTP 84" BYPASS GATE | GRAND CALUMET RIVER | RAIN .62" AND 2 TANKS OUT OF SERVICE | PLANS IN PROGRESS TO GET TANKS BACK UP AND RUNNING
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-01 | 0 - 20:58 | 84500000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-02 | 0 - 23:59 | 85100000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-03 | 0 - 23:59 |  | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | NEW MOTOR IS BEING PROCURED AND INSTALLED REDUCE LOAD FACTOR WHEN POSSIBLE AND REDUCE CHANNEL LEVEL BY PLACING ADDITIONAL SCREW PUMP
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-03 | 7:20 - 23:40 | 9900000 | WWTP 84" BYPASS GATE | GRAND CALUMET RIVER | RAIN 1.16" AND 2 TANKS OUT OF SERVICE | INCREASE HOLDING CAPACITY BY PLACING ADDITIONAL CLARIFIER ON LINE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-04 | 08:25 - 05:40 (8/5) | 10500000 | WWTP 84" BYPASS GATE | GRAND CALUMET RIVER | RAIN .95" AND 2 TANKS OUT OF SERVICE | INCREASE HOLDING CAPACITY BY PLACING ADDITIONAL CLARIFIER ON LINE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-05 | 0 - 23:59 | 84000000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-06 | 0 - 23:59 | 96000000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-07 | 0 - 23:59 |  | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-08 | 0 - 23:59 | 84400000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-08 | 13:00 - 14:45 | 25 | 3639 WEST 13 AVENUE | BASEMENT | BLOCKAGE FORMED IN SEWER LINE | SEWER LINE RODDED CLEARED BLOCKAGE CONTINUE SEWER CLEANING PROGRAM
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-09 | 0 - 23:59 | 80700000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-10 | 0 - 23:59 | 78000000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-11 | 0 - 23:59 | 70300000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-12 | 0 - 23:59 | 62800000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-13 | 0 - 23:59 | 87400000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED, MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-14 | 0 - 23:59 | 73000000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED, MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-15 | 0 - 23:59 | 41000000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED, MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-16 | 0 - 23:59 |  | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED, MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-17 | 0 - 23:59 |  | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED, MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-18 | 0 - 23:59 |  | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED, MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-19 | 0 - 23:59 | 31500000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-20 | 0 - 23:59 | 31600000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-21 | 0 - 23:59 | 45200000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-22 | 0 - 23:59 | 12700000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-23 | 0 - 23:59 | 18300000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-24 | 0 - 23:59 |  | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-25 | 0 - 23:59 |  | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-26 | 0 - 23:59 | 35500000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | RESTORE WEISMAN SCREEN TO SERVICE AS SOON AS POSSIBLE
IN00322977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-08-27 | 0 - 5:48P | 40500000 | WWTP BYPASS OF TREATMENT PROCESS | GRAND CALUMET RIVER | WEISMAN SCREEN BYPASSED MALFUNCTIONING DRIVE MOTOR | WISEMAN BACK IN SERVICE AND BYPASS IS CLOSED
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-09-24 | 14:05 - 14:35 | 100 | DEWATERING BLDG LS AT WWTP | GROUND | FAULTY TRANSDUCER | CLEANED UP ARE REPLACED TRANSDUCER AND CONFIRM PROPER OPERATION
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-10-14 | 11:20A - 3:00P | 50 | DIGESTER | GROUND | BACK FLUSHING DIGESTER FEED LINE TO THE #2 DIGESTER AND WATER SUPPLY VALVE WAS NOT CLOSED. ALLOWED #2 SLUDGE BOX TO TO BACK FEED AS THOUGH THEY WERE FEEDING #2 DIGESTER | PROCURED A CORRUGATED/FLEXIBLE HOSE AND ATTACHED IT TO THE OVERFLOW DRAIN AND DIRECTED THE DISCHARGE TO THE INLET OF THE 42" SANITARY SEWER TO THE WEST INTERCEPTOR
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-10-25 | 1:30A - 6:15A |  | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | RAIN 1.08" 2 OF 5 SCREW PUMPS NOT OPERATING | OPENED 84" BYPASS GATE
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-11-30 | 13:30 - 14:30 |  | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | RAIN AND 2 OF 5 SCREW PUMPS NOT OPERATING | PLANS IN PROGRESS TO REPAIR AT LEAST ONE OF SCREWS
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-11-30 | 4:15A - 4A (12/1) | 23000 | FORCE MAIN NORTH PRIMARY | SANITARY SEWER | DRESSER COUPLING RUPTURED | REALIGNED AND BOLTED BACK THE DRESSER COUPLING
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-12-30 | 15:40 - 19 | 8000000 | WWTP | GRAND CALUMET RIVER | COUPLER BRAKING ON SCREW PUMP #2 RESULTED IN ONLY 2 0F 5 SCREW PUMPS OPERATING AND MELTING SNOW | PLANS IN PROGRESS TO GET AT LEAST ONE OF THE THREE OPERATING
IN0022977 | GARY WASTEWATER TREATMENT PLT | LAKE | 2010-12-31 | 8:30A - 11:45A (1/1) | 52900000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | BROKEN COUPLER ON #2 SCREW PUMP | OPENED BYPASS GATE 30%
| GRIFFITH, TOWN OF | LAKE | 2010-06-23 | ? - (6/24) | 4100000 | PUMP STATION | SWAMP | EMERGENCY NECESSARY DUE TO DRENCHING RAINS ON TOP ALREADY SATURATED GROUND 2.7"
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2010-01-04 | 10:30A - 11:00A |  | BARING AVE PUMPING STATION | LCR | CONTRACTING COMPANY WORKING ON PUMPS | NO DISCHARGE, CONTRACTOR WILL CONSULT SD PERSONNEL PRIOR TO MAKE CHANGES TO HSD EQUIPMENT
| HIGHLAND | LAKE | 2010-06-18 | 4P - 4A (6/19) | 326817 | 5TH STREET PUMP STATION | STORM SEWER | REDUCED PUMPING CAPACITY BECAUSE ONE PUMP OUT FOR SERVICE AND HEAVY RAINS 1.53"
| HIGHLAND | LAKE | 2010-06-23 |  | 1248000 | 5TH STREET PUMP STATION 16 HOURS | STORM SEWER | REDUCED PUMPING CAPACITY BECAUSE ONE PUMP OUT FOR SERVICE AND HEAVY RAINS 2.33"
| HIGHLAND | LAKE | 2010-06-23 |  | 546000 | GRACE PLACE DULUTH STREET 7 HOURS |  | REDUCED PUMPING CAPACITY BECAUSE ONE PUMP OUT FOR SERVICE AND HEAVY RAINS 2.33"
| HIGHLAND | LAKE | 2010-06-23 |  | 712775 | MH 1345 BYPASS 27 HOURS |  | REDUCED PUMPING CAPACITY BECAUSE ONE PUMP OUT FOR SERVICE AND HEAVY RAINS 2.33"
| HIGHLAND | LAKE | 2010-06-23 |  | 569382 | MH 1230 BYPASS 21 HOURS |  | REDUCED PUMPING CAPACITY BECAUSE ONE PUMP OUT FOR SERVICE AND HEAVY RAINS 2.33"
| HOBART, CITY OF | LAKE | 2010-05-13 | 2:15A - 8:30P |  | LS @ 705 N. WISCONSIN ST | DEEP RIVER | RAIN 1.78" | TRYING TO FIND I & I SOURCES
| HOBART, CITY OF | LAKE | 2010-06-23 | 7:15P - 5:30A (6/24) |  | LS 705 NORTH WISCONSIN STREET | DEEP RIVER | SUDDEN HEAVY RAIN ON SATURATED GROUND | RAN L.S. 100% CAPACITY CITY IS CURRENTLY LOOKING FOR I & I
| HOBART, CITY OF | LAKE | 2010-06-23 | 8P - 11P |  | NORTH LINDAST MH 704-002 | FROG CREEK | HEAVY RAIN 2.15" | RAN L.S. 100% CAPACITY CITY IS CURRENTLY LOOKING FOR I & I
| HOBART, CITY OF | LAKE | 2010-06-23 | 11:39A - 3P |  | LS 705 NORTH WISCONSIN STREET | DEEP RIVER | SUDDEN HEAVY RAIN ON SATURATED GROUND | RAN L.S. 100% CAPACITY CITY IS CURRENTLY LOOKING FOR I & I
| HOBART, CITY OF | LAKE | 2010-06-23 | 8P - 11P |  | SOUTH LAKE PARK AVENUE MH 605-003 | LAKE GEORGE | HEAVY RAIN 2.15" | RAN L.S. 100% CAPACITY CITY IS CURRENTLY LOOKING FOR I & I
| HOBART, CITY OF | LAKE | 2010-06-23 | 8P - 2:30A (6/24) |  | MH 705-063 | DEEP RIVER BELOW LAKE GEORGE DAM | SUDDEN HEAVY RAIN ON SATURATED GROUND | RAN L.S. 100% CAPACITY CITY IS CURRENTLY LOOKING FOR I & I
| HOBART, CITY OF | LAKE | 2010-06-23 | 8P - 11P |  | 3RD WISCONSIN MH 505-018 | LAKE GEORGE | HEAVY RAIN 2.15" | RAN L.S. 100% CAPACITY CITY IS CURRENTLY LOOKING FOR I & I
| HOBART, CITY OF | LAKE | 2010-07-25 | 12:47A - 3:55A |  | LS #13 16TH AND LIVERPOOL | TURKEY CREEK | HEAVY SUDDEN RAIN 1.83" ON SATURATED GROUND | LS RAN AT CAPACITY 100% UNTIL BYPASS ENDED CITY LOOKING INTO I & I
| HOBART, CITY OF | LAKE | 2010-12-31 | 10:25A - 12:50P |  | MH 705-063 | DEEP RIVER | RAIN 2.5" SNOW MELT | LS AT 100% CAPACITY
INJ031089 | INDEPENDENCE HILL C.D. | LAKE | 2010-07-26 |  | 50 | MH YGAM0365 | GROUND | PRECIPITATION 4.5"
INJ031089 | INDEPENDENCE HILL C.D. | LAKE | 2010-08-03 | 7:30A - 10:00A | 400 | MH YGAM # 0394, E. 78TH, 7310 MARSHALL ST. | GROUND | RAIN 2.1" I & I IN SEWER SYSTEM | CHECK VALVE INSTALLED ON SEWER LATERAL AT 7310 MARSHALL ST.
INJ031089 | INDEPENDENCE HILL C.D. | LAKE | 2010-12-31 | 9:00A - 9:30A | 200 | 78TH AVE & KAISER DITCH | GROUND | RAIN 1.3" SNOW MELT | AREA CLEANED
IN0033081 | LAKE DALECARLIA RWD | LAKE | 2010-02-03 | 8:00A - 10:00A |  | LIFT STATION NORTH LAKE VIEW DR. | GROUND | BOTH PUMPS AT LS FAILED | BOTH PUMPS REPAIRED
IN0033081 | LAKE DALECARLIA RWD | LAKE | 2010-08-03 | ? - 9 |  | NORTH LAKEVIEW DRIVE LS | GROUND AND LAKE | POWER FAILURE HEAVY STORM ALSO KNOCKED OUT CHATTER BOX TO ALARM OPERATOR | BOTH PUMPS WERE TURNED BACK ON AND RUNNING SATISFACTORY REPAIR CHATTERBOX
IN0033977 | LAKE STATION, CITY OF | LAKE | 2010-01-29 | ? - 9:30 (1/30) |  | 35TH & ALLEN LIFT STATION | GROUND | HEATER INSIDE PUMP HOUSE FAILED | REPLACED HEATER, VACTORED UP AS MUCH AS POSSIBLE. INSTALLING COMMUNICATION SYSTEM. LIMED AREA.
IN0022977 | LAKE STATION, CITY OF | LAKE | 2010-05-13 | 3:50A - 4:05A | 4500 | VIKING VILLAGE LS #7 | DEEP RIVER | RAIN 1.5" MECHANICAL SEAL ON PUMP FAILED | MANUALLY PRIMED PUMP 1 AND RAN UNTIL WET WELL LOW ENOUGH PUMP 2 COULD KEEP UP
IN0022977 | LAKE STATION, CITY OF | LAKE | 2010-05-13 | 3:40A - 1:15P | 107125 | 2548 DEARBORN ST | DITCH LINE THAT LEADS TO BURNS DITCH | RAIN 1.5" | SLOWED RATE FROM CENTRAL AND ALLEN LS
| LAKE STATION, CITY OF | LAKE | 2010-06-23 | 7:35P - 7:50P | 750 | VIKING VILLAGE | DEEP RIVER | 2.4" RAIN OVER CHARGED SYSTEM | BOTH PUMPS AT LS RUNNING FULL CAPACITY SYSTEM OVERCHARGED CURRENTLY THIS AREA IS BEING VIDEOTAPED FOR I & I
| LAKE STATION, CITY OF | LAKE | 2010-06-23 | 7:46P - 5:20A (6/24) | 92550 | 2548 DEARBORN STREET | DITCH LINE TO BURN DITCH | 2.4" RAIN OVER CHARGED SYSTEM | CONTROLLED FLOW AT SEVERAL LS TO MINIMIZE IMPACT CONTINUE TO INVESTIGATE AND ELIMINATE I & I
| LAKE STATION, CITY OF | LAKE | 2010-06-26 | 11:40P - 12:50A (6/27) | 126000 | 2548 DEARBORN STREET | DITCH LINE TO BURN DITCH | VFD FAILURE AND COULD NOT RESTART PUMPS | CONTACTED REPAIR COMPANY OPERATED CENTRAL AND ALLEN LS AS SLOW AS POSSIBLE TO USE COLLECTION SYSTEM AS STORAGE CALLED FOR PUMP BY TIME PUMP GOT THERE THE LS BACK IN SERVICE
| LAKE STATION, CITY OF | LAKE | 2010-06-27 | 12:25P - 5:50P | 58500 | 2548 DEARBORN STREET | DITCH TO BURN DITCH | PRECIPITATION 1" ON ALREADY OVER-CHARGED SYSTEM | OPERATED CENTRAL AND ALLEN LS AS SLOW AS POSSIBLE TO USE COLLECTION SYSTEM AS STORAGE
IN0022977 | LAKE STATION, CITY OF | LAKE | 2010-10-13 | ? - 3:30P |  | 1385 28TH AVE | BASEMENT | ROOTS IN GRAVITY LINE | CUT OUT ROOTS
INJ035548 | MERRILLVILLE CONSERVANCY DIST. | LAKE | 2010-10-18 | 10:00A - ? |  | 66TH & TAFT ST. | TURKEY CREEK |  | DAM CREEK, PUMP OUT CREEK, ADD CLEAN WATER
| PIMA PROPERTIES | LAKE | 2010-07-07 |  |  | 640 - 660 US HIGHWAY 30 | GROUND | EQUIPMENT FAILURE | BLDG INSPECTOR LAKE COUNTY ISSUED NOTICE VIOLATION HAVE IT REPAIRED IN 24 HOURS
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2010-06-24 |  |  | MH @ 83RD LANE | RETENTION POND | RAIN | CLEANED UP DEBRIS
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2010-08-03 | 7:30A - 1:00P | 10800 | MH @ 7930 84TH PL. | RETENTION POND | RAIN 2.12"
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2010-08-03 | 7:30A - 6:15A | 35775 | MH 83RD LN | RETENTION POND | RAIN 2.12"
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2010-11-14 | 1P - 2:30P | 18000 | MH 83RD LANE | RETENTION POND | BLOCKED SEWER | VACTOR CREW CLEARED BLOCKAGE CLEANED UP AREA AND VERIFIED SEWER RUNNING FULL CAPACITY
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2010-12-31 | 1:00P - 2:00P | 2600 | 6613 W. 86TH COURT | BASEMENT | RAIN 1.18" SNOW MELT. MAYBE VENTING ISSUE | MH COVER PULLED AND AIR ENTERED MH AND SEWAGE RECEDED. PERFORMING DYE TESTS AND LINE INVESTIGATIONS
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2010-02-19 | 1:30A - 6:30A |  | 1982 GREEN VALLEY DRIVE | BASEMENT | OBSTRUCTION IN SANITARY SEWER MAIN | JETTED SEWER MAIN WITH HIGH PRESSURE JET TRUCK AND HAVE A CONTINUING SEWER CLEANING AND MAINTENANCE PROGRAM IN PLACE
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2010-03-04 | 15:45 - 18:30 |  | 1982 GREEN VALLEY FLOOR DRAIN | BASEMENT | ROOT MASS | SEWER LINE JETTED REMOVED ROOT MASS VIDEOED SEWER MAIN
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2010-06-18 | 6:17P - 7:10P | 100 | 3473 W. LAKE SHORE DR | BASEMENT | RAIN 1.1" LS LOST POWER | SET UP PORTABLE TRANSFER PUMP, REPAIR LS
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2010-10-05 | 9:04A - 10:15A | 50 | 2537 EAST LAKE SHORE DRIVE | GROUND | FORCE MAIN AIR RELEASE VALVE MALFUNCTIONED | AIR RELEASE VALVE WILL BE REPAIRED OR REPLACED AND LIME APPLIED TO AFFECTED AREA
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2010-12-06 | 7:00A - 9:00A | 250 | WWTP - DIGESTER | GROUND | PACKAGE PLANT WASTEGATE TO DIGESTER MALFUNCTIONED CAUSING DIGESTER TO OVERFLOW | AREA VACUUMED AND LIME APPLIED
IN0058343 | WINFIELD WWTP | LAKE | 2010-02-25 | 8:00A - 10:00A (2/22) |  | TREATMENT PLANT, OUTFALL #001 | RECEIVING STREAM | RETURN ACTIVATED SLUDGE FLOW STOPPED DUE TO BLOCKAGE | REMOVED BLOCKAGE, INCREASE PRE-TREATMENT CLEANING FREQUENCY
IN0025577 | LAPORTE MUNICIPAL STP | LAPORTE | 2010-02-21 | 10:38A - 11:30A | 1 | 911 GREENWAY STREET | BASEMENT | GREASE SEWER BLOCKAGE | CLEARED THE BLOCKAGE AND A GREASE FLYER WAS DISTRIBUTED
IN0025577 | LAPORTE MUNICIPAL STP | LAPORTE | 2010-06-03 |  | 1 | 554 CIRCLE DR. | BASEMENT | RAIN 2" | CREW CLEARED BLOCKAGE
IN0025577 | LAPORTE MUNICIPAL STP | LAPORTE | 2010-11-22 |  |  | 1008 GREENWAY ST. | BASEMENT | RAIN .62" LEAVES AND STICKS IN LINE | CLEANED SEWER MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-02-17 | ? - 9:20A | 200 | 4125 FRANKLIN ST. MH | GROUND | UPSTREAM RESTAURANT DISCHARGING | VACUUMED MH AND GROUND, SPEAK TO UPSTREAM USERS
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-05-23 | 10:08A - | 1 | 526 FIR ST. | BASEMENT FLOOR | BLOCKAGE IN LINE | JETTED AND CLEANED PUBLIC MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-10-19 | 2:12P - 2:17P | 20000 | BYPASS OF TERTIARY TREATMENT | CONTACT TANK | MOMENTARY POWER LOSS NIPSCO UTILITY PROVIDER TRIPPED BREAKER | ALL EQUIPMENT REACTIVATED IMMEDIATELY AND CONTACTED NIPSCO TO PREVENT FUTURE OCCURRENCE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-11-05 | 12:15P - 1:23P | 1 | 1008 SPRING ST. | BASEMENT FLOOR | PLUG IN PUBLIC MAIN | CREW ALLEVIATED PLUG
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-11-22 | 11:53A - 1:40P | 20 | 206 DEWEY ST. | BASEMENT FLOOR | PLUG IN PUBLIC MAIN | JETTED MAIN AND ALLEVIATED PLUG
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-12-08 | 10:53A - 12:40P | 1000 | FIRST MH UPSTREAM OF MH AQZA9 | GROUND | PLUG IN PUBLIC MAIN | JETTED PUBLIC MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-12-08 | 9:13A - 9:55A | 2 | 329 S. PORTER ST | BASEMENT FLOOR | PLUG IN PUBLIC MAIN | JETTED PUBLIC MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-12-18 | 4:40P - 5:33P |  | 221 RIDGELAND AVE | BASEMENT FLOOR | PUBLIC MAIN PLUGGED | JETTED PUBLIC MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LAPORTE | 2010-12-20 | 8:05P - 8:50P | 2 | 307 N. DICKSON ST | BASEMENT | PLUG IN PUBLIC MAIN | JETTED PUBLIC MAIN
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2010-01-06 | 11:00A - 2:00P |  | BEDFORD HEIGHTS LS #008 | BAILEY BRANCH OF PLEASANT CREEK | HIGH PRESSURE LINE FROM LS BROKE | DUG UP AND REPAIRED LINE
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2010-01-10 | 11:00 - 14:00 | 5000 | BEDFORD HEIGHTS L.S. #8 | BAILEY BRANCH OF PLEASANT CREEK | EQUIPMENT FAILURE BREAKDOWN ON HIGH PRESSURE LINE SAME LINE DIFFERENT PLACE HAS LAST WEEKS BREAK | CREW ONSITE TO DIG UP AND REPAIR WILL CONTINUE TO MONITOR THIS AREA PLANNING FOR REPLACEMENT OF ENTIRE SECTION OF OLD LINE IN THIS AREA
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2010-04-21 | ? | 1000 | FORCE MAIN GREEN GABLES L.S. HWY 58 EAST | GROUND | CHECK VALVE LEAKING | WATCH AREA CLOSER
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2010-10-26 | 11:00A - 12:45P | 1000 | 22ND & T LS | LEATHERWOOD CREEK | POWER OUTAGE AT LS
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2010-10-26 | 11:00A - 5:00P | 10000 | BROADVIEW LIFT STATION, SPIDER CREEK LS | SPIDER CREEK | POWER OUTAGE AT LS
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2010-11-26 | 11 - 12 |  | 1215 4TH STREET | BASEMENT | SEWER MAIN BLOCKAGE | CREW OPENED LINE AND DRAINED BACK INTO SANITARY SEWER
IN0023787 | MITCHELL MUNICIPAL STP | LAWRENCE | 2010-02-11 | 6:00P - 9:30P | 2000 | RESIDENCE CLEAN OUT | GROUND | RELAY IN POWER PANEL FAILED | CITY WILL CLEAN AND LIME YARD, INSTALL FLOW CHECK
IN0030044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-03-13 |  |  | MH NORTH OF VILLAGE PANTRY | STORM SEWER | RAIN 2.33" | MAXIMIZE FLOW TO WWTP
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-02 | 8P - 8A (6/3) | 20000 | M.H. NORTH OF WILLOWS L.S. | GROUND | ROOTS COLLECTED IN M.H. | CLEARED OUT ROOTS AND CLEANED PARKING LOT WITH VAC TRUCK
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-22 | 8:00A | 20000 | RAM GRAPHICS LIFT STATION | GROUND | RAIN 2.52" | MAXIMIZE FLOW TO WWTP
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-22 | 8:00A | 50000 | MH @ JOHN & EDGEWAY | GROUND | RAIN 2.52" | MAXIMIZE FLOW TO WWTP
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-22 | 8:00A | 50000 | MH NORTH OF VP | STORM SEWER | RAIN 2.52" | MAXIMIZE FLOW TO WWTP
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-22 | 8:00A | 100000 | MH @11TH AND SR 9 | BILL CREEK | RAIN 2.52" | MAXIMIZE FLOW TO WWTP
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-23 | 12:45P - 12:50P | 20000 | RETURN SLUDGE WELL | GROUND | OPERATOR LOWERED SLIP TUBE TO CLEAR UP SLUDGE; SLUDGE CAME TOO FAST FOR PUMPS TO HANDLE AND FLOOD OVER TOP | PAY MORE ATTENTION
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-28 | 9:30A | 5000 | LS | GROUND | PRECIPITATION 1.78" | MAXIMIZE FLOW TO TREATMENT PLANT
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-28 | 7A - | 20000 | MH NORTH VILLAGE PANTRY | STORM SEWER | PRECIPITATION 1.78" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-28 | 7A - | 50000 | MH 11TH STREET & ST RD 9 | BILLS CREEK | PRECIPITATION 1.78" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-06-28 | 7A - | 20000 | MH EDGEWAY DRIVE | GROUND | PRECIPITATION 1.78" | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-08-12 | 10:50A - 11:30A | 10 | LIFT STATION | GROUND | BLOWN FUSE | REPLACED FUSE
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-10-04 | 8A - 9A | 50 | L.S. BELMONT | GROUND | POWER SURGE
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2010-11-01 | (4/1/11) |  | CHLORINE CONTACT TANK |  | NORMAL CLEANING AND MAINTENANCE FOR THE 2011 DISINFECTING SEASON
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-14 | 7:30 - 9:30 | 0 | PLANT CAPACITOR | NO RELEASE | CAPACITOR BANK B WILL BE SHUTDOWN TO CHANGE A CIRCUIT BREAKER BANK B IS NOT IN SERVICE AT THIS TIME AND WONT BE UNTIL PLANT UPGRADE COMPLETED 60-90 DAYS | PREVENTIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-15 | 05:00 - 06:00 | 0 | WWTP | NO RELEASE | SHUTTING DOWN POWER TO PLANT, HAS GENERATOR IN PLACE | PART OF ONGOING CONSENT DECREE UPGRADES
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-21 | 6:15P - 10:45P | 1900000 | RAW WET WELL | WHITE RIVER | RAIN .6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-21 | 4:43P - 12:55P (1/22) | 1800000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-21 | 7:00P - 3:00P (1/22) |  | RAW WET WELL | WHITE RIVER | DURING BYPASS BAR RAKE AT RAW BUILDING GOT HUNG UP ON SOMETHING | OPENED GATED TO BYPASS BAR RAKE TO SEND FLOW TO PRIMARY'S 1, 2, 3 AND 4. FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-21 | 3:30A - 3:10A | 1000 | MANHOLE | STREET STORM SEWER | CLAY TILE ASPHALT PIECES, SAND AND ROCKS CAUSED BLOCKAGE | PUMPED SEWER CLEAN AND VACUUMED AREA OF OVERFLOW
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-22 | 6:25P - 8P | 50 | MANHOLE 2032B 47TH | DITCH | BLOCKAGE | REMOVED DEBRIS PUMPED SEWAGE FROM DITCH
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-24 | 06:35 - 07:30 | 168000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .25" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-25 | 7 - 15 | 0 | NO RELEASE |  | CEMENTECH CONVEYOR BELT DRIVE CHAIN SNAPPED | MAINTENANCE ON SITE TO FIX CHAIN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-26 | 09:00 - 09:25 | 1000 | BIO TOWERS | GROUND AND WHITE RIVER | SOUTH TOWER PUMPS KICKED OFF | OPERATOR RESET PUMPS BACK ON-LINE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-01-26 | 13:40 - 13:55 | 500 | BIO TOWERS | GROUND AND WHITE RIVER | SOUTH TOWER PUMPS KICKED OFF AGAIN COMMUNICATION ERROR WITH SYSTEM | OPERATOR RESET PUMPS BACK ON-LINE AND PUMPED WATER OUT OF AREA AND RETURNED TO SYSTEM
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-01 | 7:00A - 3:00P |  | NO RELEASE |  | REPLACING UPPER PRESSURE BELT FOR BELT PRESS #2
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-02 | 7:30A - 3:00P (2/3) |  | #1 SECONDARY CLARIFIER | #2 SECONDARY CLARIFIER | EMERGENCY BY-PASS OF #1 SECONDARY CLARIFIER | REBUILDING CLARIFIER. WILL NOT AFFECT FINAL EFFLUENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-03 | 12:00P - 3:00P |  | NO RELEASE | WHITE RIVER | TOOK SECONDARY CLARIFIER #5 OUT OF SERVICE TO DRAIN AND SWEEP LINES | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-03 | 11:57A - 12:10P | 100 | FORCE MAIN 300 E & 300 N | DITCH & STREET | FOUND WHILE REPLACING AIR RELIEF VALVE | VACUUMED OVERFLOW AND SPREAD LIME. REPAIRED FORCE MAIN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-03 | 11:00P - 7:00A (2/4) |  | CLARIFIER #3 | CLARIFIER'S 4, 5, 6 | HAD TO DRAIN #3 TO RETRIEVE A HAMMER | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-12 | 10:04A |  | NO RELEASE |  | NETWORK FAILURE CAUSED DATE LOSS | REBOOT ALL SYSTEMS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-17 | 7:00A - 3:00P |  | NO RELEASE | WHITE RIVER | REPLACED DRIVE MOTOR FOR GRAVITY BELT ON PRESS #1
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-22 | 07:38 - 09:30 | 1400000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT FLOW AT RELEASE 40.8 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-02-28 | 3:00P - 3:00P (3/3) | 0 | CLARIFIER #3 DEWEY ST. | CLARIFIERS 1, 2, 4 | TOOK CLARIFIER #3 OUT OF SERVICE TO FIX BROKEN FLIGHT CHAIN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-02 | 7A - 8A | 0 | NO RELEASE | WHITE RIVER | MECA UNIT TAKEN DOWN 30 MINS TO SWITCH OVER NEW PANEL DO NOT ANTICIPATE DATA LOSS | GENERATOR BACK UP CONTINUED P/M
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-02 | 7:00A - 12:00P |  | NO RELEASE | WHITE RIVER | POWER FAILURE - BELTS COULD NOT RUN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-04 | 1:00P - 2:00P |  | NO RELEASE | WHITE RIVER | SHUT DOWN PLANT WATER BECAUSE OF WATER LINE BREAK | FIXED BROKEN LINE. FINAL EFFLUENT NOT EFFECTED.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-07 | 14:00 - 15:00 (3/11) |  | NO RELEASE | WHITE RIVER | PRIMARY CLARIFIER #1 (DEWEY St.) OUT OF SERVICE FOR REPAIR | REPAIRING FLIGHTS, FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-10 | 07:00 - 15:00 (3/12) |  | NO RELEASE | WHITE RIVER | CONTACT TANK OUT OF SERVICE FOR REPAIR OF CRACK | REPAIRING CRACK IN WALL, FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-12 | 6:45P - 9:25P(3/14) | 38600000 | RAW WET WELL | WHITE RIVER | RAIN 2.4" | FAILURE TO MAXIMIZE RAW SHOWS ON LOG SHEETS WHICH WAS 39.4, DUE TO METER CALIBRATIONS, BELIEVED MAXIMIZED FLOW DURING BYPASS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-12 | 6:20P - 12:23P (3/15) | 25400000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 2.4" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-13 | 7:30A - 12:00P |  | NO RELEASE | WHITE RIVER | DUE TO POWER FAILURE, CPU CARD HAD TO BE RESET. | PROGRAM RESET, FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-15 | 2:30P - 8:00A (3/16) | 50 | CR 300E & CR 300N SEWER MAIN BREAK | DITCH | BROKEN PIPE | VACUUMING MATERIAL AND WILL FIX PIPE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-15 | 3:30A - 3:00P(3/17) |  | RAW WET WELL | WHITE RIVER | DURING RAW BYPASS, BAR RAKE IS GETTING HUNG UP ON SOMETHING AT BOTTOM OF RAKE | OPERATOR OPEN GATED TO BYPASS BAR RAKE AND DENS FLOW TO PRIMARIES
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-17 | 8:15A - 3:00P (3/18) |  | CONTACT TANK | WHITE RIVER | TO TANK OUT OF SERVICE TO FIX BROKEN BAFFLE | REPLACED BAFFLE; FINAL EFFLUENT NOT EFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-18 | 8:30P - 3:00P (3/19) |  | PRIMARY CLARIFIER #2 | CLARIFIERS 1, 3, 4 | PRIMARY CLARIFIER #2 TAKEN OUT FOR SERVICE TO FIX BROKEN DRIVE CHAIN | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-18 | 7:15A - 7:30A |  | NO RELEASE | WHITE RIVER | RELOCATING TWO CIRCUIT BREAKERS ON MCCA | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-22 | 0920-1120 1601-1715 | 511000 | RAW WET WELL | WHITE RIVER | RAIN EVENT 1.1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-22 | 07:30 - 19:00 (3/26) |  | NO RELEASE | BYPASS OF A TREATMENT PROCESS | PRIMARY PLANT BAR RAKE TAKEN OUT OF SERVICE FOR REPAIR | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-22 | 0656 - 1240 (3/23) | 6500000 | PRIMARY CLARIFIERS | WHITE RIVER | PARTIALLY TREATED RELEASE RAIN EVENT 1.1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-24 | 10:15 - 12:00 | 0 | NO RELEASE | BYPASS OF A TREATMENT PROCESS | TAKING DOWN NEUTRALS TO MOTORS INSTALLING NEW SWITCH GEAR | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-25 | 16:50 - 0315 (3/26) | 2900000 | PRIMARY CLARIFIERS | WHITE RIVER | PARTIALLY TREATED RELEASE RAIN EVENT .67 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-25 | 2000 - 2310 | 924000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .67" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-28 | 11:57A - 1:00P | 1000 | MH AT 2425 SHADY LANE | DITCH | LIFT STATION LOST POWER DUE TO BLOWN FUSE | PUMPED SEWAGE FROM MH AND DITCH
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-28 | 1:25A - 11:00A (3/29) | 8900000 | PRIMARY EFFLUENT | WHITE RIVER | RAIN .89" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-28 | 7:25A - 10:30A | 1000000 | RAW WET WELL | WHITE RIVER | RAIN .89" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-03-30 | 9:08A - 9:13A | 2000 | PRIMARY CLARIFIERS | WHITE RIVER | FLOW SURGE AFTER RAW SEWAGE PUMP PUT BACK IN SERVICE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-02 | 09:30 - 11:00 | 3000 | RAW SEWAGE LINE | GROUND | CONSTRUCTION HIT SEWER LINE WITH BACKHOE | CAPPED OFF LINE AND VACCED UP SPILL AND APPLIED LIME
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-05 | 20:30 - 22:55 | 750000 | PRIMARY EFFLUENT | WHITE RIVER | PARTIALLY TREATED RAIN EVENT .27 INCHES | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-06 | 2:05P - 16:00 (4/7) |  | LINE ON PLANT GROUNDS | DITCH | CONTRACTORS BROKE LINE DURING CONSTRUCTION | LIQUID PUMPED DOWN AND ALL LINES LOCATED DURING CONSTRUCTION FOR FUTURE INFORMATION
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-06 | 12:45P - 14:00 |  | NO RELEASE |  | MOO2 METER LOOP BROKEN FAILED TO COLLECT DATA | BYPASSED LOOP IN YARD (UNUSED)
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-07 | 22:05 - 08:45 (4/8) | 7900000 | PRIMARY EFFLUENT | WHITE RIVER | PARTIALLY TREATED RAIN EVENT .89 INCHES | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-07 | 22:22 - 03:40 (4/8) | 3000000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .89 INCHES | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-08 | 4:49P - 4:34P | 5000 | PRIMARY EFFLUENT | WHITE RIVER | RAW SEWAGE PUMP HAD POWER FAILURE. FLOW SURGE WHEN PUMP RESET | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-12 | 10:45A - 10:51A | 0 | NO RELEASE | WHITE RIVER | POWER CHANGE OVER, LOST DO DATA FOR SIX MINUTES | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-25 | 06:30-08:15 14:03-15:45 | 651000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .77" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-27 | 8:00A - 10:20A |  | RAW WET WELL | GRIT CHAMBER/PRIMARY'S 1,2,3,4 | BAR SCREEN UNABLE TO KEEP UP WITH INFLUENT SOLIDS SO RAISED THE BYPASS GATE | SEARCHING SEWERS FOR PROBLEM SOURCE. SHOULD NOT AFFECT FINAL EFFLUENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-04-27 | 5:30P - 12:00P (4/29) |  | DATA LOSS METERS 26 AND 49 | WHITE RIVER | EQUIPMENT FAILURE | FLOWS WILL BE AVERAGED UNTIL NEW METERS ARRIVE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-01 | 0600 - 0630 | 21000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .39" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-01 | 0530 - 0805 | 1000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .39" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-02 | 0450 - 0630 | 450000 | RAW WET WELL | WHITE RIVER | RAIN EVENT | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-02 | 2400 - 0800 |  | RAW WET WELL | GRIT CHAMBER/PRIMARY'S 1,2,3,4 | BAR SCREEN UNABLE TO KEEP UP WITH INFLUENT SOLIDS SO RAISED THE BYPASS GATE | SEARCHING SEWERS FOR PROBLEM SOURCE. SHOULD NOT AFFECT FINAL EFFLUENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-02 | 0430 - 0820 | 1900000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .59" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-03 | 20:37 - 01:45 (5/4) | 2000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .49" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-03 | 11:00 - 14:00 (5/4) |  | PRIMARY CLARIFIER #3 | PRIMARIES 1 2 &4 | TROUBLE SHOOT WHY SHORT FLIGHTS NOT TURNING ON | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-03 | 08:00 - 15:00 (6/3) |  | FINAL CLARIFIER #1 | GRIT CHAMBER | FOR TOTAL REBUILD BY MK BETTS | FLOW DIVERTED TO FINAL CLARIFIER #2 FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-03 | 21:45 - 0915 (5/5) |  | RAW WET WELL | GRIT CHAMBER/PRIMARY'S 1,2,3,4 | BAR SCREEN UNABLE TO KEEP UP WITH INFLUENT SOLIDS SO RAISED THE BYPASS GATE | SEARCHING SEWERS FOR PROBLEM SOURCE. SHOULD NOT AFFECT FINAL EFFLUENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-04 | 14:00 - 07:00 (5/7) |  | PRIMARY CLARIFIER #2 | PRIMARIES 1 3 &4 | TROUBLE SHOOT WHY SHORT FLIGHTS NOT TURNING ON | CONTINUED P/M FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-05 | 12:50 - 14:00 (5/6) |  | RAW WET WELL | GRIT CHAMBER/PRIMARY'S 1,2,3,4 | BAR SCREEN UNABLE TO KEEP UP WITH INFLUENT SOLIDS SO RAISED THE BYPASS GATE | SEARCHING SEWERS FOR PROBLEM SOURCE. SHOULD NOT AFFECT FINAL EFFLUENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-06 | 6:20P - 7:15P | 200 | M.H. 2711 WEST 18TH | STREET TO CATCH BASIN | BLOCKAGE OF GREASE, ROOTS AND DEBRIS | REMOVED BLOCKAGE WASH DOWN AND VAC OUT CATCH BASIN PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-09 | 8:00P - 3:00P (5/11) |  | PRIMARY CLARIFIER 3 | 1, 2, 4 | REPLACING DRIVE CHAIN GEARS | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-11 | 3:05A - 10:20A | 2800000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-11 | 5:15A - 8:35A | 1500000 | RAW WET WELL | WHITE RIVER | RAIN 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-12 | 11:46A - 1:10P | 175000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .30" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-13 | 6:00P - 3:00P(5/27) |  | PRIMARY CLARIFIER #1 | CLARIFIERS 2,3,4 | TROUBLESHOOTING WHY LONG FLIGHTS ARE BROKEN | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-14 | 18:09 - 18:10 | 500 | PRIMARY EFFLUENT | WHITE RIVER | POWER FAILURE | ONE MINUTE BYPASS GENERATOR IN TALKS FOR FUTURE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-17 | 10:00 - 15:00(5/21) | 0 | WWTP | NO RELEASE | TOOK RAW #2 OUT OF SERVICE | U-JOINT SHAFT IS BROKEN MK BETTS ON SITE WILL FIX ASAP
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-17 | 13:30 - 22:30 | 5400000 | RAW WET WELL | WHITE RIVER | FAILED TO MAXIMIZE FLOW CAUSE PUMP 2 OUT OF SERVICE | WAITING FOR PARTS PUMP #2
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-21 | 1:47P - 3:45P | 100 | MH AT 1502 LYNWOOD | STREET | BLOCKAGE | RESTORED FLOW, VACUUMED AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-21 | 2:14A - 5:25A | 980000 | RAW WET WELL | WHITE RIVER | RAIN .99" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-21 | 2:04A - 1:00A (5/22) | 2500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .99" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-24 | 5/25 |  | NO RELEASE |  | REPAIRING RUSTED CONVEYOR BELT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-27 | 8:24P - 10:20P | 581000 | RAW WET WELL | WHITE RIVER | RAIN 1.1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-27 | 7:54P - 11:33P | 1200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-31 | 18:40 - 21:30 | 1200000 | RAW WET WELL | WHITE RIVER | RAIN EVENT | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-05-31 | 18:20 - 23:10 | 1600000 | PRIMARY CLARIFIERS | WHITE RIVER | PARTIALLY TREATED RELEASE RAIN EVENT | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-07 | 8:30A - 3:00 (7/7) | 0 | O.S. CLARIFIER #2 | O.S. CLARIFIER #1 | REBUILDING O.S. CLARIFIER #2 | FLOW DIVERTED TO O.S. CLARIFIER #1
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-07 | 7:00A - 3:00 (6/8) |  |  |  | PRESSES UNABLE TO RUN | REPAIRED AND FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-09 | 3:52A - 10:30A | 1900000 | RAW WET WELL | WHITE RIVER | RAIN 1.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-09 | 07:00 - 15:00 (7/9) | 0 | NO RELEASE BELT PRESS DOWN |  | POLYMER PUMP NOT WORKING | MAINTENANCE STAFF WAITING ON PUMP MOTOR
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-09 | 7:00 - 13:00 (7/2) | 0 | NO RELEASE | N/A | BELT PRESS DOWN POLYMER PUMP NOT WORKING | MAINTENANCE WAITING ON PUMP
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-09 | 7:00A - 3:00P (6/15) |  | NO RELEASE | N/A | BELT PRESS #1 DOWN DUE TO POLYMER PUMP NOT WORKING | REPLACE POLYMER PUMP
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-09 | 3:26A - 12:30P | 3500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-13 | 21:50 - 22:55 | 111000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .54" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-13 | 20:55 - 12:40(6/14) | 1100000 | PRIMARY CLARIFIERS | WHITE RIVER | PARTIALLY TREATED RELEASE RAIN EVENT .54" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-14 | 21:05 - 03:00 (6/15) | 4500000 | RAW WET WELL | WHITE RIVER | RAIN EVENT 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-14 | 2050 - 1705 (6/15) | 3000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT 2.3" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-15 | 21:05 - 02:10 (6/16) | 6700000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .67" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-16 | 7:00 - 15:00 | 0 | RAW PUMP #1 | GRIT CHAMBER | WILL BE REPLACING UNIVERSAL JOINT | RAW PUMP #2 WILL ASSUME THE FLOW FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-17 | 10:00 - 15:00(6/18) |  | PRIMARY CLARIFIER 2 | PRIMARIES 1 3 4 | DRAINING SO MAINTENANCE CAN INSPECT WHY CHAIN IS OFF GEAR | MAINTENANCE ON SITE TO FIND PROBLEM
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-18 | 9:20P - 4:00P (6/19) | 3300000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.7" | FLOW WAS MAXIMIZED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-18 | 9:40A - 8:20A (6/19) | 6000000 | RAW WET WELL | WHITE RIVER | RAIN 1.7" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-19 | 2:00A - 12:00P | 1400000 | CSO 003 | WHITE RIVER | RAIN 1.7" POWER FAILURE | RESET PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-21 | 10:48A - 5:45P | 1400000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-21 | 11:20A - 1:30P | 766000 | RAW WET WELL | WHITE RIVER | RAIN 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-22 | 9:16A - 10:15A | 2000 | SSO QUINCY DR LS | GROUND | RAIN 2" | VAC TRUCK CLEANED AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-22 | 04:12 - 13:10 (6/23) | 30000000 | RAW WET WELL | WHITE RIVER | RAIN EVENT 2.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-22 | 3:52A - 8:25A (6/24) | 13300000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 2.5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-22 | 9:45A - 10:15A | 500 | SSO 27TH & RAIBLE | GROUND | RAIN 2" | JETTING LINE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-24 | 12A - 15:00 (6/25) |  | RAW WET WELL | GRIT CHAMBER | BAR RAKE GETTING JAMMED RAISED GATE TO COMPENSATE FLOW | MAINTENANCE STAFF WILL LOOK AT BAR RAKE AT 07:00 TO DETERMINE PROBLEM
IN0032478 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-25 | 8:00A - 8:20A |  | CL2 TANK | WHITE RIVER | REPLACING UNION JOINT ON HYPOCHLORITE LINE | WILL BACKWASH FILTERS TO SUBSIDE FLOW DURING REPAIR
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-26 | 20:00 - 16:00 (6/30) | 0 | NO RELEASE |  | TOOK CLARIFIER 3 OUT OF SERVICE TO REPAIR MULTIPLE SHEARED PINS | CLARIFIER 3 DIVERTED TO 4, 5, & 6
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-27 | 15:20 - 15:50 | 7000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT 1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-28 | 05:47 - 02:52 (6/29) | 1700000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT 1.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-28 | 06:03 - 15:20 | 4300000 | RAW WET WELL | WHITE RIVER | RAIN EVENT 1.9" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-06-29 | 08:00 - 15:00 (7/9) |  | SECONDARY PLANT WEST PRIMARY | GRIT CHAMBERS | TOOK OUT OF SERVICE ANNUAL PREVENTATIVE MAINTENANCE | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-05 | (7/22) |  | CSO 007 FLOW METER |  | CONSTRUCTION OF NEW SCREENING BUILDING CONTRACTORS NEED TO MOVE THE ELECTRICAL CONTROL BOX | NOTIFIED CONTRACTOR TO MINIMIZE METER DOWN TIME AND WILL CONTACT METERING COMPANY ABOUT TEMPORARY BATTERY POWERED METER
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-08 | 17:04 - 21:20 | 1400000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .88" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-08 | 17:25 - 19:10 | 785000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .88" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-08 | 19:20 - 19:30 | 0 | PRIMARY PLANT |  | POWER FAILURE AT PRIMARY PLANT | NO LOSS OF DATA ANTICIPATED FINAL EFFLUENT NOT AFFECTED BACK UP GENERATION IS PLANNED FOR FUTURE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-09 | 15:00 - 15:00 (7/23) | 0 | NO RELEASE | N/A | BELT PRESS 1 NOT WORKING | MAINTENANCE WAITING ON PUMP MOTOR TO ARRIVE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-12 | 02:24 - 09:35 | 2300000 | PRIMARY CLARIFIERS PARTIALLY TREATED | WHITE RIVER | RAIN EVENT 1.1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-12 | 02:41 - 06:45 | 2300000 | RAW WET WELL | WHITE RIVER | RAIN EVENT 1.1" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-15 | 18:30 - 20:30 | 408000 | PRIMARY CLARIFIERS PARTIALLY TREATED | WHITE RIVER | RAIN EVENT .29" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-17 | 1:15P - 2:40P | 5000 | 5901 SCATTERHELD MH | LAWN PARKING LOT | LS MALFUNCTION | TURNED OFF UPSTREAM LS REPAIRED SCATTERHELD LS VACUUM AND SPREAD LIME
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-18 | 12:07 - 12:28 | 6000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .23" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-20 | 3P - 4P (7/22) | 0 | NO RELEASE |  | UPGRADING SQL SERVERS | HONEYWELL CHART RECORDERS RUNNING IN PARALLEL
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-22 | 15:00 - 18:15 | 802000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .36" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-22 | 15:14 - 16:37 | 457000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .36" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-23 | 15:00 - 15:00 (7/28) | 0 | NO RELEASE | N/A | BELT PRESS 1 DOWN DUE TO NOT WORKING | MAINTENANCE WAITING ON PUMP MOTOR
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-24 | 6:04P - 20:20 | 50 | MH IN FRONT MAIN PLANT | GROUND | POWER WENT OUT POWER AND LIGHT PROHIBITED TURNING THE POWER BACK ON | CLEANED AREA APPLIED LIME GENERATORS ARE PART OF PHASE I IMPROVEMENTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-25 | 12:19A - 06:15 | 1300000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .37" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-25 | 12:A - 01:45 | 453000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .37" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-26 | 16:00 - 15:00 (7/30) | 0 | BYPASS OF TREATMENT PROCESS PRIMARY CLARIFIER 4 | CLARIFIERS 1, 2, 3 | DRAINING #4 FOR ANNUAL MAINTENANCE | INSPECTION CONTINUED P/M
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-28 | 15:12 - 17:55 | 500000 | PRIMARY CLARIFIERS PARTIALLY TREATED RELEASE | WHITE RIVER | RAIN EVENT .72" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-29 | 01:50 - 03:10 | 500000 | PRIMARY CLARIFIERS PARTIALLY TREATED RELEASE | WHITE RIVER | RAIN EVENT .72" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-31 | 12:35 - 15:15 | 766000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .78" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-07-31 | 12P - 17:08 | 2200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .78" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-01 | 20:34 - 15:00 (8/11) | 0 | WWTP NO RELEASE |  | TRANSFORMER A FEEDS MAIN PLANT BURNT UP | SWITCHED TO TRANSFORMER B BARTH ELECTRIC COMING TO FIX A
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-03 | 10:56A - 12:15P | 239000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .24" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-04 | 21:25 - 23:58 | 387000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .43" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-10 | 16:00 - 16:00 (8/12) | 0 | #3 PRIMARY CLARIFIER | 1,2,4 PRIMARY CLARIFIERS | ANNUAL PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-11 | 12:05P - 1:35P | 177000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .4" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-14 |  |  | GREENSBRANCH SEWER LINE | RAW WET WELL | CRACK IN LINE | UNTIL LEAK IS FIXED PUMPS WILL LIFT THE SEWERAGE DOWNSTREAM TO WET WELL CONSTRUCTION PHASE WILL LINE 96" PIPE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-14 | 8:30A - 10:10A | 1100000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .46" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-15 | 10:12A - 12:15P | 620000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .43" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-24 | 09:00 - 15:00 | 0 | #2 GRIT CHAMBER | #1 GRIT CHAMBER | GRIT SWEEP DAMAGED | BETTS ENG. ON PROJECT NO EXPECTED TO EFFECT FINAL EFFLUENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-26 | 07:00 - 15:00 (8/31) | 0 | O.S PRIMARY CLARIFIERS | INFLUENT CHANNEL AERATION BASINS | LOSS FUNCTION OF INFLUENT GATES TO CLARIFIER | INSTALLATION OF NEW GATES STAND BY PUMPS IN PLACE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-08-31 | 8:30A - 3:00P (9/1) |  | PRIMARY CLARIFIER #4 | PRIMARIES 1, 2, 3. | DRAINING #4 TO RETRIEVE BROKEN SLUDGE JUDGE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-03 | 6:20P - 7:05P | 10 | 709 MELLEN DR MANHOLE | LAWN | SEWER CLOGGED BY GREASE AND RAGS | JETTED AND PUMPED SEWER VACUUM LAWN AND SPREAD LIME FUTURE PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-06 | A - P (9/10) | 0 | CONTACT TANK | WHITE RIVER | BYPASS OF CONTACT TANK CALIBRATION OF METER 52 | DONE DURING LOW FLOW AND PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-06 | A - P (9/10) | 0 | WWTP | WHITE RIVER | REROUTING POWER CORDS | HAVE NEW POWER SOURCE IN PLACE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-07 | 06:50 - 06:58 | 0 | WWTP NO RELEASE |  | SHUT DOWN POWER TO TAKE MEASUREMENTS | BACK UP GENERATORS FOR CHEMICAL FEEDS AND PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-14 | 12:00A - 12:45A |  | NO RELEASE | WHITE RIVER | POWER OUTAGE ON CITY'S WEST SIDE | LOST 2 BLOWERS AND HALF OF BIOTOWER, EFFLUENT NOT EFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-22 | 2:25P - 5:10P | 2000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .56" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-22 | 3:10P - 3:40P | 21000 | RAW WET WELL | WHITE RIVER | RAIN .56" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-23 | 9/26/10 |  | CONTACT TANK | WHITE RIVER | CALIBRATION OF METER 52. CONTACT TANK BYPASS | DONE DURING LOW FLOW
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-28 | 10 - 15:00 | 0 | PRIMARY CLARIFIER #1 | CLARIFIERS 2, 3, 4 | WHILE INSPECTING CREW DROPPED WRENCH IN PRIMARY SO HAD TO DRAIN | MAINTENANCE CREW ON PLANT GROUNDS TO OVERSEE RETRIEVAL OF WRENCH
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-09-29 |  | 0 | BAR SCREEN | SECONDARY CLARIFIERS | BAR SCREEN REPLACEMENT | PARTS ARE ON SITE AND BETTS ENG. EST. 72 HOURS FOR PROJECT FINAL EFF. NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-02 | 12:50 - 13:50 | 515000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .46" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-06 | 8:05 | 50 | 1900 EAST 53RD MANHOLE PARKING LOT | DRIVEWAY | PRIVATE MANHOLE | ADVISED OWNER TO HAVE SEWER PUMPED AND RESTORE FLOW
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-11 | 9:00A - 3:00P (10/20) |  | BAR SCREEN AFTER SECONDARY FILTERS | NO RELEASE | REBUILDING BAR SCREEN AFTER SECONDARY CLARIFIERS | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-11 |  |  | NO RELEASE |  | METERS 51, 64, 47, 48 WILL BE OUT OF SERVICE FOR A DAY EACH TO INSTALL NEW METERS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-14 |  | 0 | MAIN PLANT LIFT STATION | NO RELEASE | TIEING IN NEW SEPTIC RECEIVING AREA 2 LARGE PUMPS WILL BE OUT OF SERVICE | PROJECT DURING LOW FLOW STAND-BY PUMPS IN PLACE AND SEWAGE PUMPER TRUCK ON SITE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-18 | (10/28) |  | 36" LINE FROM NEW RAW SEWAGE LS TIED TO EXISTING LINE TO GRIT CHAMBER | GRIT CHAMBER BY STAND BY PUMPING | 36" LINE FROM NEW RAW SEWAGE LS TIED TO EXISTING LINE TO GRIT CHAMBER | WILL USE STAND BY PUMPS FOR FOUR HOURS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-18 | 2:45P |  | NO RELEASE | NO RELEASE | SHOOK CONSTRUCTION HIT WATER LINE WHICH PROVIDES SEAL WATER PUMP | REPAIRS BEING MADE. FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-26 | 10:47A - 12:50P | 1000000 | RAW WET WELL | WHITE RIVER | RAIN .9" FAILED TO MAXIMIZE FLOW FOR 1.5 HRS DUE TO HEAVY RAIN AND LEAVES ON BAR RAKE | RAISED BAR RAKE BYPASS GATE AND TURNED ON SECONDARY RAW PUMPS TO MAXIMIZE FLOW
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-26 | 11:11A - 2:50P | 1100000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .93" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-10-26 | 1:30A - 1:45A | 106000 | RAW WET WELL | WHITE RIVER | RAIN .9" POWER FAILURE. LOST TWO RAW PUMPS AND BAR RAKE WHILE SECONDARY BYPASS PUMP KEPT RUNNING | PUMPS AND BAR RAKE RESET BY ELECTRICIANS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-04 | 19:00 - (11/8) | 0 | AERATION EFFLUENT LINE AT WWTP | HOLE IN GROUND | WAS BORER FOR SOIL SAMPLES AND HIT LINE | BETTS ENGINEERING ONSITE 11/5 NEED MORE TIME AND MATERIALS WILL BE BACK 11/8
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-15 | 8:00A - 3:00P |  | NO RELEASE | WHITE RIVER | SHUT DOWN FLOW TO CLARIFIERS AND AERATION BASINS AT SECONDARY PLANT | INSPECTING DAMAGE TO EFFLUENT LINE TO CLARIFIERS DAMAGED BY OUTSIDE CONTRACTORS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-19 | 2:50P - 3:15P | 500 | MANHOLE | GROUND | BOTH PUMPS TRIPPED OUT | RESET PUMPS, CLEANED OUT STORM SEWER
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-22 | 10:10A - 10:52A | 3000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-23 | 12:25A - 3:30A | 250000 | RAW WET WELL | WHITE RIVER | RAIN 1.2" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-24 | 4:30P - 9:10P | 1200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .66" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-25 | 12:00A - 11:30P | 10600000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-25 | 1:43A - 11:30P | 2500000 | RAW WET WELL | WHITE RIVER | RAIN 1.6" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-28 | 3:05P - 3:50P | 500 | MH MICHAEL AND HILLSIDE | DITCH | PLU TRIPPED OUT AT HARTMAN ROAD L.S. | BYPASS SEWER PUMP AREA OF OVERFLOW SPREAD LIME RESET PLU
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-29 | 23:53 - 05:05 (11/30) | 2200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .59" | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-11-30 | 12:40A - 03:00 | 230000 | RAW WET WELL | WHITE RIVER | RAIN EVENT .59" | FLOW WAS BEING MAXIMIZED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-12-11 | 19:30 - 21:50 | 322000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN EVENT .34" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-12-14 | 16:00 - 15:00 (12/17) | 0 | PRIMARY CLARIFIER 1 | PRIMARY 2, 3, 4 | OUT OF SERVICE SO STAFF CAN INSPECT WHY SHORT FLIGHTS NOT TURNING | FINAL EFFLUENT NOT AFFECTED CONTINUE PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-12-14 | 11:06A - 11:34A | 0 | DATA LOSS ON METERS 03, 18, 50 |  | CONSTRUCTION CREW BLEW BREAKER CAUSED NETWORK FAILURE | EXPLAINED POWER LIMITATIONS TO CONSTRUCTION COMPANY BATTERY P/M
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-12-21 | 3:59A - 8:15A |  | NO RELEASE | WHITE RIVER | PROCESSOR FAULTED CAUSING A FAILURE OF DATE COLLECTION | REBOOT PROCESSOR
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-12-23 | 12A - 4P (12/27) | 0 | NO RELEASE WWTP | N/A | LEVEL SENSOR COMMUNICATION CABLE CUT BY CONTRACTORS | OPERATORS ARE READING AT SCREEN CONTRACTORS ARE TO REPAIR LINE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2010-12-23 |  | 0 | TEN DAY NOTICE SECONDARY CLARIFIER #1 | SECONDARY CLARIFIER #2 | CONTRACTOR REPLACING MOTOR AND GEAR BOX | FINAL EFFLUENT NOT AFFECTED
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-22 | 12:00A - ONGOING | 2900000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | SNOWMELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-23 | 12:00A - ONGOING | 3400000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | SNOWMELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-24 | 12:00A - ONGOING | 4900000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-26 | 12:00A - ONGOING | 2120000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-27 | 12:00A - ONGOING | 1470000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-29 | 12:00A - 11:59P | 3423000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SNOW MELT. SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW. | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-30 | 12:00A - 11:59P | 1574000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SNOW MELT. SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-01-31 | 12:00A - 11:59P | 1427000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SNOW MELT. SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW. | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-01 | 12:00A - 11:59P | 1410000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-02 | 12:00A - 11:59P | 1342000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-05 | 12:00A - 11:59P | 1320000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-06 | 12:00A - 11:59P | 1100000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-07 | 12:00A - 11:59P | 771000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-09 | 12:00A - 11:59P | 1000000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS USING OPERATIONAL STRATEGY
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-10 | 12:00A - 11:59P | 856000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS USING OPERATIONAL STRATEGY
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-11 | 12:00A - 11:59P | 795000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-12 | 12:00A - 11:59P | 833000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-13 | 12:00A - 11:59P | 641000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-14 | 12:00A - 11:59P | 601000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-15 | 12:00A - 11:59P | 758000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-17 | 12:00A - 11:59P | 849000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-18 | 12:00A - 11:59P | 694000 | EQ BASIN OVERFLOW/OUTFALL #001 | BIG DUCK CREEK | SECONDARY CLARIFIER GEAR BOX FAILURE. UNABLE TO TREAT MAXIMUM FLOW | PULLED GEAR BOX AND SENT TO SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-21 | 12:00A - ONGOING | 2375000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN .19 INCHES SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-22 | 12:00A - ONGOING | 4710000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | RAIN .10 INCHES SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-23 | 12:00A - ONGOING | 3758000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-24 | 12:00A - ONGOING | 2564000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-25 | 12:00A - ONGOING | 2073000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-26 | 12:00A - ONGOING | 1334000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-27 | 12:00A - ONGOING | 900000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-02-28 | 12:00A - ONGOING | 1191000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-01 | 12:00A - ONGOING | 1521000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-02 | 12:00A - ONGOING | 2559000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-03 | 12:00A - ONGOING | 2133000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-04 | 12:00A - ONGOING | 1818000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-05 | 12:00A - ONGOING | 1574000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-06 | 12:00A - ONGOING | 2818000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-07 | 12:00A - ONGOING | 1822000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-08 | 12:00A - ONGOING | 1741000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | SNOW MELT | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-09 | 12:00A - ONGOING | 1642000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-11 | 12:00A - ONGOING | 1101000 | EQ BASIN OVERFLOW/OUTFALL #101 PARTIALLY TREATED | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION AND MIXING PUMPS OF EQ BASIN TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-12 |  | 4300000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN 1.03" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-13 |  | 6350000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .64" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-14 |  | 6100000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-15 |  | 5700000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-16 |  | 4800000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-17 |  | 3521000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-18 |  | 2300000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-19 | 12:00A - ONGOING | 1930000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-20 | 12:00A - ONGOING | 1130000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-21 | 12:00A - ONGOING | 1150000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-22 | 12:00A - ONGOING | 5110000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION .78 INCHES | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-23 | 12:00A - ONGOING | 3900000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION .78 INCHES | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-24 | 12:00A - ONGOING | 2880000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION .78 INCHES | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-25 | 12:00A - ONGOING | 3730000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-26 | 12:00 - ONGOING | 3200000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-27 | 12:00 - ONGOING | 2600000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-28 | 12:00 - ONGOING | 6100000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-29 | 12:00P - ONGOING | 5649000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | SIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-30 | 12:00P - ONGOING |  | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-03-31 | 12:00P - ONGOING |  | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURN FLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-04-01 | 12:00P - ONGOING | 1390000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-04-02 | 12:00P - ONGOING | 1140000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-04-03 | 12:00P - ONGOING | 953000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-04-04 | 12:00P - ONGOING | 894000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-04-05 | 12:00P - ONGOING | 670000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-04-06 | 12:00P - ONGOING | 1800000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN .24" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-04-08 | 12:00P - ONGOING | 820000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN .09" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-13 | 12:01A - ONGOING | 1600000 | EQ BASIN OVERFLOW/OUTFALL 001 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-17 | 12:01A - ONGOING | 2300000 | EQ BASIN OVERFLOW OUTFALL #101 | BIG DUCK CREEK | RAIN .54" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-18 | 12:01A - ONGOING | 3000000 | EQ BASIN OVERFLOW OUTFALL #101 | BIG DUCK CREEK | RAIN .09" AND PROBLEM WITH DRIVE ON SECONDARY CLARIFIER OVERLOADING | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE AND PULLED DRIVE UNIT FOR REPAIR
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-19 | 12:01A - ONGOING | 2500000 | EQ BASIN OVERFLOW OUTFALL #101 | BIG DUCK CREEK | PROBLEM WITH DRIVE OVERLOADING | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE AND DRIVE IN SHOP FOR REPAIRS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-20 | 12:01A - ? | 3130000 | EQ BASIN OVERFLOW/ OUTFALL #001 | BIG DUCK CREEK | RAIN .61" NORTH SECONDARY CLARIFIER OUT OF SERVICE | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE. REPAIRING DRIVE UNIT.
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-21 | 12:00A - STILL OVERFLOWING | 5120000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-22 | 12:00A - STILL OVERFLOWING | 2590000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-23 | 12:00A - STILL OVERFLOWING | 2700000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-24 | 12:00A - STILL OVERFLOWING | 1900000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-25 | 12:00A - STILL OVERFLOWING | 1462000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-27 | 12:00A - STILL OVERFLOWING | 1247000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-28 | 12:00A - ON GOING | 100000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-30 | 12:00A - ON GOING | 500000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-05-31 | 12:00A - ON GOING | 5000000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-01 | 12:00A - ON GOING | 5488000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-02 | 12:00A - ON GOING | 4400000 | EQ BASIN OVERFLOW/OUTFALL #101 | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE DUE TO DRIVE CONTROL | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-03 | 12:00A | 2061000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN. SECONDARY CLARIFIER OUT OF SERVICE | FIXED DRIVE CONTROL. NORTH SECONDARY CLARIFIER BACK IN SERVICE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-08 | 12:01A | 3500000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .78" | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-10 | 12:01A - | 2000000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-11 | 12:01A - ONGOING | 2300000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .11" | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-12 | 12:01A - ONGOING | 1100000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .15" | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-13 | 12:01A - ONGOING | 1200000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .14" | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-14 | 12:01A - ONGOING | 4600000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN 1.42" | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-15 | 12:01A - ONGOING | 6230000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN 1.42" ADDITIONAL .14" | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-17 | 12:01A - ONGOING | 3500000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OF AERATION AND MIXING PUMPS TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-18 | 12:00A | 3700000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-19 | 12:00A | 4900000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-20 | 12:00A | 3600000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-21 | 12:00A | 5550000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .46" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-22 | 12:00A | 8300000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN 2.56" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-22 |  | 500000 | MANHOLE | GROUND | RAIN 2.56" ELWOOD WATER UTILITY DRAINING TOWER | MH COVER BARRICADED ST.; REQUESTED UTILITY STOP DRAINING TOWER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-23 | 12:00A - |  | EQ BASIN OVERFLOW | BUG DUCK CREEK | RAIN .44" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-24 | 12:00A - | 5596000 | EQ BASIN OVERFLOW | BUG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-25 | 12:00A - ONGOING | 4800000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-26 | 12:00A - ONGOING | 3400000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .32" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-27 | 12:00A - ONGOING | 3800000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN .70" | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-27 | 12:00A - ONGOING | 3400000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-28 | 7A - 9:30A |  | MH | GROUND | PRECIPITATION .7" | REPLACED MH COVER AND WEIGHED DOWN WITH CONCRETE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-29 | 12:00A - ONGOING | 4800000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-06-30 | 12:00A - ONGOING | 4200000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-07-01 | 12:00A - ONGOING | 2848000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-07-02 | 12:00A - ONGOING | 1700000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-07-03 | 12:00A - ONGOING | 1100000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-07-04 | 12:00A - ONGOING | 500000 | EQ BASIN OVERFLOW | BIG DUCK CREEK | PRECIPITATION | TURNED OFF AERATION & MIXING PUMPS IN CELL OF EQ BASIN WITH OVERFLOW TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2010-08-23 | 8:30A - 1:30P | 20000 | SEWER MAIN | BIG DUCK CREEK | DISCHARGE PIPE CRACKED BELOW SEWAGE LEVEL | SEPTIC HAULER PUMP OUT PIT REPLACED ONE PUMP AND INSTALL NEW PIPE
IN0049026 | FALL CREEK RSD STP | MADISON | 2010-06-22 | 8:30A |  | BABY FARMS LS, SR 13 LS, CR 100 LS | DITCH, LICK CREEK | RAIN 2.56"
IN0049026 | FALL CREEK RSD STP | MADISON | 2010-06-22 | 8:30 |  | COUNTY ROAD 100 LS | FALL CREEK | RAIN 2.56" MH UNDER WATER | LINE MH
IN0049026 | FALL CREEK RSD STP | MADISON | 2010-06-22 | 8:30 |  | BABY FARMS LS | SIDE DITCH | RAIN 2.56" MH UNDER WATER | LINE MH
IN0049026 | FALL CREEK RSD STP | MADISON | 2010-06-22 | 12:15P |  | PENDLETON MAIN LS | FALL CREEK | RAIN 2.56"
IN0049026 | FALL CREEK RSD STP | MADISON | 2010-06-22 |  |  | STATE ROAD 13 LS | SIDE DITCH LICK CREEK | RAIN 2.56" MH UNDER WATER | LINE MH
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-03-13 | 7:00P - 11:00P |  | SSO #003 | PIPE CREEK | RAIN 2.1"
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-03-13 | 7:00P |  | SSO #003 | PIPE CREEK | RAIN 2.1"
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-06-01 | 4A - 5P (6/2) |  | SSO #3 | PIPE CREEK | 2.5 INCHES RAIN IN 48 HOURS
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-06-14 | 10:00P - 3:00A (6/18) |  | SSO 003 | PIPE CREEK | RAIN 2"
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-06-14 | 10P - |  | SSO #3 | PIPE CREEK | 1.8" RAIN IN LESS THAN 48 HOURS
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-06-21 | 8:00P |  | SSO #003 | PIPE CREEK | RAIN 3.5"
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-06-22 | 8:00P - 2:00P (6/23) |  | SSO #003 | PIPE CREEK | RAIN 3.5"
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-06-27 | 8P - 1A (7/1) |  | SSO # 3 | PIPE CREEK | 2.3" RAIN IN LESS THAN 24 HOURS
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2010-08-04 | 7:30P - 2P (8/6/) |  | SSO #3 | PIPE CREEK | 1.2" RAIN IN LESS THAN 12 HOURS | BLOCKAGE REMOVED
IN0020087 | LAPEL MUNICIPAL STP | MADISON | 2010-06-12 | 9:30A - 9:50A |  | MH ON GOLF COURSE NEAR PLANT | GROUND | POWER FAILURE GENERATOR STARTED BUT PUMPS DID NOT B/C DAMAGED PLC UNIT | IMMEDIATE RESPONSE BY PERSONAL RESET PUMP CONTROLS REPLACE PLC UNIT RESEARCH BETTER SURGE PROTECTION
| LAPEL MUNICIPAL STP | MADISON | 2010-06-22 | 8:45A - 2:15P |  | N. MAIN & FORD ST. LS, 300S @ MONTGOMERY FARMS LS | GROUND | RAIN 2.2" | PLANT RUNNING AT FULL CAPACITY
IN0024562 | SUMMITVILLE MUNICIPAL STP | MADISON | 2010-05-31 | 9P - 5:30A (6/1) | 300 | M.H. SOUTH RAILROAD AVE. | GROUND STORM SEWER | RAIN 3.2 INCHES 48 HOURS | AREA SOUTH EAST PART OF LONG TERM CONTROL PLAN
IN0024562 | SUMMITVILLE MUNICIPAL STP | MADISON | 2010-06-14 | 10P - 6A (6/15) | 168000 | MH 7TH & WALNUT, S. RAILROAD , 6TH &MILL ST, PROSPECT STREET, BOTH CSO OUTFALLS | STREET STORM SEWER | MORE THAN 1.5" OF RAIN | SYSTEM FULL LONG TERM CONTROL PLAN FUNDING IN THE WORKS FOR PROJECT
IN0024562 | SUMMITVILLE MUNICIPAL STP | MADISON | 2010-06-21 | 8:30A - 2p (6/22) |  | MH 7TH & WALNUT, MH RAILROAD & JOHN, MH 6TH & MILL | GROUND | RAIN 1.5"
IN0024562 | SUMMITVILLE MUNICIPAL STP | MADISON | 2010-08-04 | 8P - 7:30A (8/5/10) | 38600 | LS #2 CSO #004 MAIN STREET FISH KILL 8/17/10 | DAISY BLACK DITCH | 24" DITCH FROM COUNTY WITH WASTE | PUMPED WATER OUT REMOVED TOP LAYER OF SLUDGE LTCP INCLUDES UPGRADING THIS LS
IN0023183 | BELMONT AWT | MARION | 2010-01-21 | 7:40P - 9:15P |  | SOUTHERN AVE CSO 117 |  | RAIN
IN0023183 | BELMONT AWT | MARION | 2010-03-13 | 8:30P - 1:15A(3/14) | 8580000 | 2700 S. BELMONT AVE. OUTFALL 007 | WHITE RIVER | RAIN .25" | BOTH BASINS FULL BEFORE OVERFLOW
IN0023183 | BELMONT AWT | MARION | 2010-03-17 | 10:00A - 10:15A | 3000 | HUDNUT BLVD AND ACTIVATOR | SOIL AND ABANDONED CLARIFIER | PIPE SPLIT NEAR REPAIR CLAMP | PUMPING SUSPENDED, AREA VACTORED, PIPE CAPPED
IN0023183 | BELMONT AWT | MARION | 2010-06-19 | 4:30A - 7:20P |  | 2700 S. BELMONT AVE. OUTFALL 007 | WHITE RIVER | RAIN | EQUALIZATION BASINS USED FOR STORAGE
IN0023183 | BELMONT AWT | MARION | 2010-08-17 | 11:45A - 11:46A | 225 | WEST OF DEWATERING | PARKING LOT, EAGLE CREEK | CONTRACTOR SEPARATED TEMP BYPASS LINE | DIRECTED SPILLED LIQUID TO PLANT DRAIN, SANDBAGGED DRAIN TO CREEK
IN0023183 | BELMONT AWT | MARION | 2010-10-28 | 5:30A - 6:00A | 600 | BELMONT AWT, WEST OF DEWATERING | PARKING LOT | SLUDGE LINE BECAME PRESSURIZED DURING PROCESS CHANGE | VACTORED LIQUID FROM PARKING LOT
IN0023183 | BELMONT AWT | MARION | 2010-11-11 |  |  | BELMONT AWT, WEST OF DEWATERING | GROUND | ABANDONED SLUDGE LINE CAP FAILED AND LEAKED THICKENED SECONDARY SLUDGE | SPILLED LIQUID VACTORED OFF GROUND, LINE TO BE EXCAVATED
IN0023183 | BELMONT AWT | MARION | 2010-11-25 | 8:30A - 1:00A(11/26) | 50790000 | OUTFALL 007 | WHITE RIVER | RAIN | ALL AVAILABLE EQUIPMENT WAS OPERATING AND EQUALIZATION BASINS WERE USED FOR STORAGE
IN0021300 | CUMBERLAND MUNICIPAL STP | MARION | 2010-03-26 | 4:00P - 6:30P | 2000 | MH W84 629 WASHINGTON COVE WAY | CUMBERLAND CREEK | LINE BLOCKAGE | LINE CLEARED; AREA AROUND MH AND CREEK CLEANED
IN0021300 | CUMBERLAND MUNICIPAL STP | MARION | 2010-08-07 | 12P - 4P | 100 | NORTH GERMAN CHURCH FORCE MAIN | GROUND | CONSTRUCTION RELATED WORK ON US 40 AND GERMAN CHURCH ROAD | AREA CLEANED AND FORCE MAIN REPAIRED
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-05 | 7:45P - 10:17P | 30 | 8805 SUNBOW DR. 750318 | LOT/YARD/FIELD | DEBRIS IN LINE | CLEANED SEWER AND FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-06 | 6:59P - 8:52P | 300 | 7900 W 56TH LS112 | DITCH TO EAGLE CREEK | PIPE COLLAPSE | EXCAVATE AND REPAIR SEWER
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-10 | 10:15P - 10:30P | 3000 | 2700 S BELMONT AVE | GROUND | EQUIPMENT FAILURE END CAP ON DISTRIBUTION ARM ON BIO ROUGHING FILTER CAME OFF | FLOW TO TOWER WAS REDUCED AND ARM END CAP WAS REPLACED WITH ORIGINAL PART BOLTS TIGHTENED INSPECTION OF ARMS ARE DONE WEEKLY
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-13 | 12:45P - 2:50P | 10 | 8738 LOG RUN DR S | STREET | LS FORCE MAIN RUPTURE | EXCAVATE AND REPAIR SEWER, NEW FORCE MAIN GOING IN
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-15 | 12:35P - 2:15P | 488 | 1831 TEMPERANCE AVE. | LOT | DEBRIS | CLEANED SEWER BLOCKAGE, REMOVE DEBRIS, FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-16 | 4:00P - 10:15A (1/17) | 5348 | 42 N. LAWNDALE | LYNN CREEK | PIPE COLLAPSE | CLEAN SEWER BLOCKAGE EXCAVATE AND REPAIR SEWER
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-26 | 9:36A | 25 | ASSET # 151605 2210 EAST 36TH STREET | LOT FIELD | GREASE BLOCKAGE | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-27 | 11:28A - 2:32P | 3595 | 8530 DEPOT DR. | DITCH PLEASANT RUN | GREASE | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-01-30 | 6:30A - 11:31A | 100 | 7840 W 56TH ST | STREET - EAGLE CREEK | LIFT STATION FORCE MAIN RUPTURE | EXCAVATE AND REPAIR SEWER. PLAN REPLACEMENT OF FORCE MAIN
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-02-05 | 4:27P - 4:40P | 127 | 5599 DANDY TRAIL ASSET ID #LS113 | LOT/FIELD | LIFT STATION FORCE MAIN RUPTURE | EXCAVATE SOIL AND REPAIR SEWER
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-02-07 | 2:00P - 4:33P | 1495 | 4822 N BOLTON AVE ASSET ID #171265 | STREET | GREASE BLOCKAGE | CLEAN SEWER BLOCKAGE REMOVE DEBRIS FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-02-08 | 2P - 10A (2/11) |  | SOUTHPORT ROAD FLOW CONTROL BOX | SOIL AROUND STRUCTURE | PIPE SEAL IS LEAKING BETWEEN CONDUIT AND STRUCTURE | PIPE AND JOINT INCASED IN CONCRETE COLLAR INSPECT IN NEXT FEW MONTHS
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-02-14 | 1:03P - 4:20P | 50 | 8850 BOWEN RD | LOT | GREASE | CLEANED DEBRIS AND FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-02-16 | 10:30A - 12:31P | 25 | 6155 E. 86TH ST | LOT | PIPE COLLAPSE | CLEANED DEBRIS AND FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-02-23 | 11A - 1P | 352 | 1229 TAYLOR DR E ASSET ID # 330178 | STREET | DEBRIS BLOCKING LINE | CLEAN SEWER BLOCKAGE REMOVE DEBRIS AND AREA CLEANING
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-03-06 | 3:45P - 6P | 659 | 4801 TEMPE CT ASSET ID# 770194 | STORM STRUCTURE WHITE RIVER | DEBRIS | FLUSH AREA REMOVE DEBRIS CLEAN AREA AND T.V.
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-03-11 | 11A - 1:55P | 171 | 4751 CENTURY PLAZA RD ASSET ID#820878 | LOT/FIELD | GREASE BLOCKAGE | CLEAN SEWER BLOCKAGE REMOVE DEBRIS FLUSH AREA AND AREA CLEANING AND REPORT TO OES
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-03-20 | 3:30P - 4:58A (3/21) | 1500 | 7628 ALMADEN CT ASSET ID #LS201 | LOT EAGLE CREEK | LS FORCE MAIN RUPTURE | EXCAVATE AND NEW FORCE MAIN BEING INSTALLED
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-03-25 | 12:09P - 1:45P | 2813 | 5515 PLEASANT HILL CIR | LOT/BIG EAGLE CREEK | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-03-26 | 12:26A - 2:06A | 2400000 | 2700 SOUTH BELMONT AVENUE OUTFALL 007 | WHITE RIVER | WET WEATHER | ALL AVAILABLE EQUIPMENT OPERATING CITY IS PLANNING AN UPGRADE IN LTCP
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-04-08 | 4:15P - 5:55P | 200 | 7953 ZIONSVILLE RD | SPILL CONTAINED | PRIVATE CONTRACTOR DAMAGE | EXCAVATE AND REPAIR SEWER
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-04-08 | 5:05P - 6:40P (4/6) | 1856 | 5702 SIMMUL LN | DITCH | GREASE | FLUSHED AREA, CLEANED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-04-08 | 4:26A - 5:46A | 470000 | 2700 SOUTH BELMONT AVENUE | WHITE RIVER | WET WEATHER EVENT | ALL AVAILABLE EQUIPMENT WAS OPERATING AND EQUALIZATION BASIN WERE FULL
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-04-12 | 2:35P - 6:05P | 75 | 1319 MUNSEE CIR ASSET ID#930738 | LOT | DEBRIS | REMOVE DEBRIS FLUSH AREA AND AREA CLEANING AND T.V.
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-04-12 | 9:19P - 10:50P | 89 | 5316 WEST SOUTHERN AVENUE ASSET ID #770145 | LOT | GREASE | REMOVE DEBRIS FLUSH AREA AND AREA CLEANING AND T.V.
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-04-14 | 2:50P - 5P | 635 | 5316 WEST SOUTHERN AVENUE ASSET ID #770145 | LOT | GREASE | REMOVE DEBRIS FLUSH AREA AND AREA CLEANING AND T.V.
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-02 | 4:15A - 8:30A |  | 2700 BELMONT AVENUE OUTFALL 008 | WHITE RIVER | WET WEATHER EVENT IN COUNTY | ALL RAW PUMPS RUNNING BOTH BASINS FULL UPGRADE IS IN LTCP
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-04 | 10:50P - 2A (5/5) | 2784 | 7926 CENTERSTONE WAY | FIELD & BUCK CREEK | L.S. INSTRUMENTATION FAILURE | REPAIR L.S.
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-17 | 7:07A - 12:46A (5/18) | 20 | 5341 EAST THOMPSON ROAD ASSET L.S. 316 | PAVED AREA | L.S. VALVE MALFUNCTION | REPAIR L.S. AND REMOVE DEBRIS
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-20 | 1:15P - 2:14P | 100 | 3102 MERTS DR | LOT | ROOTS | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-20 | 5:00P - 6:10P | 1368 | 2901 S. KEYSTONE | BEAN CREEK | DEBRIS | CLEANED BLOCKAGE AND FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-21 | 11:45A - 1:57P | 2579 | 3215 JOEY WAY | SEERLEY CREEK | GREASE | CLEANED BLOCKAGE AND FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-21 | 11:45A - 1:57P | 2579 | 3215 JOEY WAY | STORM STRUCTURE SEERLEY CREEK | GREASE BLOCKAGE | CLEAN SEWER BLOCKAGE FLUSH AREA AND T.V. LINES
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-05-27 | 6:43P - 11P | 2511 | 6840 GUNNERY ROAD ASSET #900011 900003 | LOT YARD EAGLE CREEK | PRIVATE CONTRACTOR DAMAGE | EXCAVATE & REPAIR SEWER CLEAN AND T.V AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-13 | 10:55P - 11:08P | 10000 | 2700 SOUTH BELMONT AVE. | WHITE RIVER | WET WEATHER EVENT IN COUNTY | ALL AVAILABLE EQUIPMENT WAS OPERATING AND EQ BASIN WERE USED FOR STORAGE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-14 | 7:50P - 12:15P (6/15) | 16150000 | 2700 S BELMONT AVE | WHITE RIVER | WET WEATHER EVENT IN COUNTY | ALL AVAILABLE EQUIPMENT OPERATING AND EQ BASIN USED FOR STORAGE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-15 | 8:55P - 2A (6/16) | 7450000 | 2700 SOUTH BELMONT AVE. | WHITE RIVER | WET WEATHER EVENT IN COUNTY | ALL AVAILABLE EQUIPMENT WAS OPERATING AND EQ BASIN WERE USED FOR STORAGE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-16 | 12:13P - 12:17 | 1000 | 4241 SPRINGWOOD | CROOKED CREEK | RAIN .26" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-16 | 12:22P - 12:26P | 1000 | 4235 SPRINGWOOD | CROOKED CREEK | RAIN .26" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-19 | 11:45A - 9:00A (6/20) | 186823 | 4241 SPRINGWOOD CT | DITCH | RAIN 1.27" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-19 | 11:45A - 9:00A (6/20) | 24910 | 4235 SPRINGWOOD TRAIL | DITCH | RAIN 1.26" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-20 | 11:00A | 25000 | 5764 COBURN | CROOKED CREEK | RAIN 1.26" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 2:05P - 10:11A (6/23) | 23562 | 2263 COUNTY CLUB | DITCH | RAIN 2.58" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 1:05P - 7:00 (6/24) | 368517 | 6716 CREEK BAY DR | LITTLE BUCK CREEK | RAIN 4" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 3:32A - 7:16A (6/23) | 325096 | 1830 WINCHESTER | CROOKED CREEK | RAIN 4.67" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 1:20A -1:44A | 352 | 5507 STATE ST. | BUCK CREEK | RAIN 4"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 8:25A -7:11A (6/23) | 266876 | 3160 W 79TH | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 8A - 7:11 (6/23) | 27176 | 1320 MUNSEE CIRCLE | CROOKED CREEK LOT FIELD | PRECIPITATION 2.19" WET WEATHER | REMOVE DEBRIS AND FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 11:00A 12:00P (6/23) | 43958 | 4408 BRITTANY | LITTLE EAGLE CREEK | RAIN 2.88"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 3:32A - 7:16A (6/23) | 16255 | 1920 WINCHESTER | LICK REEK | RAIN 4.67" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:49A - 7:11A (6/23) | 27391 | 1701 W 66TH ST. | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:56A - 7:11A (6/23) | 27254 | 6601 GRANDVIEW DR | CROOKED CREEK | RAN 2.19"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 6:28A - 6:38A (6/23) | 28329 | 2018 MAC CT | BEAN CREEK | RAIN 3.58" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 8:01A - 7:11A (6/23) | 135782 | 7041 GRANDVIEW | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:45P - 9:42 (6/23) | 8176 | 6475 EXCALIBUR CT | LOT | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 2:20P - 7:55A (6/23) | 2061 | 4108 BISCAYNE | FIELD CREEK | RAIN 1.82" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 3:32A - 7:16A (6/23) | 32510 | 1736 WINCHESTER | LICK CREEK | RAIN 4.67" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:47A - 7:11A (6/23) | 342875 | 6500 GRANDVIEW DR | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:13A - 9:29P | 25 | 8635 ADMIRALS WOODS | GEIST RESERVOIR | RAIN 4" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:23A - 7:11A (6/23) | 13949 | 4225 SPRINGWOOD | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 11:00A - 12:00P (6/23) | 43958 | 4408 BRITTANY RD | LITTLE EAGLE CREEK | RAIN 2.88"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 6:00A - 6:45A | 220 | 1237 BUTTER NUT | WHITE LICK CREEK | RAIN 4"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 9:29P - 7:13A | 25 | 8635 ADMIRALS WOOD DR | LOT GEIST RESERVOIR | LS WET WEATHER CAPACITY | REMOVE DEBRIS FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 12:50A - 6P (6/23) | 191780000 | BELMONT AVENUE | WHITE RIVER | WET WEATHER EVENT | ALL AVAILABLE EQUIPMENT OPERATING EQ BASINS USED FOR STORAGE INDIANAPOLIS PLANNING ON UPGRADING
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 6:23P - 1:32P (6/23) | 11224 | 3934 DAHOMA DR | DITCH | RAIN 4" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:50A - 7:11A (6/23) | 68428 | 1733 W 66TH ST. | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 9:00A - 8:30A (6/23) | 206604 | 7611 BROOKVIEW | HOWLAND DITCH | RAIN 2.3" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 6:26A - 6:38A (6/23) | 141839 | 2594 HARLAN | BEAN CREEK | RAIN 3.58" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 5:30P - 6:38A (6/23) | 115464 | 3532 WOODCLIFF | BEAN CREEK | RAIN 3.58" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 10:20A - 11:40A | 3907 | 3833 ST SIMONS CT | LOT | RAIN 4"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 6:24A - 6:38A (6/23) | 38407 | 2601 KEYSTONE | BEAN CREEK | RAIN 3.58" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:35A - 7:11A (6/23) | 345806 | 5800 COBURN | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 9:11A - 8:30A (6/23) | 204992 | 4355 E. 75TH ST | HOWLAND DITCH | RAIN 2.3" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 7:23A - 7:11A (6/23) | 139494 | 4241 SPRINGWOOD | CROOKED CREEK | RAIN 2.19" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 10:00A - 6:38A (6/23) | 1000 | 2437 BEECHCREST | BEAN CREEK | RAIN 3.58" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 6:20A - 6:38A (6/23) | 284850 | 3121 E BRADBURY | BEAN CREEK | RAIN 3.58" | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 1:40P - 7:16A (6/23) | 257889 | 8326 DELAWARE ST | BUFFALO CREEK | RAIN 4.67"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-22 | 6:57A - 7:00A (6/24) | 422440 | 6927 ARJAY DT | BUCK CREEK | RAIN 4" PUMP FAILURE | REMOVE DEBRIS, REPAIR LIFT STATION
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-23 | 7:14P - 8:46P | 899 | 6844 ARJAY DR | LITTLE BUCK CREEK | RAIN 2.88"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-23 | 6:38A - 10A | 1000 | 2437 BEECHCREST DR | STREET BEAN CREEK | WET WEATHER I & I CONTRIBUTION | REMOVE DEBRIS FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-23 | 1:19P - 8:46P | 20 | 8665 ADMIRALS WOODS | LOT | RAN 2.88"
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-24 | 6:47P - 9:27P | 313 | 1429 BROOKSIDE PKWY | POGUES RUN | DEBRIS | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-26 | 8P - 10:16P (6/27) | 30790 | 7100 RALSTON AVENUE ASSET ID #LS504 | PAVED AREA WHITE RIVER | LS INTERNAL PIPE FAILURES | REMOVE DEBRIS REPAIR LS RUN LS MANUAL
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-28 | 3:30P - 4:34P | 1250 | 5910 WINSTON DRIVE MH ASSET ID #170938 | STROM STRUCTURE DEVON CREEK | DEBRIS WASHED INTO SIPHON BARRELS | FLUSH AREA CLEAN SEWER & TV
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-28 | 9:15A - 10:16P | 20 | 6845 SHORE ISLAND DRIVE ASSET ID #185023 | STREET | LS INTERNAL PIPE FAILURE | REMOVE DEBRIS REPAIR LS RUN LS MANUAL
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-06-28 | 8A - 7:16A (6/29) | 1000 | 8409 STEN COURT ASSET ID #510956 | LOT YARD | WET WEATHER | REMOVE DEBRIS FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-01 | 11:15A - 11:19 | 1000 | 8627 LOG RUN DRIVE SOUTH | LOG RUN STORM STRUCTURE | LS INSTRUMENTATION FAILURE | REMOVE DEBRIS, CLEAN SEWER, FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-07 | 11A - 1:45P | 161 | 6720 W 79TH STREET ASSET ID #900068 | LOT YARD | LS ARV FAILURE | REMOVE DEBRIS FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-08 | 11:29A - 1:30P | 2364 | 6304 COMMONS DRIVE ASSET ID #831300 | YARD | GREASE | CLEAN SEWER BLOCKAGE FLUSHED AREA TV AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-16 | 11A - 12:15P | 733 | 2490 POST DR | STORM STRUCTURE RETENTION POND | GREASE BLOCKAGE | BLOCKAGE IN MAIN CAUSED LATERAL UPSET CLEAN AND FLUSH SEWER TV. LINES
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-20 | 22:50 - 00:15A | 2360000 | 2700 SOUTH BELMONT 007 | WHITE RIVER | WET WEATHER EVENT IN COUNTY | ALL AVAILABLE EQUIPMENT WAS OPERATING EQ BASINS WERE USED
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-21 | 6:09P - 7:10P | 1030000 | 3800 W SOUTHPORT ROAD | LITTLE BUCK CREEK | WET WEATHER EVENT IN COUNTY | ALL AVAILABLE EQUIPMENT WAS OPERATING EQ BASINS WERE USED
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-22 | 10:36A - 11:30A | 106 | 3067 BALTIMORE AVE | LOT | UPSTREAM MH FULL OF STICKS AND TRASH | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-24 | 16:57 - 17:45 | 1100000 | BELMONT RAW OVERFLOW
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-07-25 | 10:27A - 10:38A | 50 | 8635 ADMIRALS WOODS DR | LOT | LS INSTRUMENTATION FAILURE | REMOVE DEBRIS REPAIR LS AND RUN LS ON HAND
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-07 | 5:06P - 7:03P | 2286 | 5750 MCCLOUD CT | LIBERTY BRANCH | GREASE | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-09 | 11:00A - 12:30P | 1319 | 2241 RACEWAY | LICK CREEK | GREASE | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-09 | 2:00P - 3:14P | 361 | 5128 E STOP 11 | RETENTION POND | DEBRIS | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-10 | 6:00A - 11:15P | 1000 | 3900 MILLERSVILLE RD | FALL CREEK | WATER MAIN BREAK
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-17 | 9:50A - 11:15A | 4152 | 2629 PLAZA DR. | CROOKED CREEK | GREASE | REMOVED DEBRIS, FLUSHED AREA, EXCAVATE SOIL
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-23 | 1:15P - 1:16P | 50 | BELMONT AWT | PARKING LOT | CONTRACTORS HOSE SEPARATED FROM FITTING | EMPLOYEES CONTAINED SPILL AND VACTORED OFF CONTRACTOR WAS ASKED TO INSPECT ALL HOSES AND INSURE ALL IN GOOD WORKING CONDITION
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-24 | 10:30A - 12:14P | 305 | 6211 EAST HAMPTON DRIVE | STORM STRUCTURE TO DEVON CREEK | GREASE | REMOVE DEBRIS AND FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-08-24 | 7:20P - 9:55P | 151 | 2380 EAST 54TH STREET | STORM STRUCTURE TO WHITE RIVER | GREASE | REMOVE DEBRIS AND FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-09-09 | 9:50A - 11:08A | 381 | 7563 CHERRY HILL DR. | STORM STRUCTURE, EAGLE CREEK | GREASE | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-09-10 | 11:30A - 2:30P | 527 | 2161 BOULEVARD | FALL CREEK | PIPE COLLAPSE | EXCAVATE AND REPAIR SEWER
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-09-23 | 9P - 9:17P | 1661 | 500 EAST FALL CREEK PKWY ASSET #CSO059 | STORM STRUCTURE FALL CREEK | WATER MAIN BREAK
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-09-23 | 9P - 9:27P | 2638 | 535 EAST FALL CREEK PKWY ASSET #CSO061 | STORM STRUCTURE FALL CREEK | WATER MAIN BREAK
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-10-04 | 3:13P - 4:27P | 5422 | 8904 BASH STREET | DITCH RETENTION POND | L.S. INSTRUMENTATION FAILURE | FLUSH AREA REPAIR L.S.
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-10-05 | 2:44P - 3:43P | 1441 | 8440 MICHIGAN ROAD ASSET ID # 952482 | STORM STRUCTURE RETENTION POND | PRIVATE L.S. LOWES L.S. OFF AND NOT WORKING | CLEANED BLOCKAGE REMOVED DEBRIS SANITARY SEWERS ASSERTED WRONG LINES ARE PRIVATE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-10-07 | 2:00P - 2:15P | 15 | 6910 WILDWOOD CT | LOT | DEBRIS | CLEANED SEWER BLOCKAGE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-10-12 | 10:00A - 11:16A | 223 | 4116 REDFERN DR. | STORM STRUCTURE/LICK CREEK | ROOTS | CLEANED SEWER BLOCKAGE. FLUSHED AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-10-20 | 2:40P - 5:40P | 176 | 9002 GINNYLOCK DRIVE LS#549 | LOT YARD | L.S. FORCE MAIN RUPTURE | EXCAVATE AND REPAIR SEWER
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-10-25 | 12:25P - 3:00P | 10 | 3105 N ALTON AVE | PAVED AREA | GREASE | REMOVE DEBRIS, CLEAN SEWER, FLUSH AREA
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-10-29 | 3:56P - 5:53P | 571 | 1716 MINTURN LANE | LOT TO CROOKED CREEK | DEBRIS BLOCKAGE | CLEANED SEWER BLOCKAGE FLUSH AREA AND AREA T.V.ING
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-11-08 | 2:30P - 7:05P | 1343 | 1700 IRON LIEGE RD | LOT/YARD/FIELD | LS FORCE MAIN RUPTURE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-11-15 | 18:10 - 20:10 | 1800000 | BELMONT AWT | WHITE RIVER | HIGH VOLUME LEAVES CAUSE BAR SCREEN FAILURE | HAD TO PINCH MAIN INFLUENT TO CLEAN SCREENS
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-11-17 | 13:45 - 13:50 | 2000 | CONCORD ROAD NORTH OF BANTA | FIELD | MAIN CONVEYING SLUDGE SPRUNG A LEAK | VACTOR TRUCK USED TO CLEAN AREA EXPOSED AND REPAIRED PIPE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-11-19 | 2:25P - 7:00P | 537 | 7350 EAGLE BEACH DR. | DITCH | LS FORCE MAIN RUPTURE | EXCAVATE AND REPAIR SEWER
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-11-28 | 9:52P - 10:31P | 9524 | 7899 FENNWAY AVE. ASSET ID# 905204 | HOWARD JOHNSON DITCH | GREASE BLOCKAGE | CLEAN SEWER REMOVE DEBRIS FLUSH ARE AND T.V. LINE
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-12-01 | 14:00 - 14:30 | 1500 | CONCORD RD NORTH OF BANTA ROAD | FIELD | SLUDGE LEAK FORCE MAIN BETWEEN SOUTHPORT AND BELMONT | VACTOR USED TO CLEAN AREA PIPE WILL BE REPAIRED
IN0023183 | INDIANAPOLIS DPW & UWS (WWTP) | MARION | 2010-12-07 | 1:04P - 1:43P | 190 | 7171 TWIN OAKS | PAVED AREA | GREASE IN CITY MAIN | REMOVED DEBRIS, FLUSHED AREA
IN0039608 | LAWRENCE, CITY OF | MARION | 2010-03-01 | 1:46P - 2:35P | 100 | FORCE MAIN AT 7156 INDIAN LAKE WEST DR | GROUND | FORCE MAIN BREAK FROM POWER FAILURE | REMOVED BAD SECTION OF FORCE MAIN, REPAIRED AND CLEANED AREA
| LAWRENCE, CITY OF | MARION | 2010-06-22 | 10:30A |  | MH @ 45TH AND CLINTON | STREET | RAIN 4.3" | CLEAN AREA WHEN FLOODING CEASES
| LAWRENCE, CITY OF | MARION | 2010-06-22 | 11:15A | 50 | LS 10 7103 OAKLANDON | GROUND | RAIN 4" | SAND BAG AROUND LS
| LAWRENCE, CITY OF | MARION | 2010-06-22 | 8:40A |  | 9000 46TH ST. | GROUND & STORM SEWER | RAIN 3" | SAND BAG AROUND MH
| LAWRENCE, CITY OF | MARION | 2010-06-22 | 10:00A - 1:45P | 6500 | MH @ 12406 SYCAMORE | GROUND | RAIN 4.3" | SAND BAG AND VAC TRUCK
| LAWRENCE, CITY OF | MARION | 2010-07-17 | ? - 10:30 (7/19) | 75000 | 11402 EAST 79TH MH | GROUND TO NORTH BRANCH CREEK | LIFT STATION FAILED SCADA DID NOT SEND ALARMS | SAND BAGGED AREA CLEAN UP SEWAGE TOOK DO READINGS LIMED AREA CONTACTED SCADA CONTRACTOR
| LAWRENCE, CITY OF | MARION | 2010-07-20 | 9:15P - 4:30A | 2000 | 46TH AND POST MH | STREET | HEAVY RAINS 2" | BARRICADED AREA AND CLEANED WITH VAC TRUCK
| LAWRENCE, CITY OF | MARION | 2010-07-20 | 9:15P - 4:30A | 1500 | 45TH AND CLINTON MH | STREET | HEAVY RAINS 2" | BARRICADED AREA AND CLEANED WITH VAC TRUCK
| LAWRENCE, CITY OF | MARION | 2010-08-08 | 10:50A - 11:30A | 75000 | 5205 MITTHOEFER MH | STORM SEWER | LS FAILED DUE TO POWER FAILURE AND SYSTEM SURCHARGED | SANDBAGGED ENTRANCE STORM SEWER AND SET OF GENERATOR AT LS PLAN TO INSTALL ON SITE GENERATOR IN 2011
IN0023183 | SOUTHPORT AWT | MARION | 2010-10-27 |  | 100 | WEST PRIMARY INFLUENT WET WELL | SOIL ALONG EFFLUENT CHANNEL | DISCHARGE HOSE SPRAYED ON TO SIDEWALK AND OPEN CHANNEL | REMOVED TWO INCHES OF SOIL FROM EAST END OF CHANNEL AND CLEANED SIDEWALK
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-01-18 | 11:00A - 11:30A | 15000 | DEWATERING OPERATION, MAIN ST. PROJECT | DRAINAGE DITCH | PLUG IN SANITARY SEWER GAVE WAY, RUNNING RAE SEWAGE INTO DEWATERING WELL | STANDING WATER IN DITCH REMOVED WITH VACTOR TRUCK AND AREA LIMED
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-14 | 3:45P - 6:45P | 5000 | CHAPEL HILL L.S. 6821 W 10TH STREET | STORM SEWER | POWER FAILURE | DEBRIS CLEANED BACK UP GENERATOR IS IN OUR CURRENT 5-YR CAPITAL IMPROVEMENT PLAN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | 6508 WEST 13TH STREET MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | 1219 THORNDALE MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | DORIS DRIVE & BUICK MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 12:45A - 8:45A (6/23) | 480000 | CHAPEL HILL LS | STORM SEWER | RAINFALL VERY INTENSE 3.5" | TRASH AND DEBRIS CLEANED UP SEWER SYSTEM IS CURRENTLY BEING EVALUATED BY ENGINEER
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | 6729 DORIS DRIVE MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | 16TH STREET& FARLEY DRIVE MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | 16TH STREET & THORNDALE MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | 6605 DORIS DRIVE MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | DORIS DRIVE & FARLEY DRIVE MH | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | CHAPEL HILL LS | GROUND | 2.52" RAIN
IN0032972 | SPEEDWAY MUNICIPAL STP | MARION | 2010-06-22 | 7A- |  | 6705 DORIS DRIVE MH | GROUND | 2.52" RAIN
IN0049436 | SPRING VALLEY MHC | MARION | 2010-10-31 | 4:00P - 12:00P (11/2) |  | 8820 PENDLETON PIKE SITE 730 | GROUND | 4 INCH PIPE BROKE | CLEANED AND DISINFECTED AREA, PUT NEW PVC IN PLACE
IN0032972 | TOWN OF SPEEDWAY | MARION | 2010-01-05 | 9:00A - 11:30A | 110000 | SECONDARY BYPASS OUTFALL #001 | CHLORINE CONTACT TANK | BYPASS PUMPING SYSTEM FROZE DURING SEWER SEPARATION PROJECT CAUSING INTERCEPTOR TO BACK UP | PUMPING SYSTEM RESTORED. CONTRACTOR TO PROVIDE 24 HR MONITORING, HEAT WRAPPED FLOATS, AUTOMATIC DIALER ALARM SYSTEM
IN0032972 | TOWN OF SPEEDWAY | MARION | 2010-01-05 | 9:00A - 11:00A | 20000 | CSO #002 | BIG EAGLE CREEK | OCCURRED WHEN PUMPING SYSTEM RESTORED AND INTERCEPTOR PUMPED TO WWTP
| TOWN OF SPEEDWAY | MARION | 2010-08-31 | 7:45A - 8:45A | 100 | 14TH ST AND MAIN BYPASS LINE | GROUND | CONSTRUCTION | HYDRO EXCAVATED; AREA LIMED
IN0022438 | BOURBON MUNICIPAL STP | MARSHALL | 2010-05-21 | 5:35P - 8:00P | 188000 | LIFT STATION SSO #003 | TRIBUTARY TO BAKER DITCH | RAIN 3.4" | MAXIMUM PUMPING
IN0022438 | BOURBON MUNICIPAL STP | MARSHALL | 2010-11-01 | 7:27A - 7:59A | 60 | MH #158 | STORM SEWER BASIN TO ERWIN DITCH | PLUGGED SEWER MAIN STICKS AND CLOTHING | JET RODING AND MONITOR SEWERS NEAR HALLOWEEN
IN0020247 | BREMEN_MUNICIPAL STP | MARSHALL | 2010-09-29 |  | 0 | BIO-TOWER SOUTH | BIOTOWER NORTH | ANTICIPATED BYPASS TO RECAULK AND PRE-TENTATIVE MAINTENANCE | ALL FLOW WILL STILL GO THROUGH NORTH TOWER
IN0040223 | LAPAZ MUNICIPAL STP | MARSHALL | 2010-03-24 | ? - 6:20P |  | FORCE MAIN FROM LS | GROUND AND UNKNOWN DITCH | FORCE MAIN CAME APART AT OLD REPAIR SITE | LS TURNED OFF VACTOR AND HAUL TO PLANT WAS REPAIRED
IN0021539 | CRANE NSWC | MARTIN | 2010-02-15 | 11:30P - 8:20A | 10000 | LIFT STATION #2 DOWN HILL FROM WATER PLANT | GROUND, BOGGS CREEK FEEDER | BLOWN CONTROL FUSE IN PUMP PANEL | PUMPED LEVEL DOWN TO STOP OVERFLOW, REPAIR ALARM SYSTEM
IN0021539 | CRANE NSWC | MARTIN | 2010-05-12 |  | 30000 | LS 17 & 48 | STREAM AND GROUND | RAIN 2.5" | PUMP TRUCKS ON SITE TO REDUCE VOLUME
IN0021539 | CRANE NSWC | MARTIN | 2010-06-19 | 4:15A - 4:45A |  | LIFT STATION | GROUND | RAIN 1.2" | USED VAC TRUCKS TO CONTROL FLOW
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2010-02-09 | 01:00 - 08:00 (2/10) | 1000 | MANHOLE 171 | GROUND DRY RAVINE | SEWER LINE BLOCKAGE | TV LINE AND DO ADDITIONAL SEWER CLEANING AND MAINTENANCE
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2010-06-15 | 22:20 - 02:45 (6/16) |  | PLANT | BOGGS CREEK | PLANT SUFFERED LIGHTENING STRIKE GENERATOR FAILED TO ENERGIZE | REPAIR GENERATOR CHLORINE PUMP, FINAL CLARIFIER DRIVES
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2010-06-28 | 00:05 - 08:45 |  | WWTP BLENDED WITH FINAL EFFLUENT | BOGGS CREEK | 1.75" RAIN IN 45 MINUTES | ALL FLOW WAS TREATED INCLUDING DISINFECTION PRIOR TO DISCHARGE
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2010-07-08 | 08:00 - 10:30 | 3000 | FORCE MAIN AIR VENT VALVE EAST LS 17 | STREAM GROUND BOGGS CREEK FEEDER | BROKEN VALVE | LS SHUT DOWN PUMPING WITH VAC TRUCK EXCAVATE AND REPAIR STRUCTURE
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2010-07-15 | 21:00 - 23:35 | 3500 | LS 6 | GROUND | POWER FAILURE | PUMPED AND HAULED TO WWTP UNTIL POWER WAS RESTORED
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2010-07-20 | 06:00 - 08:30 | 3000 | LS 17 & 48 | GROUND | TORRENTIAL RAINS 1.23" | BOTH PUMPS ON HAND PUMP TRUCK ONSITE TO REDUCE VOLUME ENGINEER REVIEWING OPTIONS TO DETERMINE I & I
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2010-11-25 | 08:00 - 16:00 |  | L.S. 34 | GROUND | PRECIPITATION 4.3" | SEWER CREWS HAD PUMPER TRUCKS TO PULL EXCESS AND DUMP BUT COULD NOT KEEP UP WITH RAINFALL
IN0024902 | GRISSOM WWTP | MIAMI | 2010-06-21 | 11:45A - 5:25P |  | MH AT THULE ST | STORM DRAIN | RAIN | MAXIMIZING FLOW IN SEWER AND WASTEWATER PLANT
IN0024902 | GRISSOM WWTP | MIAMI | 2010-11-10 | 8:00A - 11:00A | 180 | MH @ CANNON CIRCLE | STORM DRAIN | PLUGGED SEWER | UNPLUGGED SEWER AND JETTED LINE
IN0032328 | PERU MUNICIPAL STP | MIAMI | 2010-04-12 | 8:00A - 9:15A | 0 | CSO 16 | WABASH RIVER | PLUG IN SEWER LINE | CREWS REMOVED BLOCKAGE, NO DISCHARGE
IN0024902 | PERU UTILITIES GRISSOM DIV. | MIAMI | 2010-06-14 | 2:30 - 6 (6/15) | 10000 | MH THULE CT | STORM DRAIN | HEAVY RAINS 1.78" TOTAL THIS MONTH 7.1" | MAXIMIZING FLOW TO PLANT TO EMPTY COLLECTION SYSTEM
IN0035718 | BLOOMINGTON | MONROE | 2010-06-19 | 5:55A - 9:00A | 12155 | GIFFORD RD MH 3437 | SINKING CREEK | RAIN | AREA CLEANED OF DEBRIS
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2010-03-25 | 11P - 1A (3/26) | 16050 | GRIMES LANE MH #6 | CLEAR CREEK | PRECIPITATION | AREA WAS CLEANED OF DEBRIS UNDER AN AGREED ORDER
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2010-05-17 | 2P - 4:15P | 31725 | GIFFORD ROAD MH #3437 | SINKING CREEK | PRECIPITATION | AREA WAS CLEANED OF DEBRIS UNDER AN AGREE ORDER HAVE WET WEATHER PLAN
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2010-06-07 | 5:30P - 7P | 21150 | GIFFORD RD MH 3437 | SINKING CREEK | GREASE CAUSED OVERFLOW | AREA WAS CLEANED OF DEBRIS
IN0035218 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2010-06-15 | 8:33P - 9:22P | 21886 | GIFFORD RD MH 3437 | SINKING CREEK | PRECIPITATION .56" | AREA WAS CLEANED OF DEBRIS
IN0054992 | COTTONWOOD MOBILE HOME PARK | MONTGOMERY | 2010-03-13 | 5:00P - 9:00P | 200 | LIFT STATION | GROUND | FORCE MAIN PLUGGED UP | WILL REPLACE FORCE MAIN FROM STATION TO PLANT; AREA AROUND LS CLEANED AND LIMED
IN0038806 | CRAWFORDSVILLE ELECTRIC | MONTGOMERY | 2010-01-19 | ? - 9:15A |  | FORCE MAIN | WHITLOCK SPRINGS | FROZEN LINE CAUSED COUPLING TO SPREAD ON THE FORCE MAIN | FORCE MAIN REDIRECTED TO SECONDARY SETTLING POND
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-01-03 | 7:40P - 8:10P | 50 | 509 SOUTH WALNUT LATERAL | BASEMENT | SEWER BACK-UP | CLEARED BLOCKAGE INFORMED RESIDENT OF BACK FLOW VALVE
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-02-10 | 1A - 1:40A | 0 | 915 WEST MAIN STREET | BASEMENT | BLOCKAGE DUE TO GREASE | BLOCKAGE CLEARED NOTIFIED HOMEOWNER IN NEED OF BACK FLOW VALVE
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-05-17 | ? - 1:50P | 20 | 1008 WEST MARKET STREET | BASEMENT | BLOCKAGE | OWNER DOES NOT HAVE REQUIRED BACK-FLOW DEVICE, HOMEOWNER HAD LATERAL ROTO-ROOTERED AND THAT CAUSED BACK UP
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-06-14 | 8:30P - 9:30P | 100 | MH AT PARK ON MILL STREET | GROUND | RECEIVED 1.8" RAIN IN 40 MINS | CLEANED AND LIME APPLIED ALSO TWO INLETS HAVE BEEN DISCOVERED ON THIS LINE AND ALSO GOING TO LIEN TE SEWER
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-06-21 | 10:30 | 7000 | MH @ PARK AND MILL ST., SUGAR CREEK LS | GROUND | RAIN 2.75" POWER FAILURE
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-06-22 | ? - 6:00P | 200 | LS | BASEMENT | RAIN 2.75 | WILL ASSIST IN CLEAN UP AND LIME
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-06-22 | 6P | 200 | 900 904 COTTAGE STREET COTTAGE LS | BASEMENT | EXCESSIVE RAIN 2.75" POWER FAILURE | OFFERED LIME TO HOMEOWNER DOES NOT HAVE BACK FLOW VALVE AS REQUIRED BY CITY ORDINANCE
IN0032964 | CRAWFORDSVILLE MUNICIPAL STP | MONTGOMERY | 2010-06-22 | 4P | 50 | 705 JOHN STREET | BASEMENT | EXCESSIVE RAIN 2.75" POWER FAILURE | OFFERED LIME TO HOMEOWNER DOES NOT HAVE BACK FLOW VALVE AS REQUIRED BY CITY ORDINANCE
IN0022721 | DARLINGTON MUNICIPAL STP | MONTGOMERY | 2010-07-09 | 12A - 1:15A | 1000 | DARLINGTON LS #1 | GROUND | FREQUENCY DRIVES TRIPPED OUT | CONSTRUCTION COMPANY HAS NOT PROGRAMMED ALARMS
IN0022721 | DARLINGTON MUNICIPAL STP | MONTGOMERY | 2010-07-23 | 5A - 7A | 2000 | LS #1 | GROUND | FREQUENCY DRIVES TRIPPED OUT CONSTRUCTION COMPANY HAS NOT PROGRAMMED ALARMS | ADDED LIME TO AFFECTED AREA CONSTRUCTION CO. CORRECT ALARM SYSTEM
IN0040274 | LINDEN MUNICIPAL STP | MONTGOMERY | 2010-06-22 | 6A - 3:50P (6/23) |  | EQ BASIN | STODDARD DITCH TO WEA CREEK TO WABASH RIVER | FACILITY RECEIVED 4.04" RAIN IN APPROX 6 HOURS | PROCESS MAXIMUM VOLUME BYPASS REMAINDER TO EQ TANK FOR UV
IN0040274 | LINDEN MUNICIPAL STP | MONTGOMERY | 2010-06-22 | 6A - ONGOING |  | EQ BASIN | STODDARD DITCH TO WEA CREEK TO WABASH RIVER | RECEIVED 4.04" IN 6 HOURS | PROCESSING MAXIMUM VOLUME THROUGH PLANT REMAINDER VOLUME THROUGH EQ BASIN AND UV HIRED INDY FIRM TO EXPAND FACILITY
IN0040711 | LITTLE RACCOON RSD | MONTGOMERY | 2010-02-05 | 8P - 10:30 | 1000 | LIFT STATION 4 | STREAM | SNOW STORM BROUGHT DOWN LARGE TREE ON POWER LINES | SPRAYED AREA WITH BLEACH
IN0020504 | WAYNETOWN MUNICIPAL STP | MONTGOMERY | 2010-06-19 | 8:00A - 6:00A | 7920 | MH #2 | STREAM BOTTOM | RAIN 3" | SPREAD LIME ON OVERFLOW AREA
IN0020524 | WAYNETOWN MUNICIPAL STP | MONTGOMERY | 2010-06-22 | 6:00A - 6:00P (6/24) | 36000 | MH #2 | GRASSY STREAM BOTTOM | RAIN 3" | AREA TO BE CLEANED
IN0020524 | WAYNETOWN MUNICIPAL STP | MONTGOMERY | 2010-06-22 | 6:00A |  | MH #2 | GRASSY STREAM | RAIN 3" | CLEAN AREA WHEN FLOODING CEASES
IN0040771 | WINGATE MUNICIPAL STP | MONTGOMERY | 2010-03-14 | 4:00P - 10:00P | 50000 | WEST HIGH ST LS AND EAST MAIN ST LS | GROUND | RAIN 2.5" | LIMED AREA
| WINGATE MUNICIPAL STP | MONTGOMERY | 2010-06-22 | ? - 8:45P (6/23) | 55000 | LS MAIN ST. | GROUND | RAIN 3.5" | TREATED AREA WITH LIME
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2010-05-02 | 4:30A - 5:30A |  | #76 | WHITE LICK CREEK | RESET KICKED OUT LEFT ONLY ONE PUMP RAIN 2.5" | RESET BREAKER AND TOOK SOME TIME TO CATCH UP WITH THE FLOW
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2010-06-14 | 6:25A - 9:10A |  | #32 | WHITE LICK CREEK | RAINFALL 3"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2010-06-14 | 5A - 8:30A |  | #76 | WHITE LICK CREEK | RAINFALL 3" STARTER WENT OUT | REPLACE STARTER
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2010-06-22 | 8:10A - 9:30A |  | MH #76 | WHITE LICK CREEK | RAIN 2"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2010-08-26 | 8:45A - 8:55A | 300 | #99 | STORM DRAIN | MAIN PLUGGED | USED VAC TRUCK TO CLEAN MAIN
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2010-11-15 | 8:30A - 8:30A (11/16) | 25000 | WWTP PARTIALLY TREATED RELEASE | WHITE LICK CREEK | COMPUTER CHIP OUT | HUT OFF AIR LET SETTLE THEN DECANT ALLOW TO FILL UP AGAIN SHUT OFF AIR AND DECANT
| MAPLETURN UTILITIES INC | MORGAN | 2010-07-13 | 3P - 7A (7/14) | 24000 | MH FOXCLIFF ESTATES | LAKE IN FOXCLIFF ESTATES | LS FAILED TO ENERGIZE DUE TO BLOWN FUSE | GENERATOR IS BUDGETED FOR 2011 REPAIRING SCADA
IN0020303 | MARTINSVILLE MUNICIPAL STP | MORGAN | 2010-04-29 | 10:15A - 2:10P | 1200 | 37 & ROGERS RD | GROUND | FORCE MAIN TURNED OFF FOR GAS CONSTRUCTION PIPE HIT BY BACK HOE DRAINING WHAT WAS LEFT IN MAIN | REPAIRS MADE AND LIME ON WET SURFACES WILL HAVE UPDATED SEWER MAPS FROM MILLER PIPE WHEN WORK IS COMPLETE
IN0020303 | MARTINSVILLE MUNICIPAL STP | MORGAN | 2010-05-05 | 10A - 11A |  | 829 PLAZA DRIVE GRAVITY MAIN | GROUND | LEAKING PIPE | REPAIRED PIPE VAC UP SEWAGE AND APPLIED LIME
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2010-04-08 | 7:00A - 8:00P |  | LS SR 32 | GROUND TO STREAM | RAIN 1.4" PUMP #2 WAS IN TIMEOUT FAULT DUE TO STORM | RAN PUMP IN MANUAL MODE THROUGH DAY
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2010-05-12 | AM - 1:00P |  | LS AT BELFIELD ON 252 | GROUND TO STREAM | RAIN 1" PUMP IN TIMEOUT FAULT DUE TO LIGHTENING STORM | PUMP TURNED TO MANUAL OVERRIDE
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2010-06-20 | 5:00P - 6:00P |  | LS @ 252 HWY | GROUND TO STREAM | RAIN 2.75" POWER FAILURE
IN0020664 | AVILLA MUNICIPAL STP | NOBLE | 2010-06-01 | 6P - 8P | 30000 | M.H. WEST OF 4TH ST. L.S. | ELEY DITCH | RAIN 2.5" NORTH END OF TOWN | RESIDUE WILL BE CLEANED UP INVESTIGATING POSSIBLE SOURCES OF INFILTRATION
IN0020664 | AVILLA MUNICIPAL STP | NOBLE | 2010-12-18 | 3:30P - 4:30P | 300 | MH WEST OF 4TH ST LS | GROUND | FLOAT MALFUNCTIONED | MANUALLY PUMPED LS. REPLACED FLOAT.
IN0021814 | CROMWELL MUNICIPAL STP | NOBLE | 2010-02-17 | 1:30P - 1:45P | 3900 | HATCHERY LIFT STATION | PARKING LOT | OVERLOADED CIRCUIT TRIPPED BREAKER TO PUMP CONTROLS | CLEANED PARKING LOT. SEPARATE CIRCUIT FROM CONTROLS
IN0021814 | CROMWELL MUNICIPAL STP | NOBLE | 2010-05-21 | 4:37P - 8:59P | 20000 | MH @ 12A | GROUND | RAIN 4"
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-02-09 | 1:30P - 2:30P | 4000 | CSO #009 |  |  | CONTACTED CITY ENGINEER WORKING WITH WATER DEPARTMENT TO FIND SOLUTION
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-06-01 |  |  | CSO #7 DRY WEATHER |  | POWER FAILURE BREAKER OVERHEATING AND TRIPPING | ELECTRICIAN DETERMINED THERE ARE TOO MANY BUILDINGS AND EQUIPMENT ON BREAKER
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-06-18 | 7:30P - 7:20A (6/19) | 256000 | CSO #7 |  | LIGHTENING STRIKE NO POWER SO PUMPS SHUT DOWN ALSO KNOCKED OUT THE AUTO DAILER | REPLACED MICROLOGIC PROGRAMMER
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-07-18 | 7:15P - 8P | 24000 | CSO #7 |  | PUMP FAILURE | HAD TWO LOANER PUMPS RUNNING WAS NOT ABLE TO KEEP UP PUMPS IN FOR REPAIR
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-07-24 | 12P - 1:30P | 37000 | CSO #9 |  | WATER DEPARTMENT BACKWASHED | MAYOR AND ENGINEER WERE INFORMED IT NEEDS TO BE RESOLVED
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-07-25 | 12:30p - 1:40 | 1000 | CSO #2 | ELKHART RIVER | BUILT UP GREASE | JET RODDING OF 3 SECTIONS AND REMOVED GREASE AREA WILL BE ADDED TO MAINTENANCE CLEANING SCHEDULE
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-08-03 | 12:15P - 1P | 6000 | CSO #9 |  | WATER DEPARTMENT BACKWASHED | ISSUE IS UNDER CONTINUING CONSIDERATION BY THE ENGINEER AND MAYOR
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-09-27 | 8:30A - 3P | 10000 | 100 BLOCK OF CAVIN STREET PARKING LOT | ELKHART RIVER | PIPE FAILURE IN TWO LOCATIONS HYDRAULIC HEAD PRESSURE | DIG UP AND REPAIR FAILED PIPE AND BYPASS TRAILER SET UP ONSITE TO BYPASS THIS FAILED SECTION PIPE
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-10-13 | 4:30P - 5:45P | 1000 | CSO #9 | ELKHART RIVER | BACKWASHING OF FILTERS
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-11-04 | 10:15A | 23000 | CSO 009 | ELKHART RIVER | CITY WATER DEPARTMENT BACK WASHED THE PLANT FILTER
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-11-17 | 4:15A - 7:15A | 43000 | 007 |  | POWER FAILURE AND BACK UP SUPPLY POWER FAILED | NEW POWER SUPPLY ORDERED AND INSTALLED AND MONTHLY CHECK WILL BE IMPLEMENTED
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-11-23 | 11:30A | 11000 | CSO 009 |  | CITY WATER DEPARTMENT BACK WASHED THE PLANT FILTER | POTW HAS MEETING WITH ENGINEER DEC. 22 TO DISCUSS FUTURE OPTIONS
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-12-09 | 11:30A | 23000 | PLANT FILTER | CSO 009 | WATER DEPARTMENT BACK WASHED PLANT FILTER CAUSING CSO DISCHARGE
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2010-12-29 | 3:30P | 32000 | CSO 009 |  | WATER DEPARTMENT BACK WASHED PLANT FILTER | MEET WITH CITY ENGINEER ON DEC. 22
IN0021229 | WOLCOTTVILLE MUNICIPAL STP | NOBLE | 2010-01-17 | 8:00A - 6:30A (1/18) | 139000 | FINAL EFFLUENT LIFT STATION (2 MILES WEST OF CITY) | ROAD DITCH AND FARM LAND | RESET FLOAT ON LIFT STATION MALFUNCTIONED | LIFT STATION BYPASSED UNTIL REPAIRED
IN0024431 | RISING SUN MUNICIPAL STP | OHIO | 2010-03-13 | 8:00A - 8:02A | 30 | MH 0-1 BY LIFT STATION | GROUND | BLOCKAGE IN PUMP | TURNED OFF PUMPS AND JETTED LINE
IN0024431 | RISING SUN MUNICIPAL STP | OHIO | 2010-05-10 | 3:15 | 20 | MANHOLE 01 BY LIFT STATION | GROUND | CONTRACTOR KICKED OUT PUMPS AND DID NOT RESET; GREASE | CLEANED MH AND LINE
IN0024431 | RISING SUN MUNICIPAL STP | OHIO | 2010-10-29 | 8:45A - 9:00A | 15 | 406 4TH STREET BASEMENT DRAIN | FLOOR | ROOTS IN LINE | JETTED LINE
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-04-08 | 7A - ONGOING |  | JOSEPH INDUSTRY #004 | FIELD TO LICK CREEK | PRECIPITATION 1.25 " | CLEAN UP AND APPLY LIME ALL RAW PUMPS UP AND RUNNING
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-04-08 | 7:00A - 8:00P |  | JOSEPH INDUSTRY #004 WILLOW CREEK ROAD | LICK CREEK | RAIN 1.25" | CLEAN AND APPLY LIME
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-05-02 | 8:30A - 2:45P (5/3) |  | JOSEPH INDUSTRY #4 WILLOW CREEK RD | FIELD TO LICK CREEK | PRECIPITATION 2.39" IN LAST TWO DAYS | CLEAN UP SITE ALL PUMPS RUNNING
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-05-21 | 7:00P - 7:00A (5/22) |  | NEAR 711 W. MAIN ST. #006 | YARD, LICK CREEK | RAIN 1.1" | WILL APPLY LIME
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-06-15 | 9:30P - 10P |  | NEAR 711 WEST MAIN STREET #006 | YARD 50 FT FROM LICK CREEK | LOCAL FLOODING HEAVY RAIN SHORT TIME .95" | ALL RAW PUMPS UP AND RUNNING
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-08-09 | 2:30P - 3P |  | 711 WEST MAIN STREET #006 | YARD LICK CREEK | OBSTRUCTION CAUSED BY SHOP RAGS | WILL CLEAN UP AND APPLY LIME ALL RAW PUMPS RUNNING
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-08-26 | 1:30P - 2P |  | 711 WEST MAIN STREET 006 | YARD TO LICK CREEK | TOWEL CAUSED AN OBSTRUCTION | LET SITE DRY UP WILL CLEAN UP AND THEN APPLY LIME
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-10-20 | 11:40A - 11:50A |  | NEAR 711 W. MAIN ST. #006 | YARD, LICK CREEK | SHOP RAGS CAUSED OBSTRUCTION | WILL APPLY LIME TO CLEAN AREA
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-11-01 | 2:30P - 3P (11/3) |  | 711 WEST MAIN STREET #006 | YARD TO LICK CREEK | CONSTRUCTION COMPANY HIT MAIN WATER LINE BACK FLOW PRESSURE CAUSED OVERFLOW AT ROYER HOME | OVERFLOW WAS CLEAN WATER WILL LET SITE DRY UP AND APPLY LIME CONSTRUCTION SHOULD BE DONE ANY DAY NOW
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-11-25 | 9:30A - 10:30A (11/26) |  | JOSEPH INDUSTRY #4 WILLOW CREEK ROAD | FIELD TO LICK CREEK | PRECIPITATION 4.01" | CLEAN UP SITE AND APPLY LIME ALL RAW PUMPS UP AND RUNNING
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2010-11-30 | 8:30A - 8:30A (12/1) |  | JOSEPH INDUSTRY #4 WILLOW CREEK ROAD | FIELD TO LICK CREEK | PRECIPITATION 1.71" | CLEAN UP AND APPLY LIME ALL RAW PUMPS UP AND RUNNING
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2010-06-14 | 7:10P - 7:40P | 5000 | STRAWBERRY ROAD L.S. | GROUND | POWER OUTAGE DUE TO SEVERE STORM | PERSONAL WAS ON SITE TO ENSURE BOTH PUMPS RESTARTED WHEN POWER RESUMED L.S WILL BE REPLACED DURING UPCOMING AWARDED PROJECT
INM082901 | CANNELTON, CITY OF | PERRY | 2010-01-11 | 11:45A - 12:30P |  | FORCE MAIN RIVER ROAD | GROUND | HOLE IN FORCE MAIN | REPAIRED HOLE WITH STAINLESS STEEL BAND
INM082901 | CANNELTON, CITY OF | PERRY | 2010-02-17 | 9:00A - 9:15A |  | FORCE MAIN ON RIVER ROAD | GROUND | HOLE ON FORCE MAIN | SEALED HOLE WITH STAINLESS STEAL REPAIR CLAMP
IN0021016 | TELL CITY MUNICIPAL STP | PERRY | 2010-04-08 | 3A - 7A | 5000 | MANHOLE ON MOZART 18TH AND 19TH | STREET | SEVERE STORMS HEAVY GREASE CHUNKS 1.8" | SEWER RODDED TO CLEAR GREASE WILL INCREASE PREVENTATIVE MAINTENANCE
IN0021016 | TELL CITY MUNICIPAL STP | PERRY | 2010-05-05 |  |  | 1410 12TH STREET AND 131 BURGLIN HILLS DR | BASEMENT | SEVERE PRECIPITATION 5.3" 4/30/10 - 5/2/10 | WORKING ON LTCP AND CONSTRUCTION IN PROGRESS
IN0021016 | TELL CITY MUNICIPAL STP | PERRY | 2010-12-01 | 8:34A - ? |  | PLANT OUTFALL | OHIO RIVER | APPROVED ANTICIPATED BYPASS | PERMIT LIMITS ARE BEING MET
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-03-26 | 8:20A - 8:45A | 143 | 355 MIDWAY MANHOLE # M-0144 | GROUND | BLOCKAGE IN SEWER MAIN | ALL SOLIDS COLLECTED AND DISPOSED OF AT PLANT SEWER MAIN WILL BE CLEANED AND TV
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-04-16 | 11:45A - 11:46A | 100 | TREATMENT PLANT PORTABLE PUMP HOSE | ASPHALT DRIVE | FOUR INCH PORTABLE PUMP HOSE DISCONNECTED FROM THE PUMP | SLUDGE WAS RECOVERED WITH VAC TRUCK
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-05-13 | 3:23A - 12:15P | 427886 | M-0337, M-0246, M-0407 | STREET AND STORM BASINS | RAIN 1.44" | CLEANED UP SOLIDS
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-06-18 | 7:20P - 11:30P | 74052 | SALT CREEK MAIN PUMP STATION LS-0008 ON SANDALWOOD AND 500 NORTH | SALT CREEK | RAIN 1.9" | USED EMERGENCY PUMP; CLEANED AREA
IN0030641 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-06-19 | 1:00A - 3:30 | 33279 | M-0337, M-0246 | STREET | RAIN 1.9" | AREAS INSPECTED AND CLEANED
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-06-23 | 1:10P - ? |  | 337 LAHONDA 372 LAHONDA MH M-0337 & M-0246 |  | SEVERE RAIN EVENT
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-06-23 | 8:38P - 4A (6/24) | 296725 | M- 0337, M-0246, M-0253 | STREET STORM BASINS | PRECIPITATION TOTAL 2.9" | AREAS INSPECTED AND CLEANED REHAB WORK IN COLLECTION SYSTEM WILL CONTINUE
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-06-23 | 1:10 - 3P | 14631 | M- 0337, M-0246 | STREET STORM BASINS | PRECIPITATION .85" IN 2 HOURS | AREAS INSPECTED AND CLEANED REHAB WORK IN COLLECTION SYSTEM WILL CONTINUE
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-07-02 | 7:46P - 12:30A (7/3) | 106 | 497 NORTH 266 WEST | DITCH NEAR ROAD | LEAKING 2" FORCE MAIN | SOLIDS CLEANED UP AND CONNECTION FITTING REPLACED
IN0030651 | AQUA INDIANA - SOUTH HAVEN | PORTER | 2010-12-22 | 9:57A - 10:55A | 408 | 784 TIMBERLINE MH M-0266 | AROUND MH | BLOCKAGE IN SEWER MAIN | BLOCKAGE CLEARED
IN0022578 | CHESTERTON MUNICIPAL STP | PORTER | 2010-07-24 | 1:30A - 12P | 300000 | PLANT BYPASS | EAST BRANCH LITTLE CALUMET RIVER | HEAVY RAINFALL EVENTS 4.36" | OPERATORS AND MAINTENANCE ON HAND TO MAXIMIZE TREATMENT CAPACITY
IN0022578 | CHESTERTON MUNICIPAL STP | PORTER | 2010-11-12 | 9:00A - 9:17A | 50 | MH @ 114 N. 16TH ST. | GROUND | ROOTS IN SANITARY SEWER | REMOVED ROOTS AND JETTED LINE. CLEANED AREA
IN0022578 | FRITZ C DIETRICH | PORTER | 2010-06-09 |  |  | PORTER AVE MAIN | COFFEE CREEK | SANITARY SEWER GRAVITY MAIN COLLAPSED | PLUGGED FLOW AND REPAIRED PIPE
IN0022578 | FRITZ C. DIETRICH ENV. CON. FAC. | PORTER | 2010-06-23 | 7:45P -12:45A (6/24) |  | WWTP | EAST BRANCH LITTLE CALUMET RIVER | RAIN 2.6"
| KOUTS MUNICIPAL STP | PORTER | 2010-02-25 | 5:30P - 7:45P | 8000 | DIGESTER | GROUND | PIPE FITTING CAME APART ON END OF SLUDGE TRANSFER LINE | VACUUMED UP SLUDGE, WILL APPLY LIME AND REPAIR LINE
IN0024368 | PORTAGE MUNICIPAL STP | PORTER | 2010-02-16 | 11:00P - 11:30A | 20 | 6592 POTOMAC | BASEMENT | MAIN LINE PLUGGED WITH GREASE | JETTED LINE TO RELIEVE BACKUP
IN0024368 | PORTAGE MUNICIPAL STP | PORTER | 2010-02-16 | 11:00P - 11:30A | 20 | 2111 KENNEDY | BASEMENT | MAIN LINE PLUGGED WITH GREASE | JETTED LINE TO RELIEVE BACKUP
IN0024368 | PORTAGE MUNICIPAL STP | PORTER | 2010-06-18 | 5:15P - 6:15P | 100 | ROBINWOOD ST LS | GROUND | POWER OUTAGE AT LIFT STATION | SET UP PORTABLE GENERATOR UNTIL UTILITIES WERE RESTORED
INJ046949 | PORTER WWTP | PORTER | 2010-12-31 | 9:30A - 4:00P | 200 | TRIANGLE LIFT STATION | GROUND | RAIN | USED LIQUID WASTE HAULER; THREE TRUCKS; WORKING ON I&1
INJ046949 | PORTER, TOWN OF (COLLECTION) | PORTER | 2010-06-23 | 11:42A - 12:20P | 1557 | PORTER AVE LS | LITTLE CALUMET RIVER | PRECIPITATION 2.01" | VAC TRUCKS PUMPED LS DOWN UNTIL ABLE TO HANDLE FLOW WORKING TO FIND AND STOP I & I
INJ046949 | PORTER, TOWN OF (COLLECTION) | PORTER | 2010-07-24 | 8A - 10A | 10000 | TRIANGLE LS | GROUND | PRECIPITATION 5.27" | VAC TRUCKS CALLED AND PUMPED LS WORKING ON I & I
INJ046949 | PORTER, TOWN OF (COLLECTION) | PORTER | 2010-07-24 | 6A - 10A | 23365 | PORTER AVENUE LS | LITTLE CALUMET RIVER | PRECIPITATION 5.27" | VAC TRUCKS CALLED AND PUMPED LS WORKING ON I & I
IN0031119 | SHOREWOOD FOREST UTILITIES | PORTER | 2010-11-06 | ? - 7:30A | 800 | NATURE PRESERVE & SHOREWOOD DR LS | SWAMP AREA | FLOATS WRAPPED AROUND GUIDE RAIL | VACUUMED UP LS, APPLIED LIME, MOVED FLOATS
IN0031119 | SHOREWOOD FOREST UTILITIES | PORTER | 2010-12-02 |  | 200 | 174 WEXFORD | BASEMENT | HP THOMPSON BORING FOR NIPSCO HIT A SERVICE LATERAL AND FILLED GRAVITY MAIN WITH MUD CAUSING BACKUP | HB THOMPSON IS CLEANING THE LINE AND REPAIRING THE LINE FOR HOMEOWNER AND HIRED CLEANING COMPANY
INJ046949 | TOWN OF PORTER | PORTER | 2010-05-13 | 3:15A - 11:30A | 137980 | PORTER AVE LS | LITTLE CALUMET RIVER | RAIN 3.82" | VAC TRUCKS CALLED TO OVERFLOWING AREAS AND LS PUMPED DOWN. LOOK FOR I & I
INJ046949 | TOWN OF PORTER | PORTER | 2010-05-13 | 3:15A - 7:30A | 50000 | TRIANGLE LS | GROUND | RAIN 3.82" | VAC TRUCKS CALLED TO OVERFLOWING AREAS AND LS PUMPED DOWN. LOOK FOR I & I
IN0037176 | TWIN LAKES UTILITIES | PORTER | 2010-06-01 | 9:18A - 1:43P | 750 | M.H. 2465 2472 2482 E. LAKESHORE DR | GROUND | ROOTS AND DEBRIS PARTIALLY OBSTRUCTING FLOW IN SEWER MAIN | MONITOR LEVELS I & I CURRENTLY IN PLACE
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-03-26 | 2:10P - 2:55P | 100 | LOW PRESSURE FORCE MAIN SR 130 & CR 250W | DITCH | VALVE PARTIALLY TURNED ON BY UNKNOWN PERSON | VACED UP STANDING WATER N DITCH
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-06-16 | 2P - 2:30P | 1000 | WEST SOUTH SEC CLARIFIER | GROUND | MAINTENANCE STAFF FULLY OPENED SECONDARY DRAIN VALVE SURCHARGING A 12" LINE | IMMEDIATELY CLOSED VALVE AND INSTRUCTED WORKERS APPROPRIATE ADJUSTMENTS
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-07-10 | 3:55P - 4:25P | 500 | 355 S WASHINGTON STREET MH | STORM SEWER TO CROSBY RUN | HEAVY RAIN IN SHORT TIME AND RESTRICTED FLOW BECAUSE SEWER COLLAPSE | MANHOLE CHECKED DAILY COLLAPSE REPAIRED WITHIN 30 DAYS
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-07-13 | 6:10A - 6:40A | 100 | 355 S WASHINGTON STREET MH | STORM SEWER TO CROSBY RUN | HEAVY RAIN IN SHORT TIME AND RESTRICTED FLOW BECAUSE SEWER COLLAPSE | MANHOLE CHECKED DAILY COLLAPSE REPAIRED WITHIN 30 DAYS
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-07-24 | 11:45P - 12:15P (7/25) | 50 | 355 SOUTH WASHINGTON STREET MH | STORM INLET TO CROSBY RUN | DURING HEAVY RAIN AND SANITARY SEWER COLLAPSE WERE PUMPING WHICH SWITCH FROM ONE TRUCK TO NEXT IT SPILLED | VAC TRUCKS REMOVED 16,000 GALLONS FROM MH SEWER MAIN SCHEDULED TO BE FIXED WITHIN 14 DAYS
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-07-24 | 8:00A - 8:03A | 20 | 355 SOUTH WASHINGTON STREET MH | STORM INLET TO CROSBY RUN | DURING HEAVY RAIN AND SANITARY SEWER COLLAPSE WERE PUMPING WHICH SWITCH FROM ONE TRUCK TO NEXT IT SPILLED | VAC TRUCKS REMOVED 16,000 GALLONS FROM MH SEWER MAIN IS SCHEDULED TO BE FIXED WITHIN 14 DAYS
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-09-01 | 8:00A - 8:15A | 200 | MH AT 1560 SHERWOOD DR. | BEATY CREEK WEST BRANCH | POWER OUTAGE | USED VAC TRUCK TO CLEAN AREA, POWER RESTORED
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2010-12-02 | 6:30P - 8P | 100 | MH MARKS ROAD BETWEEN LINCOLN WAY AND FIRESTONE | SMITH DITCH | SEWER MAIN BLOCKED WITH GREASE | SEWER DEPARTMENT CLEANED LINE AND WILL TELEVISE
IN0024660 | VALPARAISO WATER REC. DEPT. | PORTER | 2010-05-31 | 1:50P - 1:55P | 1000 | ELDAR KUCHL POLL. CON. FACILITY OUTFALL 002 | SALT CREEK | RAIN | MANUALLY OPENED SECOND FLOOD GATE TO CSO BASINS
IN0020516 | WINAMAC MUNICIPAL STP. | PULASKI | 2010-10-12 | 12:45P - 5:30P | 76300 | 501 S. HUDDLESTON ST. LS #2 | TIPPECANOE RIVER | CONTRACTOR INSTALLING FIBER OPTIC PHONE LINE BORED THROUGH FORCE MAIN IN 4 PLACES | SHUT DOWN LS AND INSTALLED REPAIR CLAMPS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-02-10 | ONGOING |  | MIDWAY MOTEL NORTH MAIN STREET | GROUND | 4" SEWER LATERAL IS CLOGGED AND FLOWING ON GROUND | NOTIFIED OWNER TO IMMEDIATELY REPAIR PROBLEM
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-02-22 | 9A - 3P | 50 | FORCE MAIN L.S. #4 | GROUND | SIX INCH DUCTILE FORCE MAIN CRACKED DUE TO GROUND FREEZING AND THAWING | TOWN IS CURRENTLY LOOKING TO REPLACE THIS LINE IN THE NEAR FUTURE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-02-25 | 11:03A - 1:25P | 1000 | MANHOLE W-300 & W-301 | RABBIT RUN | FLOW METER LEFT IN MH CAUSED BLOCKAGE IN LINE | REMOVED FLOW METER AND JETTED LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-03-17 | 9:00A - 3:00P | 500 | FORCE MAIN | GROUND | 6" FORCE MAIN HAD 7" SPLIT | TURNED OFF LS AND USED VAC TRUCK TO KEEP WATER LEVEL DOWN; REPLACE FORCE MAIN
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-04-10 | 10:52A - 1:06P | 500 | MH W-65 | RABBIT RUN CREEK | SEWER MAIN HAD ROOT BLOCKAGE | JETTED LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-04-23 | 10:45A - 1:55A | 20 | MH W-77 | PAVED PARKING LOT | BLOCKAGE | JETTED MH W-76, W-77 CLEANED ENTIRE SYSTEM REQUESTED KFC GREASE TRAP RECORDS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-05-13 | 3:45P - 2:00A (5/14) | 300 | GRAVITY MAIN 6" | GROUND | ROOTS IN MAIN | REMOVED BLOCKAGE, WILL REPAIR LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-05-21 | 6:00A - 8:46A | 5000 | LS #1 1556 E. CO. RD. 925 S | FERGUSON BRANCH STREAM | RAIN .09" PUMP #2 IN SHOP FOR REPAIR | RESET BREAKER IN PUMP #1
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-14 | 7A - 8:59A | 150000 | OUTFALL BYPASS OF UV | RABBIT RUN | 2.75" RAIN IN 2 HR PERIOD
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-14 | ? - 9A |  | MH D-2 | DOE CREEK | PRECIPITATION 1.5" | TOWN IS CURRENTLY WORKING ON GRANT TO REPLACE THIS L.S.
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-14 | ? - 2:30P |  | 53 WALNUT STREET MH W-52 | GROUND | PRECIPITATION 1.5" | TOWN IS CURRENTLY WORKING ON GRANT TO REPLACE THIS SEWER LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-15 | 9:20P - 10:50A (6/16) | 750 | MH A-81 | GROUND | BLOCKAGE TREE ROOTS | JETTED SEWER WITH PIPE WOLF NOZZLE WILL CLEAN UP DEBRIS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-19 | 4:30P - 6:50A | 200000 | OUTFALL | RABBIT RUN | RAIN 2" | PARTIALLY BYPASSED TO UV TO KEEP FROM FLOODING UV SYSTEM
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-22 | 8:23A - 10:34A | 250 | LS #4, MH D-2 | DOE CREEK | RAIN 2"
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-22 | 5:30A - 6:50A | 86160 | OUTFALL | RABBIT RUN | RAIN 1.5" | PARTIALLY BYPASSED UV & AERATION TO KEEP FROM FLOODING UV
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-22 | 7:45A - 10:13A | 187000 | OUTFALL | RABBIT RUN | RAIN 2" | PARTIALLY BYPASSED UV & AERATION TO KEEP FROM FLOODING UV
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-06-23 | 2:35P - 7:21P | 14300 | MH D-2 | DOE CREEK | DOE CREEK LS #4 PUMP 2 FAILURE PUMP 1 NOT PUMPING | TOOK PUMP 2 OUT FOR REPAIRS WORKING ON GRANT TO REPLACE LS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-07-17 | 22:00 - 23:00 | 11000 | CLARIFIER #1 WWTP | GROUND | PRECIPITATION 2.0 SHORT PERIOD TIME | CLEANED UP AND INCREASE SIZE OF PIPE GOING TO UV
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-07-18 | 6:45A - 9P | 553000 | OUTFALL 001 | RABBIT RUN | PRECIPITATION 2.0 UV SYSTEM FLOODED OUT | CALGON CARBON REPAIRED WWTP EMPLOYEES TRAINED TO REPAIR IF OCCURS AGAIN
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-07-18 | 13:20 - 22:00 | 1000 | 1556 EAST COUNTY ROAD 925 SOUTH | FERGUSON BRANCH CREEK | PUMP # 1 RUNNING ROUGH PUMP #2 OUT FOR SERVICE | USED BYPASS TRASH PUMP UNTIL IT OVERHEATED BAKER SEPTIC RAN PUMPS ALL NIGHT KEEP BELOW OVERFLOW PUMP CONSULTATIONS IN ROUTE TO REPLACE PUMP #2 AND PULL PUMP #1
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-07-22 | 15:30 - 15:33 | 50 | 503 SOUTH MAIN STREET GRAVITY MAIN | GROUND TO DOE CREEK | BLOCKAGE | JETTED BLOCKAGE CLEANED UP AND REPAIR SEWER LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-09-16 | 8:10A - 10:18A | 200 | FORCE MAIN | GROUND | 6" PVC FORCE MAIN HAD GASH | CLEANED WITH VAC TRUCK AND REPAIRED
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-09-23 | 9:30A - 12:15P | 200 | FORCE MAIN | GROUND | FORCE MAIN HIT WITH BACKHOE | CLEANED AREA AND REPAIRED FORCE MAIN
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-10-11 | 9:40A - 11:30A | 150 | FEED MILL LAFAYETTE ST | STREAM | 8" GRAVITY MAIN HAD BLOCKAGE | JETTED LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2010-10-25 | 11:50A - 12:15P | 50 | FORCE MAIN FROM LS #6 | GROUND | CREW STRUCK FORCE MAIN WHEN BORING FIBER CABLE | LS SHUT OFF AND BREAK REPAIRED
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2010-01-28 | 12:45A - 2:10 | 30000 | NORTH JACKSON STREET | STREAM | FORCE MAIN FROM LIFT STATION BROKE | CREW IN ROUTE TO REPAIR ALSO PUMP TRUCKS PUMPING UNTIL REPAIR COMPLETE
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2010-03-23 | 11A - 11:10A | 500 | FORCE MAIN FROM WAL-MART DISTR. LS | GROUND | 2" FORCE MAIN BROKE, PIPE BROKE IN VALVE PIT | PUMP TRUCK PUMPING WHILE PIPE IS FIXED
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2010-04-02 | 1:45P - 1:50P | 5000 | HEAD CELL AT FRONT OF PLANT | STREAM THROUGH PLANT | CONTROL PANEL FAILED CAUSED GATE TO CLOSE | MANUALLY OPENED GATE TO STOP OVERFLOW AREA CLEANED WITH VAC TRUCK
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2010-05-22 | 8:12P - 8:20P | 5000 | NORTH JACKSON ST LS | STREAM BESIDE LS | LOST POWER TO LS | PICKED UP DEBRIS AND APPLIED BLEACH SOLUTION TO AFFECTED AREA
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2010-06-09 | 5:30A - 5:45A | 50 | SHADOWLAWN AVE. MH #89-A | GROUND | SEWER LINE HAD SMALL BLOCKAGE | CLEANED DEBRIS FROM PUMP AND RETURNED EQUIPMENT TO SERVICE
IN0021032 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2010-06-30 | 1:15P - 1:18P | 50 | MH #96-6B | STROM SEWER | WHILE CLEANING DEBRIS BUILT-UP CAUSING WATER TO SURCHARGE | PICKED UP DEBRIS AND WASHED DOWN WITH BLEACH SOLUTION
IN0042960 | PUTNAMVILLE CORR. FACILITY | PUTNAM | 2010-03-31 | ONGOING |  | BELOW TOWER 3 | CULVERT WHICH FEEDS TO DEER CREEK |  | LOOKING FOR LEEK AND WILL REPAIR
IN0039624 | VAN BIBBER CONSERVANCY DISTRICT | PUTNAM | 2010-01-21 | 11:00A - 2:00P | 500 | MANHOLE AT LOT 5190 | GROUND | SEWER LINE BLOCKED WITH ROOTS, GRASS AND BABY WIPES | JET TRUCK CLEANED LINE, SPREAD LIME ON SPILL AREA
IN0039624 | VAN BIBBER CONSERVANCY DISTRICT | PUTNAM | 2010-10-24 | 12:30 - 6:30 | 5000 | CLEAN OUT AT LOT 3012 | GROUND 500' TO GLENN FLINT LAKE | SEWER LINE BLOCKED WITH ROOTS AND GREASE | TRIED TO ROTO ROOT HAD TO CALL IN JET TRUCK SPRAYED BLEACH ON SPILL ROTO ROOT EVERY 6 MONTHS
IN0063177 | CARDINAL ETHANOL, LLC | RANDOLPH | 2010-09-25 | A - (9/27) | 42000 | MANHOLE OUTSIDE WATER TREATMENT | DRY SOIL GRAVEL | FINISHING PONDS WERE FULL AND BACKED UP THE COLLECTION SYSTEM | ADJUSTED THE WEIR SETTINGS TO DECREASE LEVEL IN PONDS AND ALLEVIATE BACK UP
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2010-03-13 | 3/15 | 300000 | OUTFALL #2 | ARBOGAST DITCH | RAIN 2.07" | ADJUST PUMPS FOR MAXIMUM FLOW
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2010-03-22 | AM - AM (3/23) | 300000 | OUTFALL 2 | ARBOGAST DITCH | 1" RAIN IN 12 HOURS SATURATED SOILS | ADJUST FOR MAXIMUM PLANT FLOW PLANNING GRANT BEING PROCESSED
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2010-04-08 | AM - |  | OUTFALL #2 | ARBOGAST DITCH | PRECIPITATION 1.06" | WAS ADJUSTED FOR MAXIMUM FLOW PLANNING GRANT HAS BEEN APPROVED
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2010-05-17 | 3P - A (5/19) | 125000 | OUTFALL #002 | ARBOGAST DITCH | MORE RAIN ON SATURATED GROUND 1.26" | ADJUST PUMPS TO MAXIMIZE FLOW WORKING ON I & I
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2010-06-14 | 9:30P - 12 (6/16) | 200000 | OUTFALL #2 | ARBOGAST DITCH | HEAVY RAIN IN SHORT TIME 2" | MAINTAIN PUMPS TO MAXIMIZE FLOW
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2010-06-21 | 8:30A - PM (6/23) | 300000 | OUTFALL #002 | ARBOGAST DITCH | RAIN 2.61" | ADJUST PLANT AND PUMPS FOR MAXIMUM FLOW
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2010-08-04 | 21:00 |  | OUTFALL #2 | ARBOGAST DITCH | PRECIPITATION 2.35"
IN0020001 | RIDGEVILLE MUNICIPAL STP | RANDOLPH | 2010-03-13 | 8:00A - 4:00A (3/15) |  | WWTP CSO | MISSISSINEWA RIVER | RAIN 1.93" | LTCP
IN0020001 | RIDGEVILLE MUNICIPAL STP | RANDOLPH | 2010-05-21 | 9:00P - 4:00A |  | WWTP CSP | MISSISSINEWA RIVER | RAIN 2.14" | LTCP
IN0109703 | HOLTON MUNICIPAL STP | RIPLEY | 2010-03-25 | 14:30 - 15:30 |  | 21 NORTH DERRICK STREET | YARD | EQUIPMENT FAILURE PUMP OUT | PIT WAS PUMPED OUT AND TAKEN TO PLANT AND REPLACED PUMP AND CONTROLS
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2010-06-09 | 2:00P - 6:00P | 30000 | HEADWORKS | TRIBUTARY OF PLUM CREEK | RAIN 2.7" | ALL PUMPS AT HIGHEST FLOW SETTINGS
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2010-06-12 | 11:15P - 2:30A (6/13) | 60000 | HEADWORKS | PLUM CREEK | FLASH FLOODING RAIN 1.8" & .8" | PUMP & PROCESS CONTROLS WERE AT HIGH FLOW SETTING
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2010-06-12 | 9:30A - 1:30P | 60000 | HEADWORKS | PLUM CREEK | FLASH FLOODING RAIN 1.8" & .8" | PUMP & PROCESS CONTROLS WERE AT HIGH FLOW SETTING
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2010-06-14 | 9:30P - 12A (6/15) | 20000 | HEADWORKS | TRIB OF PLUM CREEK | STORMS 1.0" FLASH FLOODING | ALL PUMPS & PROCESSES PUT IN HIGHEST FLOW SETTINGS
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2010-06-21 | 12:30P - 2:50P | 20000 | HEADWORKS | PLUM CREEK | RAIN 1.7" | ALL PUMPS AND PROCESSORS PUT IN LIGHTEST FLOW SETTINGS
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2010-11-30 | 4A - 5:30A | 15000 | HEADWORKS | TRIBUTARY OF PLUM CREEK | HEAVY RAINS 1.8" | MAXIMIZED TREATMENT TO MINIMIZE POTENTIAL FOR OVERFLOW FINAL STAGES FOR SECURING FUNDS TO BUILD EQ BASIN
IN0021679 | SUNMAN MUNICIPAL STP | RIPLEY | 2010-06-25 | ? - 10A |  | 627 EASTERN AVENUE AIR RELIEF VALVE | BEAN FIELD | DAMAGED AIR RELIEF VALVE WHEN PLANTING CROPS | REPLACED VALVE CLEANED SITE AND TALK TO PROPERTY OWNER ABOUT PLACING STAKES TO DECREASE RISK OF HAPPENING AGAIN
IN0109746 | ANDERSON TOWNSHIP RSD | RUSH | 2010-06-12 | 11:30A - 7:30A (6/13) | 48000 | 7352 S ST RD 3 | GROUND | 3.05" RAIN COUNTY FLOOD | SHUT WOODS LIFT STATION OFF TO PREVENT FLOODING IN MORE POPULATED AREA
IN0109746 | ANDERSON TOWNSHIP RSD | RUSH | 2010-06-19 | 8:15A - 1:00P | 12000 | 7352 S ST. RD 3 | GROUND | RAIN 1.8" | LS SHUT OFF TO PREVENT OVERFLOW TO MORE POPULATED AREA
IN0109746 | ANDERSON TOWNSHIP RSD | RUSH | 2010-06-22 | 8:00A - 4:00P | 14000 | 7352 ST RD 3 | GROUND | RAIN 2" | SHUT DOWN LS TO PREVENT OVERFLOW IN POPULATED AREAS
IN0024937 | CARTHAGE MUNICIPAL STP | RUSH | 2010-06-25 | 11A - 1:35P (7/2) | 691200 | SOUTH MAIN STREET SERVICE LINE AT HOUSE | GROUND | PUMP 1 STOPPED WORKING | HAD BACK UP PUMP AND REPAIRED OLD ONE
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2010-07-08 | ? - 11:30A (7/9) |  | 2523 MILBURN AVENUE | BASEMENT | CONTRACTOR CRUSHED LATERAL SERVICE LINE | LATER WAS REPLACED CLEANING COMPANY HIRED TO CLEAN AND SANITIZE BASEMENT
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 8P |  | 608 WEST 3RD | BASEMENT | BETWEEN 7 & 8P RECEIVED 2" RAINFALL | AFFECTED RESIDENCES WILL HAVE LATERAL TV.
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 8P |  | 639 NORTH STATE STREET | BASEMENT | BETWEEN 7 & 8P RECEIVED 2" RAINFALL | AFFECTED RESIDENCES WILL HAVE LATERAL TV.
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 8P |  | 627 NORTH WENGER | BASEMENT | BETWEEN 7 & 8P RECEIVED 2" RAINFALL | AFFECTED RESIDENCES WILL HAVE LATERAL TV.
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 8P |  | 217 WEST LAWRENCE | BASEMENT | BETWEEN 7 & 8P RECEIVED 2" RAINFALL | AFFECTED RESIDENCES WILL HAVE LATERAL TV.
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 8P |  | MH #19 MERRIFIELD PARK | GROUND | BETWEEN 7 & 8P RECEIVED 2" RAINFALL | RELEASE WAS VACTORED WHERE IT POOLED CORDONED OFF AND WILL BE DISINFECTED
IN0025640 | MISHAWAKA MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 8P |  | MH #33 EBERHART GOLF COURSE | GROUND | BETWEEN 7 & 8P RECEIVED 2" RAINFALL | RELEASE WAS MINIMAL DRAINED BACK INTO MH
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-01-22 | 10:44A - 1:15P |  | PRIVATE SEWER 18485 WOODED WAY | BATH TUB | BLOCKAGE | JET RODDER OPENED BLOCKAGE AND SCHEDULE C.C.T.V. CREW
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-05-02 | 6:06A - 6:51A |  | INTERCEPTOR M.H. NEAR 27TH STREET L.S. | ST JOSEPH RIVER | RAIN EVENT 5/2/10 | NOTICED DEBRIS NOT SURE OF FACTS THE CITY WILL NEED TO FURTHER INVESTIGATE
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 17:49 - 19:04 |  | 1217 ALTGELD | BASEMENT | HEAVY RAIN 2.4" IN 40 MINUTES | INFORMATION FORWARDED TO ENGINEER
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 17:49 - 19:04 |  | 1702 WEST CALVERT | BASEMENT | HEAVY RAIN 2.4" IN 40 MINUTES | INFORMATION FORWARDED TO ENGINEER
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 17:49 - 19:04 |  | 1718 EAST JEFFERSON BOULEVARD | BASEMENT | HEAVY RAIN 2.4" IN 40 MINUTES | INFORMATION FORWARDED TO ENGINEER
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 17:49 - 19:04 |  | 117 EAST JENNINGS AVENUE | BASEMENT | HEAVY RAIN 2.4" IN 40 MINUTES | INFORMATION FORWARDED TO ENGINEER
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-07-15 | 17:49 - 19:04 |  | 1736 PRAIRIE AVENUE | BASEMENT | HEAVY RAIN 2.4" IN 40 MINUTES | INFORMATION FORWARDED TO ENGINEER
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-07-28 | ? - 4:14P |  | MICHIGAN STREET MH | ST JOSEPH RIVER | INTENSE BAND SHOWERS .23" | CCTV'D AREA AND CONTROL OPTIONS BEING STUDIED
IN0024520 | SOUTH BEND MUNICIPAL STP | SAINT JOSEPH | 2010-09-28 | 8P - 9:30P | 3000 | CSO 019 | SAINT JOSEPH RIVER | LARGE ASPHALT CHUCK WAS OBSTRUCTION | CREW WAS DISPATCHED IMMEDIATELY SITE MONITORED 24 HOURS DAY
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-05-02 | 4P - 8P | 1000 | M.H. #102 | AROUND MANHOLE | HEAVY RAINFALL BACKING UP SYSTEM 2.0"
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-06-28 | 5A - 7A |  | MH #97, 85 | GROUND | HEAVY RAINFALL BACKING UP SYSTEM
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-11-30 | 12 - 12:30 |  | MH 351-352 | AROUND MANHOLE | PEPSI RELEASING TO MUCH FLOW L.S. CANT HANDLE | CALLED THEM HAD THEM SLOW DOWN FLOW
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-12-02 | 1P - 2P |  | MH 351-352 | AROUND MANHOLE | PEPSI RELEASING TO MUCH FLOW L.S. CANT HANDLE
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-12-19 | 1:30P - 5:00P |  | MH 351-352 | AROUND MANHOLE | PEPSI RELEASING TOO MUCH FLOW. LS CAN'T HANDLE IT
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-12-20 | 10:30A - 2:30P |  | MH 351-352 | AROUND MANHOLE | PEPSI RELEASING TOO MUCH FLOW. LS CAN'T HANDLE IT.
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-12-22 | 1:00A - 2:30A |  | MH 351-352 | AROUND MH | PEPSI RELEASING TOO MUCH FLOW. LIFT STATION CAN'T HANDLE IT.
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-12-27 | 3A - 5A |  | 351 - 352 | GROUND | PEPSI RELEASING TO MUCH FLOW L.S. CANT HANDLE
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2010-12-30 | 1:10A - 7A |  | 351 - 352 | GROUND | PEPSI RELEASING TO MUCH FLOW FOR L.S. HANDLE | TALKED TO PEPSI
IN0020397 | SCOTTSBURG MUNICIPAL STP | SCOTT | 2010-07-11 | ? |  | SCOTTSBURG MIDDLE SCHOOL 425 SOUTH 3RD STREET | FLOOR DRAIN | COOLING TOWER PUMP FAILED | PUMP TAKEN OUT OF SERVICE CONTACTED WASTEWATER PLANT
IN0020397 | SCOTTSBURG MUNICIPAL STP | SCOTT | 2010-11-22 | ? - 10:00A | 2000 | AMBERY POINT LS PRIVATELY OWNED | CREEK | LS FLOAT STUCK IN GREASE; ALARM FLOAT DID NOT WORK | CLEANED FLOATS, INSTALLED NEW ALARM FLOAT AND PUMPED STATION DOWN
IN0032867 | SHELBYVILLE MUNICIPAL STP | SHELBY | 2010-06-13 | 2A - 6:55A | 529000 | CONREY STREET L.S. | BIG BLUE RIVER | 2.42" RAIN WITH SATURATED GROUND | CONTINUE I & I REDUCTION AND REPLACEMENT OF OLD LINES
IN0032867 | SHELBYVILLE MUNICIPAL STP | SHELBY | 2010-06-19 | 6:00A - 12:10A (6/20) | 3135000 | CONREY ST. LIFT STATION | BIG BLUE RIVER | RAIN 2.10"
IN0032867 | SHELBYVILLE MUNICIPAL STP | SHELBY | 2010-06-22 | 6:50A - 8:30A | 5749000 | CONREY LS & MCKAY ROAD LS | BIG BLUE RIVER & VAN PELT COUNTY DITCH | 2.39" RAIN ALREADY SATURATED GROUND | CONTINUE I & I PROGRAM AND REPLACEMENT OLD SEWER LINES
IN0021598 | DALE MUNICIPAL STP | SPENCER | 2010-05-02 | 6A - 4P | 200000 | WEST SIDE L.S. | STREAM | SATURATED GROUND AND 4" RAIN | ASKED TOWN TO DO A STUDY AND FIND I & I HAVE DONE SLIP LINING AND M.H. REHAB BUT STILL GET INFILTRATION
INLA714 | FULDA RSD | SPENCER | 2010-05-26 | 10A - 12:30P | 200 | LATERAL | GROUND | CONTRACTOR HIT LINE | LOCATES MARKERS SHUT VALVE OFF AND REPAIR LINE
IN0061662 | ROCKPORT MUNICIPAL STP | SPENCER | 2010-08-19 |  | 50 | WASHINGTON LS | GROUND | FLOATS TANGLED | UNTANGLED FLOATS AND CLEANED AREA
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2010-07-19 | 6 - 6:30 |  | LS 17 MH | GROUND DITCH LINE | HEAVY STORMS WITH UTILITY PROVIDER POWER OUTAGES
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2010-07-19 | 6 - 6:30 |  | LS 18 MH | GROUND DITCH LINE | HEAVY STORMS WITH UTILITY PROVIDER POWER OUTAGES
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2010-07-19 | 6 - 6:30 |  | LS 8 MH | GROUND DITCH LINE | HEAVY STORMS WITH UTILITY PROVIDER POWER OUTAGES
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2010-11-25 | 12P - 9P |  | MH 63 & 24 | GROUND | RESTRICTION IN LINE PRECIPITATION 4.6" | LET LINE CLEAR ROOTS AND MONITOR SERVICE AREA
IN0024520 | CITY OF SOUTH BEND | ST JOSEPH | 2010-08-11 | ?-3:00A |  | MH 0026 | GROUND | CRACKED CLAY PIPES | PIPES REPAIRED
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2010-03-09 | 11:25A - 12:15P | 300 | MIDDLEBORO L.S. CSO 002 | ST JOSEPH RIVER | TRANSDUCER WELL OBSTRUCTED WITH GRIT | WET WELL AND INLET TO TRANSDUCER WELL CLEANED
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2010-06-17 | 5:00P |  | 3917 GRADE RD | STORM SEWER | GREASE | CLEANED SEWER AND STREET
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-02-10 | 7:30P - 8:45P | 0 | 5306 SOUTH MONTICELLO | BATH TUB | MAIN LINE BLOCKED | JET RODDER CLEARED BLOCKAGE WILL T.V. LINE IN FUTURE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-02-10 | 10A - 12:30P | 0 | 521 LAUREL STREET | NO RELEASE | MAIN SEWER WAS BACKED UP | JET RODDER CLEARED BLOCKAGE WILL T.V. LINE IN FUTURE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-02-23 | 7P - 9P |  | 51773 OLD MILL ROAD | BASEMENT | BLOCKAGE MAIN LINE | JET RODDER 461 OPENED MAIN LINE WILL C.C.T.V. OUR LINE AND ROOTX
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-04-13 | 8:58 - 9:28 | 10000 | CSO 4 | ST JOSEPH RIVER | CONTRACTOR INSTALLING 30" WATER LINE OPENED HYDRANT TO RELEASE PRESSURE FLOW ENTERED CSO 4 TEMP. WET WEATHER OVERFLOW | CSO CREW INFORMED CONTRACTOR HYDRANT HAD TO BE SHUT OFF THEN INSTRUCTED THE FLOW SHOULD BE DIRECTED TO NEARBY INTERCEPTOR
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-04-13 | 10:42 -11:22 | 10000 | CSO 26 | ST JOSEPH RIVER | SOURCE OF INCREASED FLOW IS UNKNOWN | CSO CREW CHECKED MANHOLES AND FOUND NOTHING
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-04-19 | 7:30A - 8:40P | 10 | M.H. AT 2502 S. LOCUST ROAD | GROUND | FULL OF TOILET PAPER | JET RODDER ELIMINATED BACK UP WILL PUT THIS ON THE CHECK ONCE MONTHLY LIST
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-05-11 |  |  | INTERCEPTOR MH NEAR 27TH ST LS | ST. JOSEPH RIVER | RAIN 1.1" CITY STAFF FOUND DEBRIS AROUND MH | CITY WILL INVESTIGATE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-05-11 | 2:00P - 2:15P | 2 | MAIN LINE 1201 ALTGELD ST | BASEMENT | CONCRETE AND DEBRIS IN LINE | OPENED BLOCKAGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2010-07-19 | 10:48A - 11:23A | 10000 | CSO 14 | ST JOSEPH RIVER | CONTRACTOR HIT CLAY PIPE WHILE INSTALLING LARGER DIAMETER THROTTLE LINE | CSO CREW DISPATCHED
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2010-06-12 | 5:15P - 6:15P | 90815 | CSO # 4 | UNNAMED DITCH TO PINE CREEK | FLASH FLOOD RAIN 1.25" IN 20 MINS | ALL EQUIPMENT WAS WORKING PROPERLY AS DESIGNED ST RD 39 STORM DRAINS STILL TIED INTO SANITARY SEWER WORKING ON GRANT TO CORRECT
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2010-07-08 | 12:25P - 2:55 | 4769 | CSO #4 | UNNAMED DITCH TO PINE CREEK | PRECIPITATION .85" IN A SHORT TIME | PLANT AND CSO RUNNING AT FULL CAPACITY STATE ROAD 39 STORM DRAINS MAJOR I & I
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2010-07-24 | 8:15A - 11:30P | 420000 | CSO #4 | UNNAMED DITCH TO PINE CREEK | 3.84" RAIN IN 2 HOURS | PLANT WAS RUNNING FULL SPEED AND CSO BASIN PUMPS FLOW OVERLOADED PLANT
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2010-08-03 | 6:45A - 7:50A | 44718 | CSO #4 | UNNAMED DITCH TO PINE CREEK | .55" IN 15 MINUTES ANOTHER .45 OVER NEXT HOUR | PLANT WAS RUNNING FULL SPEED AND CSO BASIN PUMPS FLOW OVERLOADED PLANT
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2010-08-04 | 8:10A - 8:45P | 9886 | CSO #4 | UNNAMED DITCH TO PINE CREEK | .5" IN 15 MINUTES AS WE WERE RESTORING POWER TO OUR LARGEST LS | INDOT NEEDS TO REMOVE STORM DRAIN FROM HWY 39
| ANGOLA GARDENS TRAILER PARK | STEUBEN | 2010-09-06 | 12:00A - 10:00A (9/14) | 172000 | TRAILER PARK LIFT STATION | GROUND TO UNNAMED WETLAND | LIFT STATION NOT WORKING PROPERLY REGULAR REPAIR AND MAINTENANCE PROGRAM | REGULAR REPAIR AND MAINTENANCE PROGRAM
| ANGOLA GARDENS TRAILER PARK | STEUBEN | 2010-09-16 |  | 2000 | LS 550 S. 300 W | GROUND | LIFT STATION NOT WORKING PROPERLY | LS REPAIRED
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2010-06-25 | 0 - 09:00 (6/29) | 35000 | AIR RELIEF VALVE N HETZLER COURT | GROUND | FAILED AIR RELIEF VALVE | SHUT DOWN STATION VAC UP ALL DEBRIS REPAIRED STATION AND WILL CONSIDER ADDING VISUAL INSPECTIONS
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2010-06-29 | 3P - 8A (6/30) | 5000 | AIR RELIEF VALVE N HETZLER COURT | GROUND | FAILED FLOAT WITHIN AIR RELIEF VALVE | SHUT DOWN STATION VAC UP ALL DEBRIS REPAIRED STATION AND WILL CONSIDER ADDING VISUAL INSPECTIONS
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2010-08-17 | 4:45P - 5:15P | 300 | MH AT 2795 WOODHULL DR. | GROUND | PARTIAL SEWER COLLAPSE | STOPPED OVERFLOW AND REPAIRED SEWER
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2010-09-01 | 8:00A - 9:30A |  | 700 PINE RUN | BASEMENT | ROOT BLOCKAGE IN SEWER | REMOVED BLOCKAGE
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2010-11-29 | 06:00 - 13:00 | 500 | AIR RELIEF VALVE NORTH HETZLER | GROUND | AIR RELIEF VALVE LODGE WITH DEBRIS | REPAIRED AIR RELIEF VALVE AND CONTINUE MAINTENANCE
IN0022942 | FREMONT MUNICIPAL STP | STEUBEN | 2010-06-20 | 5:00P - 6:00P | 1500 | LS @ CR 100 E & SR120 | GROUND | BREAKERS TRIPPED | BREAKERS RESET AND LS PUT BACK ON LINE
IN0022942 | FREMONT MUNICIPAL STP | STEUBEN | 2010-12-26 | 5:30P - 6:30P | 2000 | L.S. #1 SR 120 & CR 100E | GROUND | BOTH MAIN BREAKERS FOR PUMPS TRIPPED | RESET AND MONITORED
IN0050822 | HAMILTON LAKE C.D. | STEUBEN | 2010-09-22 | 11:00A - 12:00P | 150 | DISCHARGE LINE AT 1595 W. 280 | GROUND | ELECTRICAL CONTRACTOR PROBED THROUGH LINE | LINE DUG UP AND REPAIRED. VAC TRUCK REMOVED SEWAGE
IN0050822 | HAMILTON LAKE C.D. | STEUBEN | 2010-10-11 | 4:30P - 5:00P | 100 | 40-8, 7377 BROOKSIDE DR. | GROUND | FLANGE FAILED OUTSIDE GRINDER TANK | DUG UP AND REPAIRED
IN0050822 | HAMILTON LAKE C.D. | STEUBEN | 2010-11-15 | 2P? - 2:30 | 25 | GRINDER STATION 28-17 | GROUND | FLOATS FOULED DID NOT ALLOW PROPER OPERATION OF PUMP OR ALARMS | STATION REPAIRED AND BACK IN SERVICE
IN0061557 | STEUBEN LAKES RWD | STEUBEN | 2010-08-04 | 6:30P - 10P | 1500 | 310A LAKE JAMES | GROUND LAKE JAMES | NIPSCO BROKE 2" MAIN | QUICKLY REMEDIED INCREASE AWARENESS NECESSITY TO LOCATE BEFORE DIG
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2010-03-16 | ? - 11:00A (3/17) | 50000 | MAIN LIFT STATION SAWMILL RD. | GOAT CREEK | B&T REPLACING WATER LINES HIT FORCE MAIN FROM LIFT STATION | REPLACED DAMAGED LINE; BETTER COMMUNICATION ON LINE LOCATION
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2010-09-17 | 14:30 - 16:30 | 500 | BORE HOLE | STORM WATER TRENCH | SURFACE DRAINAGE PIPE AND 4" CAST IRON PIPE | TOOK SAMPLES PUMPED TO SETTLING BASIN AND TREATED BASIN WITH HTH CLEANOUT RISE PIPE WAS CAPPED
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2010-09-20 | 07:30 - 09:30 | 500 | BORE HOLE | STORM WATER TRENCH | SURFACE DRAINAGE PIPE AND 4" CAST IRON PIPE | TOOK SAMPLES PUMPED TO SETTLING BASIN AND TREATED BASIN WITH HTH CLEANOUT RISE PIPE WAS CAPPED
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2010-10-06 | 02:30 - 12:302800 | 2800 | SEWAGE MANHOLE 209 | NEW PIPE TRENCH | HOLE FOR NEW PIPE TO TIE INTO EXISTING LINE HAD EXCESSIVE FLOWS | PRIOR TO CUTTING INTO EXISTING LINES BY CONTRACTOR PLANT WILL BE NOTIFIED TO KEEP CLOSER EYE ON FLOWS
IN0040134 | HYMERA MUNICIPAL STP | SULLIVAN | 2010-08-10 | ? - 15:30 | 1500 | MAIN LS #1 |  | BAD PHASE MONITOR | SYCAMORE WORKED ON IT AND WILL FIX IT 8/11/10
IN0030228 | SHAKAMAK STATE PARK | SULLIVAN | 2010-06-19 |  | 6000 | BROKEN LINE NEXT TO LIFT STATION |  | BROKEN LINE NEXT TO LIFT STATION | SHUT OFF LIFT STATION
IN0024554 | SULLIVAN MUNICIPAL STP | SULLIVAN | 2010-08-22 | ? - 8:30A | 20000 | CEMETERY CSO | BUCK CREEK | VORTEX VALVE FAILED SYSTEM CLOGGED | USING VAC TRUCK TO REMOVE SEWAGE FROM CREEK PART OF LTCP TO REMOVE THIS CSO
IN0024554 | SULLIVAN MUNICIPAL STP | SULLIVAN | 2010-11-16 |  |  | HALLAWAY STREET | DRY CREEK | SEWER MAIN COLLAPSE | CALLING IN LOCATES DIG UP MAIN AND FIX PIPES
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2010-03-20 | 15:00 - 13:00(3/21) |  | FORCE MAIN EAST EDGE OF TRAILER PARK | GROUND AND DITCH | LEAKING FORCE MAIN | FLUID WASTE SERVICES PUMPED AND HAULED TO PLANT REPAIRED SMALL AREA WITH HEAVY BAND CLAMPS
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2010-03-30 | 7:00A - 8:30A | 100 | 511 MAIN ST. MANHOLE | STORM SEWER | PLUGGED GRAVITY SEWER. | PULLED LARGE AMOUNT OF RAGS FROM GRAVITY SEWER
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2010-06-20 |  | 312000 | CONTACT TANK | POLISHING POND | VALVE CAME LOOSE | TOOK VALVE APART AND REPOSITIONED IT
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2010-06-22 | 9:30A - 7:30 (6/23) |  | PROPHETS ROCK LS, WOODS EDGE LS, WWTP | BURNETTS CREEK | RAIN 4.02" | AIR TUNED OFF TO CREATION BASINS TO RETAIN SOLIDS
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2010-08-16 | 8:30P - 9:50A (8/17) | 2500 | WOODS EDGE LS FORCE MAIN | BURNETTS CREEK | BREAK IN FORCE MAIN | TURNED OFF LS AND REPAIRED; PUMPING OVERFLOW OUT OF CREEK TO SEWER
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2010-11-06 | 6:00A - 12:00P | 5000 | WOODS EDGE FORCE MAIN | GROUND AROUND BREAK AND BURNETTS CREEK | FORCE MAIN BREAK | PUMPING AND HAULING TO TREATMENT PLANT; FORCE MAIN REPAIRED
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2010-12-03 | 1:00P - 4:00P | 1500 | WOODS EDGE LS FORCE MAIN | GROUND | BREAK IN FORCE MAIN | HAULED EIGHT LOADS OUT OF LS WHILE REPAIR WAS COMPLETED
IN0043273 | CARRIAGE ESTATES SUBDIVISION | TIPPECANOE | 2010-06-22 | 4:00A -8:00P |  | MH # CE11, HAWTHORNE LS | STREAM | RAIN 3.5" | MANUALLY RUNNING 6" PUMP TO HELP CATCH UP SEWER LINE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-01-01 | 4:15P - 5P | 100 | 2202 PUEBLO DR | BASEMENT SUMP TO GROUND | SEWER PLUGGED | OPENED WITH JET TRUCK WILL ROOT CUT AND TV LINE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-01-30 | 10:30A - 11:32A | 5 | CITY SEWER 2612 BONNIE LANE | BASEMENT | CITY SEWER PLUGGED | JETTED OPEN AND TV
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-03-14 | 1:35P - 1:45P | 30 | MH AT 1005 ALDER DR | GROUND | SEWER PLUGGED | OPENED SEWER AND CLEANED AROUND MANHOLE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-03-15 | 1:05P - 1:55P | 10 | MH BEHIND 406 PERRIN AVE | BASEMENT AT 1405 JOHNSON ST | PLUGGED CITY SEWER | SEWER WAS JETTED; SCHEDULED FOR PREVENTATIVE MAINTENANCE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-03-28 | 12:30P - 12:40P | 1000 | FORCE MAIN TOWER ON WABASH AVE | GROUND | ADDITION OF CHEMICAL DURING TRIAL STUDY FOR ODORS CAUSED A REACTION | OXYGEN INPUT HAS BEEN REDUCED AND ODOR CONTROL CHEMICAL DOSAGE ADJUSTMENTS
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-04-23 | 11:05P - 2:00A (4/24) | 300 | 2736 PORTSMOUTH | BASEMENT | CONCRETE GOT IN FLOW LINE | REMOVED CONCRETE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-06-08 | 4:25 | 50 | 726 S. 31ST ST. | GROUND | PRIVATE LATERAL
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-06-14 | 12P - 12:30P | 100 | 825 SOUTH 28TH | BASEMENT | CITY SEWER WAS PLUGGED | JETTED SEWER LINE CITY SEWERS ARE CLEANED AS PREVENTATIVE MAINTENANCE PROGRAM
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-06-22 |  |  | 1005 S 18TH STREET, 28 STAYMEN COURT, 1122 SOUTH 21ST STREET, 3901 NORTH ORCHARD COURT, 601 SOUTH 27TH STREET, 1105 ADAMS STREET, 608 ORCHARD DRIVE | BASEMENTS | 3.37 " PRECIPITATION
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-06-22 | 5:59A - 7:08A |  | FORTY AND EIGHT LIFT STATION | GROUND | RAIN 3.37" LIGHTENING CAUSED PUMPS TO TRIP OUT | ATTACHED LIST DETAILED OVERFLOWS
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-06-23 | 8:40A - 9:40A | 100 | OUTFALL 011 14TH STREET | DURKES RUN TO WABASH RIVER | HEAVY RAINS CAUSED DEBRIS TO BLOCK LINE | REMOVED BLOCKAGE AND CONTINUE FOLLOW UP INSPECTIONS AFTER HEAVY RAINS
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-07-14 | 2P - 2:10P | 1000 | HIAWATHA & KICKAPOO JET/VAC TRUCK | STORM CATCH BASIN | WE WERE DECANTING JET TRUCK MISTAKE INTO STORM CATCH BASIN | WASTE WAS CONTAINED AND CLEANED UP REFRESHER TRAINING ON LINE IDENTIFICATION
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-07-17 | 8P - 9P | 10000 | 2351 NORTH 24TH STREET, 2135 & 2122 PERRIN STREET, 1722 NORTH 15TH STREET, 2108 ULEN LANE | BASEMENT | PRECIPITATION 2" | RAIN WATER RECEDED WATER WENT DOWN WILL CHECK SEWERS 7/19/10
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-08-09 | 8:03A - 10:50A | 100 | MANHOLE | GROUND | PRIVATE SEWER PLUGGED WITH GREASE | SANDBAGGED DITCH JETTED LINE EDUCATED OWNERS ON PROPER GREASE DISPOSAL
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-08-18 | 4:35P - 6:30P | 500 | SEWER BREAK @ MAIN & EARL ST. | BASEMENT | COLLAPSED SEWER LINE | REPAIRED EQUIPMENT AND CLEANED DEBRIS FROM AREA
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-10-08 | 2:02P - 2:16P | 50 | CSO #10 | UNNAMED DITCH | WATER MAIN FLUSHING CAUSED DEBRIS TO BLOCK LINE AT OUTFALL | REMOVED BLOCKAGE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-10-17 | 2:00P - 2:40P | 55 | 305 MCCUTCHEON | BASEMENT | PLUGGED SEWER | JETTED SEWER OPEN
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-10-29 | 11:40A - 1:15P | 2 | 920 NORTH 11TH STREET | BASEMENT | CITY SEWER WAS PLUGGED | JET CLEANED TO OPEN VAC'D MH CONTINUE TO PERFORM PREVENTATIVE MAINTENANCE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-11-15 | 5:40P - 6:20P | 500 | 4112 FLETCHER DR MH | GROUND TO STORM SEWER TO POND | CITY SEWER PLUGGED | JETTED AND VAC'D RECOVERED 250 GALLONS WILL T.V. 11/16/10
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-11-24 | 5:30P - 6:10P | 500 | 21ST & CENTRAL | BASEMENT | RAIN .5" BLOCKAGE IN SEWER | REMOVED BLOCKAGE WITH JET VAC TRUCK
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-11-24 | 2:30P - 3:00P | 200 | OUTFALL #011 | DURKEES RUN TO WABASH RIVER | RAIN .25" BLOCKAGE FOUND IN REGULATOR | CLEARED BLOCKAGE FROM REGULATOR
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-12-01 | 10:10 |  | 523 SOUTH 31ST STREET | BASEMENT | CITY SEWER PLUGGED | JETTED LINE AND T.V. LINE
IN0023990 | OTTERBEIN MUNICIPAL STP | TIPPECANOE | 2010-06-22 |  |  | MH @ S. INDIANA ST. | GROUND | RAIN 6"
| PURDUE UNIV.-SCHWARTZ TENNIS CENTER | TIPPECANOE | 2010-03-12 | 8:30A - 9:00A |  | CHERRY LANE AND MCCORMICK, FORCE MAIN | GROUND | LEAK OCCURRED AT LIFT STATION 300 FEET FROM TENNIS CENTER | CLEANED DEBRIS AND LIMED AREA, REPAIR LINE; LIFT STATION DISCHARGES TO WEST LAFAYETTE FORCE MAIN
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-01-15 | 12:55A - 1:45A |  | 720 PRINCESS STREET | BATH TUB | BLOCKAGE MAY HAVE BEEN IN LATERAL ONLY ONE HOME EXPERIENCED PROBLEM | VACTOR CREW JETTED LINE AND SEWER LINE WAS CLEANED
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-02-04 | 10A - 11A | 200 | SOUTH RIVER ROAD DEHART RIVER | ROAD AND GROUND | BLOCKAGE IN SEWER MAIN | SEWER CREW USED VAC TRUCK AND CLEARED BLOCKAGE
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-02-24 | 1:15P - 1:50P | 100 | 3400 KENT AVE. | STREET AND STORM DRAIN | PIECE CONCRETE IN SEWER CAUSED BLOCKAGE | REMOVED CONCRETE AND CLEANED SEWER
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-04-08 | 10:20A - 11:30A | 50 | 408 CATHERWOOD DRIVE | STORM SEWER | BLOCKAGE GAS MAIN BORED THROUGH PRIVATE SEWER | DEVELOPER NOTIFIED AND REPAIRING SEWER BREAK
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-05-05 | 9:30A - 10:45A | 0 | 3315 KENT AVE. | SEWER TRENCH AND DRAINED BACK TO SEWER | CONSTRUCTION RELATED LATERAL CONNECTION | SEWER WILL BE CLEANED PRIOR TO FUTURE CONNECTIONS
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-05-25 | 8:15A - 9:00A | 300 | MH ON CUMBERLAND AVE NEAR US 52 | GROUND, STORM DRAIN AND RETENTION POND | LOSS OF POWER TO STATION CONTROLS | CLEANED DEBRIS FROM PUMP AND RETURNED EQUIPMENT TO SERVICE
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-06-22 | 3:50A |  | GREEN MEADOWS LIFT STATION; 316 EAST PINE AVE | GROUND & JORDAN CREEK | RAIN 1.38"
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-08-04 | 5:30P - 8P | 300 | 3049 GEORGETON ROAD | BASEMENT | SEWER BLOCKED BY TREE ROOTS | TREE ROOTS CUT OUT SEWER CLEANED OUT REGULAR PREVENTATIVE MAINTENANCE
IN0024281 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-09-10 | 7:30P - ? |  | SHERATON INN LIFT STATION | GROUND AND STORM SEWER | FORCE MAIN AIR RELEASE VALVE FAILED | USE VACTOR TRUCK TO PREVENT FURTHER DISCHARGE, FIX VALVE
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2010-09-29 | 8:25P - ONGOING | 500 | 401 SAGAMORE PARKWAY DOG N SUDS | PARKING LOT STREET | PRIVATE SEWER GREASE BLOCKAGE | CLEARED UP AND CLEARED BLOCKAGE AND EDUCATE PROPERTY OWNER ON NEED FOR GREASE TRAP MAINTENANCE
IN0041866 | PRAIRIE UTILITIES | TIPTON | 2010-08-26 |  |  | SECONDARY CLARIFIER | FINAL AERATION PUMP | BYPASSING POLISHING PONDS TO CLEAN ORGANIC MATTER | WILL RESULT IN HIGHER QUALITY EFFLUENT
| SHARPSVILLE | TIPTON | 2010-08-11 | ? - 16:00 | 4860 | DIV A STATION A PUMP PIT | MUD CREEK | 2.3" OF RAIN IN 30 MINUTES
IN0021474 | TIPTON MUNICIPAL STP | TIPTON | 2010-03-13 | 2:45P - 6:00A(3/14) | 14100 | DIV A STATION A PUMP PIT | MUD CREEK | GROUND THAW RAIN 1.7"
IN0021474 | TIPTON MUNICIPAL STP | TIPTON | 2010-03-28 | 11:34P - 3:00A (3/29) | 15645 | DIV. A STATION A. PUMP PIT | MUD CREEK | RAIN 1.5" | WILL CHECK FOR SUMP PUMPS CONNECTED TO SEWERS
IN0021474 | TIPTON MUNICIPAL STP | TIPTON | 2010-06-22 | 06:42 - 03:00 (6/23) | 57685 | DIV A STATION A PUMP PIT SHARPSVILLE | MUD CREEK | PRECIPITATION 2.4" RAIN WEEK BEFORE 3.4"
IN0021474 | TIPTON MUNICIPAL STP | TIPTON | 2010-11-25 | 10:00A - 10:00P | 6772 | DIV. A, STATION A, PUMP PIT | MUD CREEK | RAIN 2.8"
IN0040762 | WINDFALL CITY MUNICIPAL STP | TIPTON | 2010-03-13 | 10:00A - 2:30P (3/14) | 30000 | MANHOLE 3 AND 4 | STORM SEWER | RAIN 2" | REDUCED FLOWS FROM LS 2 AND 3
IN0040762 | WINDFALL CITY MUNICIPAL STP | TIPTON | 2010-03-28 | 1:00P - 7:00A (3/29) | 20000 | MH 3 AND 4 | STORM SEWER | RAIN 1.33" | REDUCED FLOWS FROM LS 2 AND 3
IN0040762 | WINDFALL CITY MUNICIPAL STP | TIPTON | 2010-06-15 | 7:30A - 3P | 150 | MH #4 | STORM SEWER | RAIN .78" + .36" + 1.3" | REDUCED FLOWS FROM LIFT STATIONS AND PLANT AND L.S. UPDATES PLANNED FOR SUMMER 2010
IN0040762 | WINDFALL CITY MUNICIPAL STP | TIPTON | 2010-06-21 | 7:15A - 4:15 (6/24) | 40000 | MH 3 AND 4 | STORM SEWER | RAIN 3.42" | REDUCED FLOWS FROM LS 2 AND 3 PLANT AND MAIN LS UPGRADES SCHEDULE FOR SUMMER 2010
IN0020681 | LIBERTY MUNICIPAL STP | UNION | 2010-06-21 | 11:30A - 2:30A |  | SS0 # 006 AND SS0 # 003 | SILVER CREEK | RAIN 2.25"
| ARBORS AT RED BANK APARTMENTS | VANDERBURGH | 2010-07-26 | 8A - 11A |  | LAKESIDE DRIVE |  | ROOTS AND GREASE BACK UP | PLUMBING CONTRACTOR CLEARED BLOCKAGE INCREASE FUTURE MAINTENANCE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-01 | 7:30A - 4:15P | 175 | 720 S. BURKHARDT ROAD | GROUND | BLOCKAGE CAUSED BY DEBRIS THAT FELL INTO OPEN LINE | CONSTRUCTION COMPANY TO REPAIR OPEN PIPE AND FLUSH LINE RECHECK LINE PERIODICALLY
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-14 | 14:15 - 15:00 | 20 | 1818 DIVISION STREET | BASEMENT | SEWER LINE BLOCKED CAUSING RESTRICTED FLOW | FLUSHED AND CLEARED BLOCKAGE HAD TO LIST OF SITES TO BE T.V.
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-20 | 1:15P - 1:30P | 25 | 1763 HICKS DR | GROUND | BLOCKAGE IN SANITARY LINE | UNBLOCKED LINE. WILL TV
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-21 | 16:45 - 18:30 | 40 | 666 GREENVIEW DRIVE | HOUSE | BLOCKAGE GREASE | CLEARED BLOCKAGE RE CHECK LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-21 | 17:05 - 23:00 | 35 | 1750 EAST DELAWARE | BASEMENT | BLOCKAGE | REMOVED BLOCKAGE AND RECHECK LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-21 | 7:30P - 9:00P | 40 | 1120 RICHMOND | GROUND | GREASE IN LINE | FLUSHED LINE AND CLEANED THOROUGHLY
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-21 | 17:10 - 20:00 | 45 | 5001 WARREN DRIVE | GROUND | BLOCKAGE ROOT BALL | REMOVED ROOT BALL AND SCHEDULE TO T.V. LINES
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-01-22 | 1:30P - 1:55P |  | CROSS POINTE & LOGAN | UNNAMED DITCH | OBSTRUCTION IN 8" MAIN | AFTER LINE IS ACCEPTED FOR MAINTENANCE BY EVANSVILLE UTILITY THEN ADD TO PREVENTATIVE MAINTENANCE SCHEDULE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-02-06 | 18:45 - 21:45 | 30 | 216 LOGWOOD DRIVE | GROUND | ROOT BLOCKAGE | RAN SEWER LINE AND REMOVED BLOCKAGE WILL TELEVISE IN FUTURE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-02-08 | 19:00 - 19:30 | 15 | 201 EAST MARYLAND STREET | BATHROOM SINK | ROOT BLOCKAGE | REMOVED BLOCKAGE TELEVISE LINE TO CHECK FOR OTHER PROBLEMS
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-02-08 | 3:45P - 7:30P | 40 | 751 CROSS STREET AND 201 EAST MARYLAND STREET | BATHROOM SINK | ROOT BLOCKAGE | RAN SEWER LINE AND REMOVED BLOCKAGE WILL TELEVISE IN FUTURE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-02-24 | 16:30 - 18:00 | 25 | 424 SHERIDAN ROAD | GROUND | BLOCKAGE | FLUSHED LINE AND FLOWING WAS NORMAL ON DEPARTURE WILL TELEVISE LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-02-25 | 12P - 8P | 100000 | KENTUCKY CSO | OHIO RIVER | CONTRACTOR OVERLOADED SEWER WHILE PUMPING OUT GROUND WATER AND BYPASS PUMPING AT SAME TIME | NONE REQUIRED, CONTRACTOR WAS PUT ON NOTICE AND INSTRUCTED TO SLOW DOWN PUMPING
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-02-26 | 4:10P - 6:30P | 30 | MANHOLE AT 3001 GALAXY DR | GROUND | BLOCKAGE IN LINE | CLEARED BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-02-27 | 2:55P - 5:29P | 100 | 2800 KOTTER AVE 6" CLEAN OUT | GROUND | RAGS & TOWELS IN LINE | CLEANED AND FLUSHED DOWN STREAM, LIMED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-01 | 9:45A - 10:45A | 5 | 6600 GREENCOVE | GROUND | CLEAN-OUT PURGING | FOUND BABY WIPES AND PAPER TOWELS. CLEANED LINE.
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-02 | 10:00A - 8:00P | 100000 | KENTUCKY CSO | OHIO RIVER | PUMPS USED BY CONTRACTOR REQUIRED MORE HEAD PRESSURE THAN ROOM IN SEWER | CONTRACTOR PUT ON NOTICE ABOUT THIS ISSUE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-02 | 6:15P - 11:00P | 40 | 406 S. GREENSBURG RD. | GROUND | GREASE BLOCKAGE IN LINE | FLUSHED LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-06 | 12:08P - 14:30P | 100 | 1751 SPRING STREET MANHOLE | STREET TO COMBINED SEWER | BLOCKAGE | DISPATCH CREW IMMEDIATELY FLUSHED LINE TO OPEN BLOCKAGE AND T.V. LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-11 | 2:15P - 3:45P | 10 | 106 S. ST. JAMES PROPERTY LINE CLEAN OUT | GROUND | LATERAL LINE HAD OBSTRUCTION | FLUSHED LINE WITH ROOT NOZZLE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-12 | 2:30P - 5:30P | 15 | 5300 CUNNINGHAM LATERAL BLOCKAGE | BASEMENT | LATERAL LINE BROKEN | REPAIRED LATERAL LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-13 | 12:30P - 2:24P | 25 | 4816 RIDGEKNOLL, MAIN BLOCKAGE | BASEMENT DRAIN | MAIN SEWER SERVICING PROPERTY BLOCKED IN EASEMENT | FLUSHED SEWER TO RELIEVE BLOCKAGE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-22 | 9:10A - 10:10 | 30 | 669 GREEN VIEW DR MANHOLE | GROUND | BLOCKAGE | FLUSHED LINE TO REMOVE OBSTRUCTION
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-25 | 5:10P - 7:15P | 3000 | 7512 E. POWELL | GROUND | BLOCKAGE FOUND IN SEWER MAIN | FLUSHED LINE WITH ROOT NOZZLE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-28 | 7:30P - 9:15P | 2625 | 401 BELMONT MH IN YARD | GROUND | RAIN .47 | CLEANED LINE TO REMOVE OBSTRUCTION
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-31 | 9:10A - 11:15A |  | MH AT 1137 W. MILL RD | GROUND | OBSTRUCTION | FLUSHED MAIN WITH ROOT NOZZLE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-31 | 3:20P - 6:30P | 19000 | 5101 N. 1ST AVE. MANHOLE | GROUND | OBSTRUCTION | REMOVED OBSTRUCTION. LINE ADDS T CLEANING SCHEDULE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-03-31 | 1:00P - 2:45P | 1575 | 2410 N. GOVERNOR 6" CLEANOUT | GROUND | BLOCKAGE | FLUSHED CLEANOUT TO REMOVED BLOCKAGE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-04-05 | 1P - 1:30P | 150 | 1937 SOUTH WALNUT LANE MANHOLE | GROUND | OBSTRUCTION | FLUSHED LINE TO REMOVE OBSTRUCTION AND CLEANED AREA ALSO ADD LINE TO BI-ANNUAL CLEANING AND TELEVISE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-04-06 | 7:45A - 9:30A | 25 | 1937 WYNDCLYFF CT CLEANOUT | GROUND | OBSTRUCTION | FLUSHED LINE TO REMOVE OBSTRUCTION AND BI-ANNUAL CLEANING SCHEDULE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-04-14 | 10A - 2P | 18442 | KENTUCKY CSO | OHIO RIVER | CONTRACTOR BYPASS PUMPING WHILE INSPECTING MANHOLE SURGE OF WATER CROSSED WEIR WHEN WATER WAS RELEASED | CONTRACTOR WAS PUT ON NOTICE AND MUST SUBMIT A PLAN TO ENSURE OVERFLOWS DO NOT OCCUR
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-04 |  | 300 | 501 PLAZA MH | GROUND | RAIN 1.6" | CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-08 | 1:20P - 2:15P | 1 | SYCAMORE AND VANN CLEANOUT | GROUND | PRIVATE PARTY LATERAL OBSTRUCTION | REMOVED OBSTRUCTION AND CLEANED AFFECTED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-19 | 12:05P - 1:00P | 275 | 3500 JACKSON AVE MH | GROUND | BLOCKAGE FOUND IN SEWER MAIN BEHIND PROPERTY | REMOVED OBSTRUCTION
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-26 | 11:55A - 1P | 22394 | 3401 POLLACK | BASEMENT | BLOCKAGE IN MAIN | REMOVED BLOCKAGE CCTV MAIN SEWER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-28 | 4P - 8P | 1064000 | WEINBACH L.S. OUTFALL #11 | PIGEON CREEK | POWER FAILURE | RESTORED POWER POSSIBLE DISCIPLINE FOR MANAGER NOT RESPONDING TO ALARMS
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-28 | 9P - 10P | 875000 | EAST PLANT OUTFALL #103 | OHIO RIVER | ULTRASONIC LEVEL DETECTOR FAILED | RETURNED GATE AND MONITORED PERFORMANCE DETECTOR BEING REPLACED POSSIBLE DISCIPLINE FOR MANAGER NOT RESPONDING APPROPRIATELY
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-29 | 6:45P - 8:20P | 20 | UTILITY CLEAN OUT | GROUND | OBSTRUCTION | REMOVED BLOCKAGE SPREAD LIME CCTV LINE SEGMENT
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-05-29 | 6:45P - 8:20P | 20 | 1751 DALEHAVEN CLEAN OUT | GROUND | OBSTRUCTION | REMOVED BLOCKAGE CLEANED AFFECTED AREA SPREAD LIME CCTV LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-06-03 | 2:30P - 3:40P | 400 | 1320 LEE CT MANHOLE | GROUND | GREASE | COMPLEX NOTIFIED OF FINDINGS. WILL MONITOR GREASE DISCHARGES
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-06-06 | 3:30P - 3:35P | 1 | 2625 RUSTON - CLEANOUT | GROUND | BLOCKAGE | REMOVED BLOCKAGE, LIMED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-06-08 | 1P - 1:30P | 20 | 801 N KELSEY CLEANOUT | GROUND | OBSTRUCTION AT LATERAL TAP | FLUSHED MAIN AND CLEAN OUT CCTV LATERAL AND MAIN
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-06-15 | 10:00A - 11:00A | 7200 | 4401 CASS AVE - MH | GROUND | BLOCKAGE IN SEWER MAIN | REMOVED OBSTRUCTION, APPLIED LIME
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-07-01 | 10:30A - 12P | 300 | EASTSIDE POTW DRAINAGE CHANNEL | GROUND | STORAGE PAD DRAIN BLOCKED DURING CLEANING OPERATIONS CAUSING OVERFLOW | FLUSHED SEWER REOPENING DRAIN SOLIDS SCRAPED UP LIME ADDED TO GROUND AND WILL RESEED MORE FREQUENT INSPECTION
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-07-07 | 8:30P - 9P |  | MAXWELL & NORTH SPRING DISCHARGE HOSE FROM BYPASS PUMP | STREET | HOSE ON 6" TEMPORARY PUMP AT OAK HILL CSO BURST | HOSE REPLACED WITH THICKER PLY MATERIAL AND STREET CLEANED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-07-08 | 7:45P - 9P |  | 806 MULBERRY | BASEMENT | PRECIPITATION 2" SHORT TIME | INSPECTED SEWER IT WAS FREE FLOWING REMINDER OF BACK FLOW DEVICES
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-07-08 | 7:45P - 9P |  | 1410 ADAMS | BASEMENT | PRECIPITATION 2" SHORT TIME | INSPECTED SEWER IT WAS FREE FLOWING REMINDER OF BACK FLOW DEVICES
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-07-13 | 10:55A - 11:25A | 75 | 700 HERNDON | BASEMENT | RAIN EVENT WATER FROM DOWNSPOUT DRAINS BACKUP INTO BATHROOM | MAIN FLOWING AND FREE OF ANY RESTRICTIONS
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-07-13 | 6:15P - 10:15P | 1500 | MH NORTH OF IROQUOIS LS | GROUND | ROOT OBSTRUCTION | AFFECTED AREA IMMEDIATELY CLEARED OF WASTEWATER AND LIME APPLIED ADDED TO PREVENTATIVE MAINTENANCE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-07-15 | 9:30A - 11:30A | 200 | MH NORTH OF IROQUOIS LS | GROUND | ROOT OBSTRUCTION DOWNSTREAM OF LS | REMOVED OBSTRUCTION FROM MAIN CLEARED AREA AND APPLIED LIME
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-10-02 | 12P - 2:50P | 10 | 1812 SHELBY | GROUND | OBSTRUCTION OF GREASE AND ROOTS | REMOVED OBSTRUCTION VACUUMED SEWAGE AND APPLIED LIME LINE SEGMENT WILL BE TV'D
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-10-12 | 10:30A - 11:15A | 40 | 301 SOUTH ROYAL | GROUND | OBSTRUCTED LATERAL | OBSTRUCTION CLEARED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-10-21 | 11:00A - 12:20P | 50 | 2808 FRISSE MH | GROUND | ROOTS IN LINE | REMOVED OBSTRUCTION AND CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-10-26 | 5:10P - 8:30A (10/27) | 10 | 609 S. ALVORD | GROUND | ROOTS IN LINE | FLUSHED LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-11-19 | 1P - 2P | 500 | 732 SOUTHFIELD | GROUND | OBSTRUCTION | COULD NOT ACCESS MH DUE TO STORAGE BARN, REMOVED STORAGE BARN AND FLUSHED AFFECTED LINE, VACUUMED AND LIMED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-11-24 | 1:00P - 1:45P | 75 | MH 3225 AUTUMN WOOD WAY | GROUND | RAIN 2" | CREW FLUSHED LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-11-25 | 11:30P - 12:30A (11/26) | 200 | 4220 OXMOOR | BASEMENT | GREASE OBSTRUCTION 2.99" RAIN PROPERTY ON DEAD-END SEWER UTILITY | FLUSHED LINE SEGMENT AND ADVISED PROPERTY OWNER TO INSTALL BACK FLOW VALVE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-12-01 | 12:15A - 1:45A | 1000 | 1226 & 1228 MACARTHUR CIRCLE | GROUND | ROOT AND GREASE OBSTRUCTION | REMOVED AFFECTED SOIL AND APPLIED LIME WILL ADD NEW SOIL AND SEED RESIDUAL REMOVED WAS TAKEN TO GRIT DISPOSAL SITE LINE WILL BE TREATED WITH ROOTX AND CCTV'D
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-12-06 |  |  | 7200 WASHINGTON AVE BASEMENT DRAIN | BASEMENT | ROOTS IN MAIN | FLUSHED LINE AND REMOVED ROOTS
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2010-12-10 | 7:35P - 9P | 2 | 1817 EAST MICHIGAN CLEANOUT | GROUND | FLUSHED LATERAL AND REMOVED BLOCKAGE | FLUSHED LATER AREA CLEANED AND APPLIED LIME
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-01-13 | 18:40 - 20:30 | 100 | 4129 KEDZIE | GROUND | BLOCKAGE APPROX. 122 FEET FROM SURGING MANHOLE | JETTED SEWER AND WILL T.V.
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-01-14 | 2A - 2:30A | 52000 | 7TH AVENUE EAST CSO AREA | OHIO RIVER | PLANT SHUTDOWN TEMPORARILY SO OUTFALL COULD BE INSPECTED PROCESS TOOK LONGER THAN EXPECTED RESULTING IN OVERFLOW | PRECAUTIONS WERE TAKEN TO TRY AND PREVENT THIS FROM HAPPENING, WILL EVALUATE WHAT ELSE COULD HAVE BEEN DONE AS PRECAUTIONS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-01-14 | 2A - 4A | 12000 | DELAWARE CSO OUTFALL AREA | UNNAMED DITCH THAT FEEDS PIGEON CREEK | PLANT SHUTDOWN TEMPORARILY SO OUTFALL COULD BE INSPECTED PROCESS TOOK LONGER THAN EXPECTED RESULTING IN OVERFLOW | PRECAUTIONS WERE TAKEN TO TRY AND PREVENT THIS FROM HAPPENING, WILL EVALUATE WHAT ELSE COULD HAVE BEEN DONE AS PRECAUTIONS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-01-20 | 3:25P - 5:00P | 30 | 8440 WOLFCREEK DR. | GROUND | PROPERTY LINE SURVEYOR'S STAKE IN LINE | REMOVED STAKE AND CLEANED LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-01-21 | 9:30P - 9:45P | 30 | 4129 KEDZIE | GROUND | MANHOLE HOLDING ON TOP | FLUSHED LINE AND OPENED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-01-22 | 15:45 - 20:30 | 150 | 4420 HOUGE ROAD | GROUND | PRECIP .82" | MONITORED LINE TO ENSURE LEVEL DROPPING RECHECK SEWER LINE AFTER RAIN EVENT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-01-24 | 6P - 7P |  | 3-5 RICHART | BASEMENT | PRECIP .64" | FLUSHED AND CLEANED LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-02-07 | 2P - 10A (2/8) | 167000 | FRANKLIN CSO (016) | PIGEON CREEK | INTERCEPTOR GATE CONTROLLER FAILURE | GATE CONTROLLER IS BEING REPAIRED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-02-10 | 11:05A - 1:15P | 10 | 1262 SHEFFIELD DRIVE | GROUND | BLOCKAGE IN SEWER MAIN | CLEARED LINE AND CLEANED UP AND LIMED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-02-14 | 10:45A - 1:00P | 5 | 4307 CHADWICK PROPERTY - LINE CLEANOUT | GROUND | LATERAL SERVICING PROPERTY HAD OBSTRUCTION BETWEEN PROPERTY LINE AND MAIN SEWER | FLUSHED LINE TO REMOVE OBSTRUCTION
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-02-15 | 8:30P - 2:30A (2/16) | 20000 | FRANKLIN CSO | PIGEON CREEK | WATER MAIN BREAK | REPAIRED WATER MAIN BREAK
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-02-16 | 8:00A - 3:30P | 40000 | OHIO ST CSO | OHIO RIVER | BLOCKAGE IN LINE THAT FOLLOWS DIVERSION STRUCTURE | LINE WAS CLEANED AND WILL BE CLEANED MORE FREQUENTLY
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-03-07 | 13:38 - 15:45 | 200 | MILL ROAD AND FULTON AVE MANHOLE | STREET UNNAMED DITCH | BLOCKAGE | DISPATCH CREW IMMEDIATELY FLUSHED LINE TO OPEN BLOCKAGE AND T.V. LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-03-08 | 15:45 - 17:15 | 20 | 614 BIDDLE CT | GROUND | BLOCKAGE | FLUSHED SEWER MAIN CLEARED MAIN FLOWING WELL UPON DEPARTURE AND WILL T.V. LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-04-03 | 10:20A- 12:25P | 3125 | FULTON AVE AND MILL ROAD | GROUND AND TRIB TO PIGEON CREEK | LINE OBSTRUCTED | FLUSHED LINE WITH ROOT NOZZLE AND TELEVISE SEWER TO FIND CAUSE
IN0023956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-04-13 | 9A - 10A | 50000 | 7TH EAST CSO | OHIO RIVER | CHAIN ON BAR SCREEN FAILED GATE MUST BE IN CLOSED POSITION TO REPAIR | OVERFLOW QUICKLY DILUTED LOW FLOW HIGH RIVER AND EVALUATE INSPECTION METHODS FOR STATION TO BE MORE PREDICTIVE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-04-24 | ? |  | 8200 HEATHER PLACE M.H. | GROUND AND TRIB. TO LITTLE PIGEON CREEK | .57" RAIN AND SIGNIFICANT ROOT INFILTRATION DOWNSTREAM | AGGRESSIVE ROOT TREATMENT MONITORING AND CCTV LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-04-25 | 12:50A - 2:00P | 350 | 704 SHEFFIELD DR. MANHOLE | GROUND | OBSTRUCTION IN MAIN SEWER | REMOVED OBSTRUCTION, WILL MONITOR
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-04-26 | 10:25A - 2:15P | 50 | 516 N 7TH AVE | GROUND | CONSTRUCTION | 18" LINE CAPPED OFF NOT ALLOWING FLOW INTO MAIN LINE. VACUUMED AND FLUSHED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-05-01 | 8P - 8:15P | 75 | 2800 LONGACRE MH | GROUND | 1.4" RAIN QUICKLY SURCHARGING SYSTEM | CLEANED AREA INVESTIGATE POSSIBLE INFILTRATION SOURCES
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-05-02 | 2:40P - 4:10P | 450 | 727 TULIP MH | STREET | OBSTRUCTION IN MAIN | CLEANED AREA CCTV INVESTIGATE POSSIBLE ROOT INFILTRATION
IN0033073 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-05-10 | 6:15P - 8:45P | 3000 | 1701 S. RED BANK RD | CREEK | OBSTRUCTION CAUSED WASTEWATER TO PURGE FROM MH | REMOVED OBSTRUCTION AT 150'
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-05-12 | 11:15A - 2:40P | 400 | 670 SCHUTTE MH | GROUND | AIR RELIEF VALVE FAILURE | VACUUMED MH. REPLACED AIR RELIEF VALVE, SPREAD LIME
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-05-13 | 10:30A - 11:15A | 225 | 4016 W. MARYLAND ST. MH | GROUND | WATER PURGING FROM MH | RODDED LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-05-19 | 10:40P - 11:45P | 300 | 5606 TWICKINGHAM BASEMENT | GROUND | BLOCKAGE | REMOVED OBSTRUCTION
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-05-28 | 4P - 8P | 3750000 | WEST PLANT 7TH AVE | OHIO RIVER | POWER FAILURE | RESTORED POWER POSSIBLE DISCIPLINE FOR MANAGER NOT RESPONDING TO ALARMS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-06-10 | 8:00A - 8:35A | 525 | 669 GREENVIEW DR. MH | GROUND | OBSTRUCTION | REMOVED OBSTRUCTION, CCTV MAIN
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-06-27 | 8P - 5:30A (6/28) | 40 | HWY 41 AZTECA MILLING SERVICE ROAD | GROUND | 12" FORCE MAIN BREAK CAUSED SINK HOLE | EXCAVATED AREA REPAIRED MAIN AND MONITORED VISUALLY 72 HOURS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-07-13 | 4:40P - 8P | 150 | 8 TULIP AVENUE CLEANOUT | GROUND | PAPER SUBSTANCE OBSTRUCTION | OBSTRUCTION WAS FLUSHED ARE CLEANED AND LIMED ADDED TO PREVENTATIVE MAINTENANCE SCHEDULE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-07-14 | 1P - 2P | 2100 | #3 OAK MEADOW LS | GROUND UNNAMED DITCH | TREE ROOTS IN POWER CONDUIT AND SEVERED THE POWER SUPPLY | GENERATOR WAS PUT IN PLACE TO SUPPLY SITE POWER AFFECTED AREA VACUUMED UPGRADED SCADA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-07-19 | 5P - 6:15P | 11250 | 900 SOUTH TEKOPPEL GRIT CHAMBER | GROUND HOWELL WETLAND | PARTIAL TREATMENT WET WEATHER EVENT .50" IN 15 MINS. | REDUCED THE FLOW TO THE DESIGNED STORM WATER FLOW THESE ACTIONS STOPPED THE SPLASHING AND OVERFLOWING
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-07-23 | 10:05A - 10:55A | 50 | 1407 NORTH BOEHNE CAMP ROAD | GROUND | OBSTRUCTION COULD NOT BE IDENTIFIED | FLUSHED MAIN SEGMENT AND BYPASS WAS ELIMINATED WILL CCTV SCHEDULE TO CHECK CONDITION OF SEWER MAIN
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-08-28 | 1:30P -1:31P | 10 | 3112 KENSINGTON DR. | GROUND | OBSTRUCTION IN LATERAL | FLUSHED LATERAL
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-09-07 | 4P - 5:20P | 50 | 1130 BOULDER PASS | GROUND AROUND MANHOLE | AIR RELIEF VALVE FOR FORCE MAIN WAS LEAKING | IMM. SHUT DOWN LS AND REPAIR VALVE VACUUMED RESIDUAL WASTE AND APPLIED LIME
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-09-11 | 3:42P - 4:07P | 250 | SOUTH OF HWY 62 - USI LIFT STATION - FORCE MAIN | GROUND AND TRIBUTARY TO CARPENTER CREEK | VAC PUMPED FAILED DURING INSTALLATION OF FITTINGS ON FORCE MAIN | FAILED VAC REPLACED AND AREA CLEANED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-09-11 | 1:25P - 2:30P | 50 | 4905 STRATFORD MH | STORM SEWER | TREE ROOTS OBSTRUCTING LINE | REMOVED OBSTRUCTION. AREA VACUUMED AND CLEARED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-09-22 | 6:15P - 9:45P | 25 | 1112 WEST OREGON | GROUND | GREASE | FLUSHED LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-10-13 | 9:00A - 11:00A | 33000 | 2414 SCHUTTE RD | TRIBUTARY TO CARPENTER CREEK | LOSS OF POWER TO LS DUE TO FAILED FUSE | REPLACED FUSE AND RESTORED POWER, USED GENERATOR, CREEK FLUSHED WITH HYDRANT WATER
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-10-23 | 9:06P - 9:57P | 2 | 4101 N HIGHWAY 41 | LOWER LEVEL OF BUILDING | GREASE | FLUSHED LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-10-28 | 3:30P - 5:30P | 5 | 3028 W. MARYLAND @ CLEANOUT | GROUND | GREASE | FLUSHED LINE AND CLEANED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-11-17 | 11A - 11:15A | 10 | HARTFORD AND FIRST AVENUE MH | GROUND | BLOCKAGE | LINE FLUSHED WILL TV LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-11-19 | 1P - 2P | 500 | 732 SOUTHFIELD MH | GROUND | GREASE AND ROOTS OBSTRUCTION | SEGMENT FLUSHED LIME APPLIED WILL BE MONITORED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-11-26 | 7A - 8:15A | 250 | 123 FERNWOOD DRIVE | GROUND | TREE ROOT OBSTRUCTION 2.99" RAIN | ROOT NOZZLE USED TO REMOVE OBSTRUCTION ALL RESIDUAL CLEARED LINE SEGMENT TO BE CCTV'D
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-12-01 | 10:15A - 10:45A | 30 | 432 SHERIDAN | GROUND | TREE ROOT OBSTRUCTION AREA RECENTLY TREATED WITH ROOTX | ALL RESIDUAL CLEARED LIME APPLIED UTILITY MAINS SHALL BE TELEVISED AFTER ROOTX TREATMENT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-12-02 | 11:15A - 12:15P | 6000 | 8440 WOLFCREEK- KEY WEST LIFT STATION | GROUND PRIVATE POND | PHASE MONITOR FAILED CAUSING LOSE OF POWER TO PUMPS DID NOT ALARM BECAUSE POWER SUPPLY INTERRUPTION | MONITOR REPLACED IMMEDIATELY CREW VACUUMED WASTEWATER FROM MH ELIMINATING RELEASE WHILE L.S. WAS BEING RETURNED TO SERVICE HYDRANT WATER WAS MIXED WITH WASTEWATER TO INCREASE OXYGEN ALL WATER SCREENED THROUGH DECHLORINATION TABLETS AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-12-23 | 5:15P - 6P | 35 | STRATFORD AND MILL MH | GROUND | OBSTRUCTION | FLUSHED LINE CLEARED AFFECTED AREA AND T.V. LINE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-12-27 | 11A - 11:45A | 1 | 3112 MUENSTERMAN CLEANOUT | GROUND | ROOTS BLOCKAGE | WILL TREAT WITH ROOTX AND ALSO CLEANED AFFECTED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-12-27 | 6P - 7P | 25 | 515 WINDSOR | OPEN EXCAVATION | 8" SEWER MAIN FRACTURED WHILE WATER UTILITY REPAIRING WATER MAIN BREAK | VACUUMED EXCAVATION AREA AND CLEARED ALL RESIDUAL COMMUNICATE TO ALL UTILITY STAFF IMPORTANCE OF LOCATES
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2010-12-29 | 11A - 12:15P | 75 | 266 SOUTH SONNTAG/ 2745 MARION | BASEMENT TO GROUND | RESTRICTION IN MAIN RAIN .3" | FLUSHED MAIN CLEANED AREA WILL T.V. AND REPAIR MAIN AS NECESSARY
| WOODBRIDGE PLACE APARTMENTS | VANDERBURGH | 2010-11-08 | 8:30A - 11:00A |  | 3550 WOODBRIDGE DR. MAIN DRAIN | GROUND - CREEK |  | PLUMBER TO REPAIR MAIN DRAIN
| WOODCREEK INN & SUITES | VANDERBURGH | 2010-05-16 | 10A - ? |  | 2530 NORTH US HWY 41 | PIGEON CREEK | ELECTRICAL ISSUES WITH PUMP STATION | ELECTRICIAN ON PREMISES WILL DISCONNECT OVERFLOW FROM STORM SEWER AND ALLOW FUTURE OVERFLOWS TO GATHER IN PARKING LOT
IN0060461 | CAYUGA MUNICIPAL WWTP | VERMILLION | 2010-02-07 | 10:30A - 10:45A | 100 | MANHOLE ON WABASH STREET | ROAD | WIRES COMING FROM FLOAT BURNT UP THAT WENT TO CONTROL PANEL | PUT PUMPS ON MANUAL OVERRIDE HAVING ELECTRICIAN TO REWIRE
IN0060461 | CAYUGA MUNICIPAL WWTP | VERMILLION | 2010-03-04 | 10:30P - 2:30P | 10 | DIVISION ST. INTO BASEMENT | BASEMENT | BLOCKAGE CAUSED LEAK THROUGH PIPE | JETTED CLEAN AND REPAIRED LINE
IN0003506 | NEWPORT CHEMICAL DEPOT | VERMILLION | 2010-04-19 | 8A - 3P (4/20) | 100 | M.H. FORCE MAIN WEST OF S.R. 63 NECD | GROUND AROUND MANHOLE | OPERATIONAL FAILURE OF AIR RELIEF VALVE | AIR RELIEF VALVE WAS RECONNECTED TO FORCE MAIN WILL PERIODICALLY INSPECT OPERATIONAL OF AIR RELIEF VALVE
IN0003506 | NEWPORT CHEMICAL DEPOT | VERMILLION | 2010-07-23 | 11P - 6:55A (7/24) | 23000 | CHLORINE CONTACT TANK- OVERFLOW PIPE | LITTLE RACCOON CREEK | POWER OUTAGE AT TREATMENT PLANT AND GENERATOR ANTIFREEZE LEAK CAUSED GENERATOR TO SHUT DOWN | POWER WAS RESTORED MACALLISTER CONTACTED TO PERFORM SERVICE ON GENERATOR
IN0001601 | AET PACKAGING FILMS | VIGO | 2010-08-23 | 9A - 10A (8/24) |  | INDUSTRIAL WASTEWATER MANHOLE NO. 1 | SPRING CREEK | FAILED PIPE PLUG | PIPE PLUG HAS BEEN IMPROVED TO ENSURE PERMANENT BLOCKAGE
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-03-12 | 9:55P - 3:30A (3/13) | 4900000 | PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | RAIN .5"
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-03-22 | 2P - 10:30P | 3600000 | PRIMARY SEDIMENTATION TANK PARTIALLY TREATED | CONTACT TANK | .65 " RAIN BASIN FULL
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-03-25 | 6:30P - 4:30P (3/26) | 7200000 | PRIMARY SEDIMENTATION TANKS | BYPASS OF TREATMENT PROCESS FINAL CONTACT TANK | RAIN 1.1" BASINS FULL
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-03-28 | 11:15A - 3:45P | 1500000 | PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | BASINS FULL. SECONDARY CLARIFIER BLANKETS GETTING HIGH. PINCHED BACK FLOW TO KEEP BLANKETS FROM GOING OVER | BELT PRESSING TO MAKE ROOM IN DIGESTERS FOR WASTE ACTIVATED SLUDGE FROM SECONDARY CLARIFIERS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-04-03 | 1:37P - 6P | 3200000 | PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | PARTIALLY TREATED BASINS FULL. SECONDARY CLARIFIER BLANKETS GETTING HIGH. PINCHED BACK FLOW TO KEEP BLANKETS FROM GOING OVER | BELT PRESSING TO MAKE ROOM IN DIGESTERS FOR WASTE ACTIVATED SLUDGE FROM SECONDARY CLARIFIERS INSTALLING ADDITIONAL SLUDGE STORAGE
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-04-04 | 5:15A - 8:55A (4/5) | 1300000 | PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | PARTIALLY TREATED BASINS FULL. SECONDARY CLARIFIER BLANKETS GETTING HIGH. PINCHED BACK FLOW TO KEEP BLANKETS FROM GOING OVER | BELT PRESSING TO MAKE ROOM IN DIGESTERS FOR WASTE ACTIVATED SLUDGE FROM SECONDARY CLARIFIERS INSTALLING ADDITIONAL SLUDGE STORAGE
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-04-08 | 6:30P (4/7) - 6:00A | 6100000 | PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | RAIN .75" BASIN FULL OPENED UP BYPASS TO KEEP PRIMARY TANKS FROM OVERFLOWING ONTO GROUND | BELT PRESSING TO MAKE ROOM IN DIGESTERS FOR WASTE ACTIVATED SLUDGE FROM SECONDARY CLARIFIERS
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-06-16 | 12:40A - 5:10A | 2600000 | PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | BASINS STILL FULL HAD TO PINCH BACK FLOW TO KEEP BLANKETS FROM GOING OVER | OPENED UP BYPASS TO KEEP TANKS FROM OVERFLOWING ONTO GROUND
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-07-20 | 1:18A - 2:30A | 11200000 | BYPASS TREATMENT PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | TOO MUCH RAIN 1.6" AND TWO CLARIFIERS DOWN FOR REPAIRS AND REPLACEMENT | AERATION TANK WORK WILL BE COMPLETED IN NOVEMBER AND PHASE 1 UPGRADES
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-07-21 | 6:15P - 2:45A (7/22) | 4700000 | BYPASS TREATMENT PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | TOO MUCH RAIN 1.6" AND TWO CLARIFIERS DOWN FOR REPAIRS AND REPLACEMENT | AERATION TANK WORK WILL BE COMPLETED IN NOVEMBER AND PHASE 1 UPGRADES
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-07-21 | 5:30A - 8A (7/22) | 1200000 | BYPASS TREATMENT PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | TOO MUCH RAIN 1.6" AND TWO CLARIFIERS DOWN FOR REPAIRS AND REPLACEMENT | AERATION TANK WORK WILL BE COMPLETED IN NOVEMBER AND PHASE 1 UPGRADES
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-07-22 | 10:45A - 6P | 3000000 | PRIMARY SEDIMENTATION TANKS | FINAL CONTACT TANK | BYPASS OF TREATMENT BASINS ARE FULL REHAB PROJECT CLARIFIER 1 UNDERWAY AND CLARIFIER 4 OUT FOR REPAIRS | AERATION TANK WORK TO BE COMPLETED NOVEMBER AND PHASE 1 PLANT UPGRADES BEGIN OCTOBER
IN0025607 | TERRE HAUTE MUNICIPAL STP | VIGO | 2010-09-02 | 1:40A - 3:40 | 495000 | PRIMARY SEDIMENTATION TANK | FINAL CONTACT TANK | BASINS FULL DUE TO PINCHING OFF FLOW TO AERATION TANKS DUE TO CONSTRUCTION | CONSTRUCTION COMPLETED AND TANK BACK ON LINE
IN0055085 | WEST TERRE HAUTE MUNICIPAL STP | VIGO | 2010-03-23 | ? - 14:30 | 200 | 66 WINDMERE | GROUND | PUMP BURNT UP | PUMP TRUCK PUMPING UNTIL PUMPS ARRIVE CLEANED UP MESS AND SPREAD LIME
IN0055085 | WEST TERRE HAUTE MUNICIPAL STP | VIGO | 2010-04-08 | 12P | 2000 | 73 SOUTH THORPE PL RESIDENTIAL GRINDER | GROUND AND STREAM | EQUIPMENT FAILURE AND TOWN EMPLOYEE FORGOT TO INSTALL PUMP | REPLACED PUMP AND LEFT CONTACT INFO OF CERTIFIED OPERATOR
IN0032468 | LAFAYETTE MUNICIPAL STP | WABASH | 2010-03-17 | 11:30A - 3:15P | 937500 | PEARL RIVER CSO 006 | WABASH RIVER | GRINDER BROKE DOWN | TOOK ONE OUT TO GET LIFT STATION BACK ON LINE
IN0020362 | NORTH MANCHESTER MUN. STP | WABASH | 2010-11-26 | 9A - 11:30A | 200 | MH 103 2ND STREET | GROUND | SEWER BLOCKAGE | JETTED SEWER CLEAN WILL CONTINUE MAINTENANCE
IN0063002 | POET BIOREFINING, N MANCHESTER | WABASH | 2010-07-17 | 3P - 4P | 40 | ADMIN BUILDING BASEMENT SUMP PUMP | STORM SEWER TO POND 1 | LS PUMP AND ALARMS FAILED CAUSING OVERLOAD | COLLECTED AND DISPOSED OF SOLIDS SAMPLES TAKEN FOR FECAL COLIFORM AND LS REPAIRED POSSIBILITY REROUTING SUMPS TO SANITARY SEWER
IN0024741 | WABASH MUNICIPAL STP | WABASH | 2010-05-26 | 12:00A - 5:00A | 5455000 | LIFT STATION #1, MIDDLE ST. (OUTFALL 004) | WABASH RIVER | TRANSFORMER FAILURE ON POWER POLE | DUKE REPLACED TRANSFORMER AND RESTORED POWER
IN0024741 | WABASH MUNICIPAL STP | WABASH | 2010-07-18 | 4:50A - 2:45P (7/19) | 14591000 | MIDDLE STREET LS 1 OUTFALL #4 | WABASH RIVER | EQUIPMENT FAILURE MECHANICAL ERROR | PULLED PUMP AND PUMP REPAIR COMPANY SET BACK UP PUMP
IN0024741 | WABASH WWTP | WABASH | 2010-01-02 | 11:23A - 12:40P | 24050 | LS #1 MIDDLE ST. OUTFALL #004 | WABASH RIVER | OPERATOR LEFT BOTH PUMPS IN OFF POSITION WHEN LEAVING | LS ACTIVATED ALARM SYSTEM OF BYPASS, CALL OPERATOR ARRIVED AND SWITCHED BOTH PUMPS TO AUTO
IN0022420 | BOONVILLE MUNICIPAL STP | WARRICK | 2010-01-04 | 7:30P - 7:45 | 200 | AIGNER LIFT STATION | GROUND | PUMP WAS PLUGGED | CLEARED DEBRIS AND SENT PUMP FOR REPAIRS, RENTED PUMP IN INTERIM
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2010-05-02 | 17:00 - 17:30 |  | M.H. #238 | UNKNOWN | BLOCKAGE IN SEWER MAIN | BLOCKAGE CLEARED BY SUB-CONTRACTOR
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2010-06-13 | 1:30P - 5:30P | 50 | THARA JANES REST. SOUTH 61 AND 68 INTERSECTION | GROUND | GREASE BUILDUP | INSPECTED AREA AND APPLIED LIME AND A NEWLY UPDATED TOWN ORDINANCE WILL BE DRAFTED
IN0040282 | LYNNVILLE MUNICIPAL STP | WARRICK | 2010-07-19 | 6P - 6:16P |  | VINE AND HWY 68 MH | DITCH | LIGHTNING BLEW OUT CONTROL PANEL OF MAIN LIFT STATION | ALARM NOTIFIED AND SENT CREW TO REPAIR TREATED AREA WITH LIME
IN0040280 | LYNNVILLE MUNICIPAL STP | WARRICK | 2010-09-20 | 6:45A - 9:15A | 100 | SE CORNER HWY 61 AND 68 | GROUND | GREASE BUILD UP IN 8" LATERAL | OWNER INSTRUCTED TO CHECK GREASE TRAP MORE OFTEN
IN0040882 | LYNNVILLE MUNICIPAL STP | WARRICK | 2010-11-23 | 2:15P - 2:40P | 100 | 1 1/2 FORCE MAIN IN LYNNVILLE PARK | GROUND | DAMAGED DURING CONSTRUCTION | LS TURNED OFF FOR REPAIRS
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-02-12 | 8:45A - 9:55P | 15 | 5099 JAMESTOWN DR. | GROUND | SEWER DOWNSTREAM OF ADDRESS CLOGGED WITH ROOTS | MAIN WAS IMMEDIATELY JET CLEANED AND CLOG CLEARED
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-02-14 | 11:00A - 2:30P | 1000 | MH14-205 | DRAINAGE DITCH | SEWER DOWNSTREAM OF MH CLOGGED WITH ROOTS | MAIN WAS IMMEDIATELY JET CLEANED AND CLOG CLEARED
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-03-20 | 5:30P - 7:30P | 1000 | MANHOLE AT 4700 HERITAGE DRIVE | GROUND | SANITARY SEWER MAIN WAS OBSTRUCTED WITH GREASE | SPILLED SEWAGE WAS VACCED UP AND DISPOSED AT PLANT WILL BE T.V.ED AND ANY DEFECTS WILL BE REPAIRED
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-04-26 | 12:50P - 1:15P | 600 | 4511 PINE DRIVE | BASEMENT AND GROUND | SEWER MAIN CLOGGED WITH ROOTS | CLEANED WITH HYDRAULIC ROOT CUTTER
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-05-02 | 6A - 6:15A | 200 | DOWNSTREAM OF INVERTED SIPHON AT OLD PLANT LS | GROUND | HEAVY RAIN AND CLOGGED PUMP DECREASED PUMPING CAPACITY | CREW WAS ON SITE B/C DETECTED PROBLEM WITH PUMP 1 SET UP EMERGENCY PUMP ASAP CONTINUE CURRENT PREVENTATIVE MAINTENANCE
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-05-02 | 6A - 6:15A | 200 | INVERTED SIPHON AT OLD PLANT L.S. | GROUND | HEAVY RAIN AND PUMPS AT L.S. BECAME CLOGGED | SET UP EMERGENCY PUMP AND LAST WEEK PREFORMED THE ANNUAL INSPECTION OF THESE PUMPS
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-06-17 | 8:00P - 9:30P | 10000 | 5600 MARTIN RD; MH 20-54 AND 20-72 | GROUND TO PRIVATE LAKE | DEBRIS IN SEWER MAIN | CLEANED SEWER LINE
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2010-09-30 | 10A - 10:30A | 800 | MANHOLE 10-151 | GROUND STORM SEWER | GREASE BLOCKAGE IN SANITARY SEWER MAIN | IMMEDIATELY JETTED AND CLEARED BLOCKAGE POOL SEWAGE WAS CLEANED UP LINE PLACED ON PERIODIC CLEANING LIST
IN0021059 | NEW PEKIN MUNICIPAL STP | WASHINGTON | 2010-05-02 | 8P - 2A (5/3) | 150000 | CHARLES STREET L.S. | BLUE RIVER | PRECIPITATION 3 - 4"
IN0020010 | HAGERSTOWN MUNICIPAL STP | WAYNE | 2010-01-27 | 5:30 - 9:30 | 1000 | 55 LEXINGTON LANE MANHOLE | GROUND DITCH | CLOG IN SEWER LINE | JETTED LINE TO CLEAR CLOG WILL RECHECK IN 2 DAYS AND SPREAD LIME ON AFFECTED AREA
IN0025615 | RICHMOND MHP | WAYNE | 2010-04-08 | 8:46A - 7:00P | 160000 | 143-102, 163-002, 182-092 | WHITE WATER RIVER | RAIN 1.4" | RELIEVE PRESSURE ON EAST SIDE BASIN
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-03-13 | 8:35A - 9:16 (3/14) | 300000 | MANHOLES | GROUND BY MANHOLES | RAIN 2" OPENED MAIN FLOOD GATE TO PREVENT FLOODING RESIDENTIAL HOMES
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-03-14 | 10:42A - 7:30A (3/15) | 300000 | 2380 LIBERTY AVE SYPHON CSO-002 | WHITE WATER RIVER | RAIN 2" SYPHON BROKE | SYPHON REPAIRED
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-04-08 | 2:00A - 8:46A | 180000 | 143-102, 163-002, 182-092 | WHITE WATER RIVER | RAIN 1.4" BYPASS TO PREVENT OVERFLOW FROM MANHOLES | INVOLVED IN ON-GOING PLAN TO ELIMINATE BYPASSES
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-04-08 | 2:00A - 8:00A | 42000 | 257-002 | FIELD NEARBY | #2 PUMP FAILED | MANUAL POWER ON #3 PUMP
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-06-09 | 4:41A - 6:30P | 300000 | MH 143-102, 162-106, 163-002, 182-092 | GROUND TO EAST FORK WHITE RIVER | HEAVY RAINS 1.68" | INVOLVED IN AN ONGOING MASTER PLAN TO ELIMINATE OVERFLOW EVENTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-07-12 | 4:26A - |  | 143-102, 163- 002, 182-092 EASTSIDE INTERCEPTOR | GROUND TO EAST FORK WHITE WATER RIVER | HEAVY RAINS 1" | INVOLVED IN AN ON GOING MASTER PLAN TO ELIMINATE OVERFLOW EVENTS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-11-08 | 8:10A - 9:40A (11/10) | 8572000 | FINAL CLARIFIERS | EAST FORK WHITEWATER RIVER | CONSTRUCTION RELATED BYPASS
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2010-12-13 | 11A - 12:25P (12/15) | 11100000 | BYPASS OF TREATMENT PROCESS FINAL CLARIFIERS | EAST FORK WHITE RIVER | BYPASS TERTIARY FILTER TO INSTALL NEW EFFLUENT PUMP | NO DAMAGE IS ANTICIPATED MAINTAINED COMPLIANCE WITH NPDES PERMIT
IN0054402 | WESTERN WAYNE RSD | WAYNE | 2010-07-13 | 5:30P - 6P | 10000 | CAPITAL HILL LS | GROUND | EQUIPMENT FAILURE DUE TO HEAVY GREASE | PULLED PUMP HAVING EMERGENCY PUMP REPAIR SPARE PUMP ORDERED WILL NOT BE DELIVERED UNTIL 8/6/10
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2010-02-25 | 7:30A - 9:00 (2/22) | 150 | 215 LYNNS LANE OSSIAN WWTP FINAL CLARIFIER | GROUND NEXT TO TANK | SCUM RETURN LINE CLOGGED | SPILLED SCUM PICKED UP AND PUT IN DRYING BED
IN0020745 | OSSIAN MUNICIPAL STP | WELLS | 2010-09-03 | 5:30P - 7:30P | 3000 | MH @ 704 W. JEFFERSON ST. | GROUND AND CREEK | 8" PIPE BROKE | AREA CLEANED AND PIPE REPAIRED
IN0020974 | BROOKSTON MUNICIPAL STP | WHITE | 2010-06-22 | 7:00 - 3:00P | 500000 | PLANT AND SEVERAL MANHOLES | MOOTS CREEK | RAIN 4" | EQ BASIN IS FULL AND DISCHARGING TO SECOND CLARIFIER
IN0030571 | CHALMERS MUNICIPAL STP | WHITE | 2010-06-22 | 07:30 - 21:00 | 40500 | MH 18 | FARM FIELD | OVER 4.25" RAIN IN LESS THAN 24 HOURS ON ALREADY SATURATED | SEARCH FOR & MINIMIZE I & I SUBMITTED GRANT APPLICATION
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2010-04-17 | 8:30P - 12:54A(4/18) | 3000 | 5142 QUIET WATER COURT | GROUND | ELECTRO FUSION COPULAR FAILED | SEWERAGE VACCED UP AND AREA LIMED PLACE SANDBAGS IN FRONT OF DRAIN TILE TO PREVENT SEWERAGE FROM FLOWING INTO DITCH
IN0062367 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2010-08-06 | 7:00P - 7:45P |  |  |  | MALFUNCTION 2" SHUT VALVE FOR FLUSH CONNECT | SEWER HAULER VACUUMED SURROUNDING AREA CHECKING SIMILAR DEVICES IN COLLECTION SYSTEM
IN0022624 | COLUMBIA CITY MUNICIPAL STP | WHITLEY | 2010-06-03 | 9:30P - 11P | 3900 | JEFFERSON STREET L.S. | GROUND BLUE RIVER | POWER OUTAGE AND BROKEN FORCE MAIN | SHUT STATION DOWN CAUSING CSO BYPASS REPLACE 5' PIPE AND SPREAD LIME
IN0020753 | MIAMI VILLAGE MOBILE HOME PARK | WHITLEY | 2010-02-10 | 9:00A - 11A | 3000 | MANHOLE 200 FEET WEST OF T.P. | GROUND | LIFT STATION PUMP FAILURE | REMOVE LIFT PUMP AND CLEAN DEBRIS FROM IMPELLER REPLACE LIFT STATION PUMP AND PURCHASE NEW TRASH PUMP AS BACK- UP
IN0055166 | TRI-LAKES REGIONAL SEWER DIST. | WHITLEY | 2010-06-30 | 9A - 11:30A | 5 | 5222 SOUTH GROVELAND DRIVE | COLLECTION CHAMBER LID | PUMP PLUGGED WITH RAG | CONTINUE TO EDUCATE USER WHAT CAN BE FLUSHED THROUGH GRINDER SYSTEM
IN0055166 | TRI-LAKES REGIONAL SEWER DIST. | WHITLEY | 2010-08-05 | 2:02P - 3:30P | 10 | 3220 WEST SHORELINE DRIVE | AROUND COLLECTION CHAMBER LID | IMPELLER HAD RAG STUCK IN IT BREAKER WAS TRIPPED | CLEANED UP GROUND APPLIED LIME CONTINUE TO EDUCATE USERS WHAT CAN NOT BE FLUSHED THROUGH GRINDER SYSTEMS
IN0055166 | TRI-LAKES REGIONAL SEWER DIST. | WHITLEY | 2010-08-22 | 1P - 2:30P |  | 3395 WEST SHORELINE DRIVE | IN AROUND COLLECTION CHAMBER | GRINDER BREAKER HAD TRIPPED DUE TO A SHORT IN JUNCTION BOX | CHECKING IN WIRING IS ROUTINE MAINTENANCE ACTIVITY AND REWIRED BOX