## 2012 Annual Summary
PERMIT # | FACILITY NAME | COUNTY | BYPDATE | DURATION | GALLONS | LOCATION | RECEIVING AREA | REASON | ACTIONS
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2012-01-03 | 2:00P - 9:00A (1/9) | 12880000 | POND 2 | HABEGGER DITCH | PUMP 1 AND PUMP 2 BROKE DOWN | TOOK MOTOR FOR REPAIR; PUMP TO RIVER
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2012-01-17 | 8:00A - 8:45A | 500 | MH AT LINN GROVE & VAN BUREN ST | CATCH BASIN | RAIN .92" | LTCP
IN0021369 | BERNE MUNICIPAL STP | ADAMS | 2012-03-09 | 2:00P-3:00A | 14118000 | POND 2 | HABEGGER DITCH | RAIN 3.34 WE HAD OVER 3 INCHES OF RAIN IN 3 WKS | PUMP TO THE HABEGGER DITCH
IN0039314 | DECATUR WWTP | ADAMS | 2012-01-17 | 9:00A- |  | MANHOLE 600 BLOCK EAST MONROE ST | FARM FIELD | RAIN 1.68"
IN0039357 | GENEVA MUNICIPAL STP | ADAMS | 2012-02-24 | 12:00A- |  | MH IN HIRSCHEY FIELD-NORTHSIDE OF C R 1050 | GROUND | RAIN .3" CONTINUE TO CONTROL FLOW @ WWTP TO MAXI TREATMENT WITHOUT UPSETTING THE WWTP | NEW SEWER PROJECT UNDERWAY
IN0039357 | GENEVA MUNICIPAL STP | ADAMS | 2012-09-26 | 13:00-? |  | ON GOING | GROUND-HIRCHY FIELD | RAIN | MONITORING WWTP & MAXIMIZING FLOW TO REDUCE OVERFLOW
| MONROE SEWER DEPT | ADAMS | 2012-01-16 | 6:00A-8:00P | 250000 | LIFT STATION E ANDREWS | RETENTION POND | RAIN 2" | WE'VE HIRED 2 FIRMS THAT HAVE SMOKE TESTED OUR SYSTEM
| MONROE SEWER DEPT | ADAMS | 2012-03-24 | 6:00P-1:00P | 30000 | PUMP STATION E ANDREWS | RETENTION POND | RAIN 1.25" FAILED CHECK VALVE | REPAIRED CK VALVE SO IT WON'T FAIL
| ALLEN CNTY REGNAL SWR DIS. | ALLEN | 2012-09-12 | 3:00P-5:00P | 300 | GRINDER PUMP STATION | GROUND | GRINDER PUMP STOPPED WORKING & TRIPPED OUT MAIN BREAKER/NO ALARM WENT OFF DUE TO NO POWER WHEN BREAKER TRIPPED | CALLED J & S TO CLEAN GRINDER PIT & GROUND, PUMP & WIRE BEING REPLACED
| ALLEN CNTY REGNAL SWR DIS. | ALLEN | 2012-10-16 | 3:00P - 3:30P | 6000 | FM ON OLD US 27 | GROUND | BORE CREW HIT FM IN GROUND | REPAIRED MAIN, SHUT OFF LS, CLEANED AREA
| ALLEN CNTY REGNAL SWR DIS. | ALLEN | 2012-10-23 | 11:00-11:30 | 400 | GRINDER STATION | GROUND | GRINDERS STATION OVER FLOWED TO GROUND. | REPAIRED STATION & CLEANED UP OVER FLOW
| ALLEN CNTY REGNAL SWR DIS. | ALLEN | 2012-12-13 | 2:30P-4:30P | 500 | GRINDER STATION ON STEPHENS DRIVE | GROUND | DISCHARGE LINE BROKE OUTSIDE OF WET WELL | LINE SHUT OFF WHEN NOTIFIED. CLEANED AREA
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-01-01 | 1:30P - 3:30P |  | 3906 MAPLE CREST BASEMENT | BASEMENT | GREASE IN LINE | FLUSHED LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-01-07 | 7:00P - 8:25P | 100 | L39 050 9023 REDFIELD DR | ST. MARYS RIVER | ROOTS IN SANITARY LINE | FLUSHED LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-01-12 |  |  | 4328 MILLFORD | BASEMENT | GREASE | JETTED LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-01-16 | 2:00P-2:30P |  | 2626 HAZELWOOD AVE | BASEMENT | THE CITY RECEIVED A REPORT THAT A BASEMENT BACKUP OCCURRED @ THE ABOVE LISTED ADDRESS. THE CITY'S LINE WAS PARTIALLY PLUGGED ETC | THE CITY CONTINUES TO IMPLEMENT ITS APPROVED CMOM AND CSSOP PROG WHICH INCLUDE MANY PREVENTATIVE MAINT
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-01-17 | 11:00A-1:30P | 180 | L23 014 | ST MARYS RIVER | RAIN 1" | THE CITY CONTINUES TO IMPLEMENT ITS APPROVED CMOM & CSSOP PROG
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-01-22 | 10:00A - 12:00A (1/23) |  | 1012 LOREE ST | BASEMENT | RAIN .02" CITY'S LINE COLLAPSED | REPAIRING LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-01-28 | 11:24A-1:30P |  | K07 126-K07 127 | BASEMENT | RAIN .0480 ROOTS | THE CITY DE-ROOTED & CLEANED THE COMBINED SEWER LINE.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-02-02 | 6:00P-7:00P | 60 | W26 032 3931 NOTTINGHAM | BULLERMAN DRAIN | AN OVERFLOW OCCURRED @ THE ABOVE LISTED SEPARATE SANITARY SEWER LINE. THE CITY FLUSHED & REMOVED A BLOCKAGE OF ROOTS. THE CITY HAVE TELEVISED THIS LINE | THE CITY FLUSHED & TELEVISED THE LINE. THE CITY CONT TO IMPLEMENT ITS APPROVED CMOM & CSSOP PROG, WHICH INCLUDE MANY PREVENT MAINT ACTIVITIES DESIGNED TO PREVENT
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-02-02 | 4:00P-5:00P | 5 | M34 057 334 W ESSEX LANE | GROUND | AN OVERFLOW TO THE GROUND OCCURRED IN THIS SEPARATE SANITARY SEWER LINE. THIS LINE WITHIN AN APRT COMPLEX AREA & IS ALREADY ON A REGULAR SCHEDULED MAINT | THE CITY CLEANED THE LINE & WILL BE TELEVISING IT. THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-02-16 | 5:09P - 7:20P | 150 | 7641 COLD SPRINGS BLVD | ST. JOSEPH RIVER | GREASE AND DEBRIS | FLUSHED LINE AND CLEANED UP OVERFLOW
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-03-02 | 5:00P-6:55P | 220 | V22 032 & V22 037 | ST. MARY'S RIVER | RAIN 0.06" AN OVERFLOW OCCURRED FROM THE ABOVE MENTIONED SEPARATE SANITARY SEWER LINE. THE LINE WAS PLUGGED WITH ROOT AND OTHER SANITARY DEBRIS. | THE CITY FLUSHED THE SEPARATE SANITARY LINE AND THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-03-09 | 6:00P-9:40P | 1000 | W30 046 4838 BELVIDERE | GROUND | THE 6 INCH FORCE MAIN THAT PUMPS INTO MH W30 046 BROKE JUST UPSTREAM OF THE MH IN THIS SEPARATE SANITARY SEWER AREA | THE CITY BYPASS PUMPED UNTIL THE REPAIR TO THE BROKEN FORCE MAIN WAS COMPLETE.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-03-13 | 11:39A-1:00P | 405 | X18 020 | BULLERMAN DRAIN | AN OVERFLOW OCCURRED FROM THE ABOVE LISTED MH WITHIN THE SEPARATE SANITARY SEWER SYSTEM. | THE CITY FLUSHED THE LINE AND THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-03-26 | 10:30A-11:45A | 10 | HOMEOWNER'S CLEAN OUT | GROUND | ROOTS IN PRIVATE CLEAN OUT | THE CITY FLUSHED THE SEPARATE SANITARY SEWER LINE. THE CITY CONTINUES TO IMPLEMENT ITS APPROVED CMOM AND CSSOP PROGRAM.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-04-07 | 11:15A-12:15P | 5 | L39 043 | GROUND | ROOTS | THE CITY FLUSHED THE LINE AND THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-04-17 | 2:36P-7:30P | 20 | G 15 010 | GROUND | CRACK IN FORCE MAIN
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-04-24 | 1:20P-2:30P | 20 | N30 099 & N 03 104 | GROUND | PRIVATE LATERAL | THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-05-05 | 4:49A - 4:40 | 4800 | MORTON ST PUMP STATION O15251 | MAUMEE RIVER | LEVEL INDICATOR TURNED PUMPS ON FOR TEN SECONDS RESULTING IN DISCHARGE | CLEANED AND INSPECTED LEVEL INDICATOR. NO ISSUED FOUND
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-05-07 | 6:00P-7:50P | 330 | L39 079 | STORM INLET | RAIN 0.38" THE CITY FLUSHED THE LINE AND REMOVED THE BLOCKAGE THE CAUSE OF THE BLOCKAGE COULDN'T BE DETERMINED THE OVERFLOW WAS CLEANED UP | THE CITY FLUSHED THE LINE AND THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-05-11 | 10:38A-1:50P | 460 | U 42 033 SALGE & ANDORRA | SALGE DITCH | GREASE IN LINE | THE LINE WAS FLUSHED AND THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-05-21 | 5:52P-7:15P |  | 2403 EUCLID AVE | BASEMENT | THE ABOVE LISTED ADDRESSED REPORTED A BASEMENT BACKUP IT CANNOT BE DETERMINED IF THE BACKUP WAS ALSO DUE TO THE HOMEOWNER'S PRIVATE LATERAL | THE CITY REMOVED THE PARTIAL BLOCKAGE & TELEVISED THE COMBINED SEWER LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-05-29 | 1:10P-3:50A |  | 2909 CLARA AVE | BASEMENT | PARTIAL BLOCKAGE | THE CITY FLUSHED AND REMOVED THE BLOCKAGE AND WILL TELEVISE THE LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-06-25 | 1:02P - 3:07P | 10 | X30 061 4619 ARLINGTON WAY | GROUND | SANITARY DEBRIS IN 8 INCH LINE | FLUSHED LINE AND REMOVED DEBRIS
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-06-29 |  | 150000 | COVERDALE PUMP STATION REGULATOR K11 009 | ROBINSON BRINDLE DITCH/ST. MARY'S RIVER | RAIN .4" POWER OUTAGE | RESTORED POWER
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-07-24 | 5:30P-7:11P | 200 | 5810 MEADOWS DR | GROUND | RAIN 0.91" AN OVERFLOW OCCURRED IN THE SEPARATE SANITARY SEWER LINE A BLOCKAGE OF GREASE AND ROOTS WAS DISCOVERED. | THE CITY FLUSHED AND ROOT SAWED THE LINE AND THE OVERFLOW WAS CLEANED UP
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-07-30 | 2:21P - 4:30P | 6000 | 4405 ENGLE DR | TRANTMAN DRAIN | HOLE IN TOP OF PIPE | REPAIRED PIPE AND CLEANED AREA
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-08-14 | 4:00P-4:45P | 1500 | FORCE MAIN G150141H15001 | TRENTMAN DRAIN | EQUIPMENT FAILURE A BREAK OCCURRED IN THE ABOVE LISTED 8 INCH FORCE MAIN. THE PUMP STATION WAS SHUT DOWN & FLOW WAS PUMPED | THE OVERFLOW WAS CLEANED UP AND THE FLOW WAS PUMPED AND HAULED TIL THE BREAK WAS FIXED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-08-28 | 11:45A - 2:00P | 100 | 3318 SEQUAYAH PASS | SCHAPER DITCH | RAIN .8" TREE ROOTS IN LINE | FLUSHED LINE AND CLEANED AREA
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-09-16 | 1:00P-3:00P | 13500 | G15010 4400 ENGLE RD | TRENTMAN DRAIN | A BREAK OCCURRED IN THE 8 IN FORCE MAIN. | THE PUMP STATION WAS SHUT DOWN & FLOW WAS PUMPED & HAULED UNTIL THE BREAK COULD BE REPAIRED. THE OVERFLOW WAS CLEANED UP.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-09-28 | 11:00A - 12:00P | 100 | CSO N10 128 110 GRISWOLD | GROUND | CONTRACTOR DUMPED SLURRY INTO MH TOO FAST, OVERFLOWING THE MH | OVERFLOW CLEANED UP AND LINE FLUSHED
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-10-07 | 9:00P-10:00P | 30 | M38 094 | GROUND | THE 8 INCH LINE WAS PARTIALLY PLUGGED AT THE MH WITH CALCIUM AND GREASE. | THE CITY ROOT SAWED THE LINE & AND THE OVERFLOW WAS CLEANED UP.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-10-27 | 7:51P-9:30P |  | 2715 GREENVIEW AVE | BASEMENT | ROOTS | THE CITY REMOVED THE BLOCKAGE & WILL BE TELEVISING THE LINE.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-11-21 | 11/26 |  | M22 146 2402 EASTBROOK | SPY RUN CREEK | CANNOT DETERMINE BECAUSE LINE WAS FLOWING FREELY DURING INVESTIGATION | CLEANED LINE TO VERIFY NO BLOCKAGE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-11-21 | 4:30P - 7:45P | 1950 | V54 012 6610 HUNTERS GLEN | STORM DRAIN | BLOCKAGE IN CLEANOUT | FLUSHED CLEANOUT AND REMOVED BLOCKAGE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-12-11 | 7:40A-12:40P | 50 | T22 093 | GROUND | GREASE | THE CITY FLUSHED THE LINE & THE OVERFLOW WAS CLEANED UP.
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-12-20 | 12:54P - 2:30P |  | 2906 FREUHAUF | BASEMENT | RAIN .76" BLOCKAGE | FLUSHED LINE
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-12-31 | 2:57A - 10:41A | 163000 | 023 080 | ST. MARYS RIVER | WATER MAIN BREAK ENTERED COMBINED SEWER SYSTEM
IN0032191 | FORT WAYNE MUNICIPAL STP | ALLEN | 2012-12-31 | 8:13A - 10:00A | 30 | 315 EDGEKNOLL LN | GROUND | BLOCKAGE IN LINE | REMOVED BLOCKAGE
IN0048119 | HOAGLAND COLLECTION SYSTEM | ALLEN | 2012-01-17 | 7:30A-1:30P | 500 | CLEAN OUT @ 8802 HOAGLAND RD | GROUND | RAIN 0.8 LIFT STATION BACK UP & OVERFLOW @ 1ST CLEAN OUT @ HOME | WILL SEAL MANHOLES
| LEO CEDARVILLE RSD | ALLEN | 2012-12-27 | 11:30A - 12:00P |  | FM ACROSS SR #1 | GROUND | CRACK IN PVC PIPE | SHUTDOWN PUMP AND BEGAN REPAIR
IN0035378 | UTILITY CENTER/MAIN ABOITE | ALLEN | 2012-01-23 | 2:05P-11:35P | 2000 | SYCAMORE L/S M/H C30-19A | GROUND | RAIN .5 7" SNOW MELT AND 5. IN RAIN OVER NIGHT AND DURING DAY | A NEW LARGE F/M UNDER DESIGN/AND A NEW PUMP STATION UP STREAM WILL BE INSTALL WHEN F/M
IN0035378 | UTILITY CENTER/MAIN ABOITE | ALLEN | 2012-04-09 | 4:20P-6:05P | 200 | MH E 3-23 | GROUND | MH WAS LEAKING
IN0035378 | UTILITY CENTER/MAIN ABOITE | ALLEN | 2012-07-16 | 12:30P-2:20P | 500 | MH B-28-51 BLD 042 V HAMILTON POINT APTS | GROUND | EQUIPMENT FAILURE SEWER PLUG DUE TO GREASE
IN0035378 | UTILITY CENTER/MAIN ABOITE | ALLEN | 2012-11-17 | 4:00P-5:30P | 3000 | SYCAMORE L/S | BEAL TAYLOR CREEK AND GROUND | EQUIPMENT FAILURE PUMP FAILURE- INDUSTRIAL RAGS STRUCK IN PUMPS | USED VECTOR TO MINIMIZE OVERFLOW
IN0042391 | UTILITY CENTER/MIDWEST | ALLEN | 2012-03-13 | 1:30P-2:30P | 200 | GRAVITY LINE @ 5811 COVINGTON RD | GROUND | GRAVITY LINE ALONG RD SEAPING THROUGH GROUND UP PLUGGED LINE WILL HAVE CONTRACTOR FIX
IN0042391 | UTILITY CENTER/MIDWEST | ALLEN | 2012-09-10 | 11:30A - 12:00P | 75 | JUST EAST OF 5110 COVINGTON RD | GROUND & DITCH | CONTRACTOR HIT 3" FORCE MAIN
IN0021407 | WOODBURN MUNICIPAL STP | ALLEN | 2012-01-17 | 8:08A - 1:12P | 6000 | OUTFALL 002 | MAUMEE DITCH | RAIN .8" SEWER BEGAN TO BACK OUT OF OUTFALL 002 @ 8:00A M THE FLOW | WORKING TO RESOLVE I + I ISSUES
IN0032573 | COLUMBUS MUNICIPAL STP | BARTHOLOMEW | 2012-09-13 | 8:30A-10:00A | 200 | MH | GROUND | AIR RELEASE VALVE IN MH BROKE OFF PIPE ALLOWING SEWAGE TO LEAK OUT OF MH | REPAIRED BROKEN AIR VALVE, COVERED AFFECTED AREA WITH STRAW.
IN0039349 | ELIZABETHTOWN MUNICIPAL STP | BARTHOLOMEW | 2012-01-17 |  | 50000 | MH & BOTH WET WELLS | GROUND | RAIN 1.8" | NEW EQ BASIN
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2012-01-17 |  | 83310 | MH 3, 3A, 4, 35 | HAW CREEK | RAIN 1.5" | CLEAN AREA, CONSTRUCTION UNDER WAY
IN0021253 | HOPE MUNICIPAL STP | BARTHOLOMEW | 2012-01-26 | 7:00A - 12:00P | 35475 | MH 3, 3A, 4 | HAW CREEK | RAIN .8" | WAITING ON ELECTRICAL PANEL DELIVERY
IN0021253 | HOPE UTILITIES WWTP | BARTHOLOMEW | 2012-05-01 | 19:00-20:30 | 6300 | MH 35 NORTH OF 519 RACE ST | HAWCREEK 419 STORM DRAIN | RAIN 3.0" | CLEANED UP SOLID THIS AM
IN0021628 | HARTFORD CITY MUNICIPAL STP | BLACKFORD | 2012-05-11 | 9:00A-? | 100000 | OLD PLANT RAIL ROAD 006 | LITTLE LICK CREEK | CONSTRUCTION RELATED | JET OUT MAIN LINE BACK LATERALS FEEDING THAT MH
IN0021628 | HARTFORD CITY MUNICIPAL STP | BLACKFORD | 2012-06-08 | 10:00A-2:00P | 50000 | OUTFALL # 005 (CSO) | LITTLE LICK CREEK | DIVERSION 10 OVERFLOW BOX FULL OF SEDIMENT | CLEANED OVERFLOW BOX OF DEBRIS
IN0021628 | HARTFORD CITY MUNICIPAL STP | BLACKFORD | 2012-12-05 | 1:00P - 6:30P | 87499 | 007 | LITTLE LICK CREEK | POWER FAILURE | POWER RESTORED
INP000082 | HARTFORD CITY PAPER | BLACKFORD | 2012-02-02 | 6:45A-7:00A | 60 | 501 SOUTH SPRING ST | STORM SEWER | EQUIPMENT FAILURE PUMP 512 VAC SUMP PUMP SHUT OFF FROM A COMPUTER PROBLEM ALLOWING THE VAC SUMP TO OVERFLOW | RESTART 512 VAC SUMP PUMP & CORRECTED COMPUTER PROBLEM
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2012-01-18 | 11:04A-11:16A | 6000 | L/S #9 2450 W 96TH ST | GROUND | ATLAS EXCAVATING WORKING AT LIFT STATION SITE HIT FORE MAIN MAIN WHILE DIRECTIONAL DRILLING. | PUMPS AT STATION WERE SHUT OFF UNTIL PIPE WAS REPAIRED
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2012-08-03 | 3:00P-3:30P | 2000 | LIFT STATION 17 | GROUND | HAD TO SHUT FORCE MAIN DOWN TO REPLACE ARV. THE LIFT STATION STARTED TO BACK UP BEFORE WORK WAS COMPLETED | WE USED COMBO TRUCK TO CLEAN UP SIGHT
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2012-10-02 | 11:30A-12:00P | 150 | 96TH ST & TOWNE RD MH MR 202 | GROUND | TPI UTILITY CONSTRUCTION WAS BORING & HIT PRIVATE LATERAL PUSHING SLURRY INTO MAIN. | TPI RESPONSIBLE FOR CLEAN UP AND REPAIRS
IN0055760 | CLAY TOWNSHIP RWD | BOONE | 2012-10-12 | 0820A-0845A | 30 | 13139 DUMBARTON RD CLEAN OUT | GROUND | CONTRACTORS PLUG LEFT IN AFTER CONSTRUCTION CAUSED BLOCKAGE. | AREA AROUND CLEAN OUT WAS CLEANED UP
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2012-01-17 |  | 874000 | PLANT | FINAL PLANT EFFLUENT | RAIN 1.09 SEWER LINES INFILTRATION | WE ARE SPENDING $200,000.00 A YEAR RELINING SEWER LINES
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2012-01-18 |  | 212000 | PLANT | FINAL PLANT EFFLUENT | SEWER LINE INFILTRATION | WE ARE SPENDING $200,000.00 A YEAR RELINING SEWER LINE
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2012-01-23 |  | 62000 | PLANT | FINAL PLANT EFFLUENT | RAIN .67 SEWER LINES INFILTRATION | WE ARE SPENDING $200,000.00 A YEAR RELINING SEWER LINES
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2012-09-07 | 9/8 | 593000 | PLANT | FINAL PLANT EFFLUENT | RAIN 2.44" SEWER LINES INFILTRATION | WE ARE SPENDING $200,000.00 A YEAR RELINING SEWER LINES
IN0020818 | LEBANON MUNICIPAL STP | BOONE | 2012-09-08 | 9/9 | 74000 | PLANT | FINAL PLANT EFFLUENT | SEWER LINES INFILTRATION | WE ARE SPENDING $200,000.00 A YEAR REFINING SEWER LINES
| WHITESTOWN MUNICIPAL UTILITY | BOONE | 2012-02-19 | ?-9:30A (2/21) | 7000 | 7340 INDIANAPOLIS RD FM ARV | GROUND | AN AIR RELIEF VALVE ON THE EAGLES NEST LIFT STATION FORCE MAIN FAILED SUN EVENING 2/19 | SHUT OFF LIFT STATION SHUT OFF ARV VALVE VAC UP ALL SEWAGE IN PIT AND ON THE GROUND
| WHITESTOWN MUNICIPAL UTILITY | BOONE | 2012-11-01 | 7:00P-11:30A | 100 | 6760 REGENTS PARK DR ZIONSVILLE | GROUND | CONSTRUCTION RELATED PARTIAL BLOCKAGE IN MAIN LINE FROM GROUND DUE TO NEW CONSTRUCTION. | MAIN LINE JET/VAC TO CLEAR BLOCKAGE & CLEAN LINE.
IN0030325 | BROWN COUNTY STATE PARK | BROWN | 2012-01-17 | 9:00A-12:00P |  | LS WET WELL | GROUND | RAIN
IN0030325 | BROWN COUNTY STATE PARK | BROWN | 2012-04-04 | 11:00A-12:30P |  | BROWN CO STATE PARK | GROUND | RAIN LIFT STATION WHERE OVERFLOW OCCURRED PUMPS WASTEWATER FROM BROWN CO STATE PARK TO THE TOWN OF NASHVILLE'S OFFICE
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2012-04-24 | 10:15A-3:00P | 110 | RESIDENTIAL LIFT STATION | GROUND | RESIDENT FLUSHED RAGS DOWN TOILET | PUMPED DOWN TANK TO EMPTY AND REMOVED RAGS SPREAD LIME ON GROUND @ GROUND @ AFFECTED AREA ADVISED RESIDENT OF THE CAUSE
IN0023876 | NASHVILLE MUNICIPAL STP | BROWN | 2012-05-30 | 11A-11:15A | 50 | DIGESTER | GROUND | VALVE AT EFFLUENT END DIGESTER DID NOT CLOSE PROPERLY | PUMPED DIGESTER DOWN, VALVE CLOSED, COVERED AREA WITH LIME
IN0030562 | CAMDEN MUNICIPAL STP | CARROLL | 2012-01-19 | 10:00P-11:30A | 250 | LATERAL | GROUND @ HOMEOWNER |  | CLEANED UP SPILL AND COVERED WITH LIME
IN0021377 | DELPHI MUNICIPAL STP | CARROLL | 2012-07-17 | 17:20-17:30 | 300 | STATE RD #39 LIFT STATION | GROUND | POWER FAILURE | STAYED AT SITE TIL LIFT STATION HAD RUN A COUPLE OF CYCLES NO FREE LIQUID TO RECOVER
IN0021377 | DELPHI MUNICIPAL STP | CARROLL | 2012-08-08 | 9:43A - 10:10A | 100 | FORCE MAIN | GROUND | AIR RELEASE VALVE FAILED | INSTALLED NEW AIR RELEASE VALVE; LIMED AREA
IN0021377 | DELPHI MUNICIPAL STP | CARROLL | 2012-08-16 | 12:50P-13:25P | 5000 | LIFT STATION | GROUND, DRAINAGE DITCH, BRIDGE CREEK | POWER SUPPLIER CARROLL CO REMC LOST POWER DURING STORM | HALTED FLOW FROM MAJOR DISCHARGER, LIMED AREA, INSPECTED BRIDGE CREEK FOR ANY DISTURBANCES
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2012-01-23 | 4:00A-7:00A | 42000 | EQ TANK EMERGENCY RELEASE POINT 2-2 DAY | TERTIARY PONDS | RAIN .48" AND SNOW MELT | I
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2012-01-23 | 7:00A-7:00 1/24/12 | 1380000 | EQ TANK EMERG RELEASE POINT 2-2 DAY TERTIARY | PONDS | RAIN .06 3.8" OF MELTING SNOW,PLUS 54" OF RAIN EQ RANK OVERFLOWING INTO 2-2 DAY TERTIARY PONDS NOT BYPASSING INTO KUNS DITCH | IN HOUSE SEWER MAIN AS FUNDS ALLOW T BIRD DESIGN WORKING ON SOLUTIONS
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2012-01-25 | 7:00A - 7:00A (1/26) | 540000 | EQ TANK EMERGENCY RELEASE POINT | 2-2 DAY TERTIARY PONDS | RAIN .8"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2012-01-26 | 7:00A - 7:00A (1/27) | 1320000 | EQ TANK EMERGENCY RELEASE POINT | 2-2 DAY TERTIARY PONDS | RAIN .3"
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2012-01-27 | 7:00A-? | 1326000 | EQ TANK EMERG RELEASE POINT 2-2 TERTIARY | PONDS | RAIN .05
IN0020141 | FLORA MUNICIPAL STP | CARROLL | 2012-01-28 | 7:00A-10:00P | 210000 | EQ TANK EMERG RELEASE POINT 2-2 TERTIARY | PONDS | RAIN
IN0023604 | LOGANSPORT MUNICIPAL STP | CASS | 2012-02-10 | 23:25P-23:55P | 100000 | CSO # 002 | WABASH RIVER | POWER FAILURE, EQUIPMENT FAILURE, AND RAIN 0.10 A TRANSFORMER FAILED @ A LOCAL INDUSTRY, BACK-FEEDING A SURGE OF POWER TO THE WWTP SWITCHGEAR. THE SWITCHGEAR PROPERTY PROTECTED THE WWTP FACILITY & EQUIP | WE EXACTLY FOLLOWED ALL PROTOCOL RELATIVE TO RESPONDING TO SUCH AN EMERGENCY INCIDENT
IN0023604 | LOGANSPORT MUNICIPAL STP | CASS | 2012-12-25 | 8:17A - 8:39A | 2750 | CSO #018 | WABASH RIVER | TEMPORARY BLOCKAGE OR AIR LOCK | JET RODDED AND VACUUMED
IN0020354 | WALTON MUNICIPAL STP | CASS | 2012-01-17 | 5:00A-11:00P | 5000 | 613 MICHELE LN/RESIDENT 4" CLEANOUT | GROUND | RAIN .85""
IN0020354 | WALTON MUNICIPAL STP | CASS | 2012-03-06 |  | 500 | 101 N MAIN | STORM SEWER | BYPASS OCCURRED DUE TO WALTON CHRISTIAN CHURCH OWNED LIFT STATION CONTROL PANEL FAILURE THROUGH THE NIGHT RENTER @ 101 N MAIN WAS PUMPING SEWAGE FROM BASEMENT INTO STREET ETC
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2012-08-10 | 2:30P - 2:45P | 20 | 720 BOYER BASEMENT | BASEMENT | GREASE IN MAIN | FLUSHED MAIN WITH VACTOR TRUCK
IN0020508 | CHARLESTOWN MUNICIPAL STP | CLARK | 2012-12-08 | 10:45A-11:10A | 1000 | M H 3-428 | PLEASANT RUN CREEK | ROOTS IN LINE. | CLEANED WITH ROOT CUTTER.
IN0020508 | CHARLESTOWN WASTEWATER | CLARK | 2012-11-02 | 12:00P-6:00P | 200 | SADDLEBACK #1 FORCEMAIN | DITCH | EQUIPMENT FAILURE GASKET ON SLIP COUPLING HAD SMALL LEAK. WAS ABLE TO SHUT DOWN STATION TILL THIS MORNING DUE TO SMALL CUSTOMER BASE & AMPLE STORAGE IN WETWELL | RETAINED ALL OVERFLOW TO WORK AREA & CLEANED UP MESS W/VACTOR TRUCK.
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2012-01-26 | 10:30P - 11:30P | 1000 | N. CLARK & WASHINGTON, CARTER & MCKINLEY | STORM DRAIN | RAIN 1.1" | BUILDING NEW PLANT
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2012-03-27 | 7:15A-7:45A | 200 | 1329 APPLEGATE LN FROM AN AIR RELIEF VALVE MANHOLE | GROUND | AIR RELIEF VALVE FAILED | AFTER SHUTTING OFF THE ARV WE VACTORED UP THE SPILL & WASHED DOWN THE ROAD
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2012-05-29 | 8:15AS-10:30A | 1000 | STATION 20 | STORM DITCH | RAIN 3.6"
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2012-05-29 | 8:45A-11:00A | 2000 | MCKINLEY & CARTER AVE | STORM DRAIN | RAIN 3.6"
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2012-09-26 | 11:00P-12:15A | 100 | STA.16 747 HARRISON | STORM/STREAM | POWER FAILURE, RAIN 2.6"
IN0047058 | CLARKSVILLE MUNICIPAL STP | CLARK | 2012-09-26 | 10:00P - 12:00A (9/27) | 25000 | MH @ N. CLARK; MH @ CARTER & MCKINLEY | STORM SEWER | RAIN 2.6" POWER FAILURE | DESIGN STAGE OF NEW PLANT
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-01-26 | 9:00P - 9:30A (1/28) |  | RIVERPORT II 3 MHS | DRAINAGE DITCH | RAIN 1.6" | MHS ALLOWED TO OVERFLOW TO PREVENT PROPERTY DAMAGE; NORTH PLANT UNDER CONSTRUCTION
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-01-26 | 8:10P - 11:15P | 390000 | CRUMS LANE I LS | DRAINAGE DITCH | RAIN 1.6" | PUMPED WITH 6" PUMP,
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-03-08 | 10:00P - 10:30A (3/9) |  | RIVERPORT II MH | STORM DRAIN | RAIN .5" | ALLOWED TO OVERFLOW TO PREVENT DAMAGE TO BUILDINGS
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-05-29 | 3:00P-8:30A |  | MH RIVERPORT II | DRAINAGE DITCH | RAIN 3.0" | RIVERPORT II ALLOWED TO OVERFLOW TO PREVENT DAMAGE TO BUSINESS/RESIDENTIAL STRUCTURES
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-05-31 | 11:15P- 7:30A (6/2) |  | RIVERPORT II LIFT STATION MH | STORM DRAIN/DITCH | RAIN 1.5 HEAVY RAIN IN AREA MH OVERFLOWING DUE TO EXCESSIVE PRECIP | MH ALLOWED TO OVERFLOW TO PREVENT DAMAGE TO PROPERTIES IN AREA
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-06-04 | 7:45P-10:00P |  | CRUMS LANE II LIFT STATION MH | GROUND | SCADA ALARM MODEM FAILED TO CALL OUT PUMP FAILURE ALARM WHICH IN TURN LEAD TO A LEVEL ALARM AND SUBSEQUENT OVERFLOW FROM MH | PUMPER TRUCK WAS USED TO VACUUM OVERFLOW. LIM APPLIED
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-09-27 | 11:30A - 9:30P |  | RIVERPORT II MH | DRAINAGE DITCH | RAIN 2.75" | MH IS ALLOWED TO OVERFLOW TO MITIGATE DAMAGE
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-12-09 | 10:00P- |  | M H ON PORT ROAD | STORM DRAIN | RAIN 3.25" MH ARE ALLOWED TO OVERFLOW IN HEAVY RAINFALL EVENTS TO PREVENT DAMAGE TO PROPERTIES. | MH ARE ALLOWED TO OVERFLOW INTO STORM DRAIN.
IN0023302 | JEFFERSONVILLE MUNICIPAL STP | CLARK | 2012-12-10 | 7:00A-7:00P |  | LITER'S L S MH | TRIBUTARY TO LICK RUN CREEK | RAIN 3.25 LITER'S CURRENTLY HAS ONE PUMP OUT FOR REPAIR. | CREWS VACTORED OUT THE STATION & CALLED IN B & H SEPTIC HAULERS TO PREVENT FURTHER OVERFLOW TO CREEK. BYPASS PUMPING WAS SET UP AT 7:00P ON 12/10/12
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2012-10-04 | 21:00-22:40 | 600 | MH # 3-73 @ 1103 PRESIDENTIAL PLACE | STORM DRAIN @ 3410 PAGE PLACE | SSO RESULTED FROM A BLOCKAGE IN THE SEWER LINE. | CLEARED BLOCKAGE, REMOVED DEBRIS, FLUSH AREA
IN0023965 | OAK PARK CONSERVANCY DISTRICT | CLARK | 2012-10-06 | 5:00P - 8:00P | 4675 | 810 COLUMBIA CT | BASEMENT | BLOCKAGE IN MAIN SEWER LINE | CLEARED OBSTRUCTION AND LIQUID IN BASEMENT DRAINED BACK INTO MAIN SEWER
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2012-01-17 | 1:00A-3:00P | 200 | VALVE @ H.S. LS BY 442 N INDIANA AVE | RAN OUT OF ONTO PARKING LOT TO GRASSY | RAIN. BROKEN DISCHARGE PUMP | WE HAD TO DIG UP THE BYPASS CONNECTION TO STOP THE LEAK, CLEANED AREA
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2012-01-27 | 8:00A - 12:00P | 10000 | MH HIGH SCHOOL LS | STORM DITCH | RAIN 2.3" | WILL CLEAN, REHABBING WET WELL IN NEXT MONTH OR TWO
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2012-02-23 | 5:00P-8:00P | 2500 | 626 LANE AVE BASEMENT BACK UP | BASEMENT AND FRONT GUTTER | SEWER MAIN BACKED UP DUE TO POSSIBLE ROOTS & GREASE WE RAN A ROOT CUTTER THROUGH MAIN | RAN ROOT CUTTER THROUGH MAIN
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2012-05-04 | 2:00P-3:00P | 50 | FORCE MAIN LEAKING | GROUND | BROKEN FORCE MAIN | WE CUT OUT THE BAD SPOT AND REPLACE A 12" SECTION
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2012-08-14 | 12:00A-4:00P |  | AN OLD REPAIR IN DITCH FAILED | DITCH | EQUIPMENT FAILURE IT LOOKS LIKE A CLAMP ON A RUBBER BOOT BROKE CAUSING A LEAK WHEN THE MAIN TO BACK-UP WE CLEANED VACED 4000 TO 5000 GAL OF WATER AND SEWAGE OUT OF THE DITCH | WE HAVE LINED THE DITCH WITH LIME
IN0020419 | SELLERSBURG MUNICIPAL STP | CLARK | 2012-10-15 | 3:00A-1:30P |  | DRYER LANE & WEST UTICA | DITCH | CO BOARD OF HEALTH CALLED & TOLD US OF A OVERFLOW FROM A MH DUE TO A ROOT HALF WAY BLOCKAGE 8 IN MAIN. | WE RAN A ROOT CUTTER THRU MAIN AND VAC OUT ABOUT 3500 GAL OF SEWAGE & WATER OUT OF DITCH.
IN0109535 | WASHINGTON TOWNSHIP RSD | CLARK | 2012-04-16 | 10:00A-11:00A | 100 | LIFT STATION | GROUND | ELECTRICAL PROBLEM @ OHIO ST LIFT STATION | MAIN BREAKER FAILED & WAS REPAIRED
IN0020443 | COLFAX MUNICIPAL STP | CLINTON | 2012-01-23 | 6:00A-? |  | MH MERIDIAN ST | FARM FIELD TO DRAIN TO WEIR CREEK | RAIN 1.00 DUE TO RAIN & SNOW LAST WEEK RETENTION TANK FULL NO WERE FOR EXTRA WATER TO GO & WITH ADD HEAVY RAINFALL & MELTING SNOW 4" | WE WILL LIME AREA WHEN WATER GOES DOWN IN FIELD
IN0020443 | COLFAX MUNICIPAL STP | CLINTON | 2012-01-23 | 6:00A-6:00A 1/24/12 |  | MH MERIDIAN ST | FARM FIELD TO DRAIN TO WEIR CREEK | RAIN 1.00 DUE TO RAIN & SNOW LAST WK RETENTION TANK FULL NO WERE FOR EXTRA WATER TO GO AND WITH ADD HEAVY RAINFALL AND MELTING SNOW 4" CAUSE TO OVERFLOW MH | WE WILL LIME AREA WHEN WATER GOES DOWN IN FIELD
IN0020443 | COLFAX MUNICIPAL STP | CLINTON | 2012-01-26 | 1:00P - 6:30P |  | MERIDIAN ST MH | FARM FIELD TO DRAIN TO WEIR CREEK | RAIN 1.2" | LETTING MORE THROUGH PLANT STOPPED OVERFLOWS; WILL LIME
IN0020443 | COLFAX MUNICIPAL STP | CLINTON | 2012-09-08 | 3:00A-8:00A |  | MH MERIDIAN ST | FARM FIELD TO DRAIN TO WEIR CREEK | RAIN 3.00 POWER FAILURE. WHEN POWER BACK ON SOMETHING STUCK IN BOTH PUMPS | WE WILL LIME AREA WHEN WATER GOES DOWN IN FIELD
IN0022934 | FRANKFORT MUNICIPAL STP | CLINTON | 2012-01-04 | 2:30A - 2:32A | 1000 | FORCE MAIN | GROUND | DRAIN VALVE CAME APART DURING BYPASS PUMPING OF HEADWORKS | NEW BALL VALVE INSTALLED
IN0022934 | FRANKFORT MUNICIPAL STP | CLINTON | 2012-01-07 | 8:30A - 8:35A | 1000 | FORCE MAIN | GROUND | CLAMP CAME LOOSE DURING BYPASS PUMPING OF HEADWORKS | RETIGHTEN CLAMP
IN0059641 | GRAIN PROCESSING CORP | DAVIESS | 2012-10-29 | 9:20A - 10:00A | 8000 | PLANT | GROUND AND POND | HIGH STRENGTH HEADER LINE SPLIT | SHUT DOWN PLANT; PUMPED MATERIAL BACK INTO PLANT
| WEST BOGGS SEWER DIST | DAVIESS | 2012-09-21 | ?-10:00 |  | FORCE MAIN, AIR RELIEF VALVE | GROUND, ROAD DITCH | VANDALISM SUSPECTED BY MAINT PERSONAL & SYSTEM BOARD PRESIDENT. A 3" PLUG VALVE FOUND TO BE MANUALLY CLOSED BY AN UNKNOWN SOURCE OR INDIVIDUAL. | VALVE PIT VACUUMED OUT & AIR/VAL VALVE INSPECTED FOR OPERATION & OR PHYSICAL DAMAGES. VALVE FUNCTIONS PROPERLY W/NO DAMAGES.
| WEST BOGGS SEWER DIST. | DAVIESS | 2012-09-15 | (9/17) |  | FORCE MAIN, AIR RELIEF VALVE | GROUND | VALVE FAILURE | VALVE TO REMAIN LOCKED OPEN UNTIL REPAIRED
| WEST BOGGS SEWER DIST. | DAVIESS | 2012-12-19 | 10:00A - 12:00P |  | FORCE MAIN AIR RELIEF COMPRESSION JOINT | GROUND | SUPPORT STRAP BROKE LOOSENING COMPRESSION JOINT | REINFORCED SUPPORT AND REPLACED VALVE
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-01-17 | 5:16A -11:50A | 301000 | CSO OUTFALL 003 | BIG RUN CREEK | RAIN .77" | WWTP STAFF RESPONDED TO THE RAIN/WET WEATHER EVENT PER THE SOP FOR WET WEATHER OPERATIONS
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-01-23 | 12.03A-2:15P | 634000 | CSO OUTFALL 003 | BIG RUN CREEK | RAIN THERE WAS .50 TOTAL INCHES OF RAIN & 3 INCHES OF SNOW MELT | WWTP STAFF RESPONDED TO THE RAIN/WET WEATHER EVENT PER THE SOP FOR WET WEATHER OPERATION
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-02-29 | 3:10A-11:00A | 279000 | CSO OUTFALL 003 | BIG RUN CREEK | RAIN. 68" A THREE RAW PUMPS RAN AT FULL CAPACITY THE STORM WATER PUMP STATION DID NOT RUN DUE TO MECHANICAL FAILURE | WWTP STAFF RESPONDED TO THE RAIN /WET WEATHER EVENT PER THE SOP FOR WET WEATHER OPERATIONS
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-03-02 | 15:15-18:10 | 104000 | CSO OUTFALL 003 | BIG RUN CREEK | RAIN .38" | WWTP STAFF RESPONDED TO THE RAIN/WET WEATHER EVENT PER THE SOP FOR WET WEATHER OPERATION. FLOW WAS MAXIMIZED TO & THROUGH THE WWTP
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-04-18 | 3:00A -3:30A |  | MH UPSTREAM OF SDI/BUTLER PUMP STATION | GROUND/SDI BUTLER PUMP STATION | BLOCKAGE CAUSED BY SCALING IN FORCE MAIN | CLEANED FORCE MAIN AND PUT BACK INTO SERVICE
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-08-04 | 2025-2150 | 131671 | OUTFALL 003 | BIG RUN | RAIN 1.10 | THE CITY HAS CLEANED THE 60" MAIN SEWER LINE TO THE TREATMENT PLANT WHICH HAS HELP TO MAXI STORAGE CAPACITY IN THAT LINE MAXI FLOW
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-08-10 |  |  | FLOW SPLITTING CHANNEL AT AERATION TANKS | GROUND | RAIN .9". OPERATOR INADVERTANTLY CLOSED GATE VALVE SO OVERFLOW COULD NOT GO TO AT#3; ALARM DIALER FAILED | CLEANED RESIDUE; OPENED GATE VALVE
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-08-27 | 0920-1100 | 67737 | CSO OUTFALL 003 | BIG RUN DITCH | RAIN 1.10 | THE FLOW TO& THROUGH THE WWTP'S ACTIVATED SLUDGE, SINGLE STAGE NITRIFICATION UNITS WAS MAXIMIZED. NO DISCHARGE FROM THE WET WEATHER TREATMENT COMPONENTS
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-10-14 | 1610-1630 |  | OUTFALL 003 | BIG RUN | RAIN .36 | THE WWTP & STORM WATER PUMP STATION WERE OPERATED AS DESIGNED.
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-10-18 | 800-830 |  | OUTFALL 003 | BIG RUN | RAIN .43 | THE WWTP & STORM WATER PUMP STATION WERE OPERATED AS DESIGNED.
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-12-16 | 800-830 |  | OUTFALL 003 | BIG RUN | RAIN .52 | THE FLOW WAS MAXI TO & THRU THE WWTP & THE OVERALL DURATION & VOLUME OF DISCHARGE FROM OUTFALL 003 WAS DECREASED BECAUSE OF THESE ACTIONS.
IN0022462 | BUTLER MUNICIPAL STP | DE KALB | 2012-12-20 | 10:00A - 11:40A |  | OUTFALL 003 | BIG RUN | RAIN .78" | FLOW MAXIMIZED THROUGH PLANT
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2012-01-17 | 615A -11:45A | 65000 | SSO #002 (MANHOLE PRIOR TO HEADWORKS) | GARRETT CITY DITCH | RAIN 1.03" | MAXIMIZE FLOW
IN0022969 | GARRETT MUNICIPAL STP | DE KALB | 2012-05-07 | 0700-1000 | 34000 | SSO#002 MH PRIOR TO HEADWORKS | GARRETT CITY DITCH | RAIN 1.3" | STAFF IMPLEMENTED THE WET WEATHER OPERATING PROCEDURE THROUGH PLACEMENT OF THE RESERVE CLARIFIER INTO SERVICE
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-01-17 | 8:00A-2:10P | 1000 | 10439 MIILSTONE | GROUND | CONSTRUCTION RELATED 3 FORCE MAIN BLOCKAGE CAUSING BACK UP IN HOUSE AND PUMP FAILURES (3) 3" CLEANOUTS | WASH DOWN CLEAN UP ANY SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-01-24 | 7:30A-10:00A | 500 | 10649 10653 MILLSTONE DR | GROUND | EQUIPMENT FAILURE 3" CLEANOUT CAP THAT WAS INSTALLED ON 1/2 BLEW OFF DUE TO PRESSURE BUILD UP REPAIR ON THE SPOT | RAKED, WASHED, AND VAC'D SOLIDS OUT OF THE YD
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-01-25 | 9:45A - 10:00A |  | BURGER KING LS | GROUND TO STORM DRAIN | TIMER IN CONTROL PANEL FAILED | REPLACED TIMER
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-02-13 | 8:00A-1:00P | 200000 | TWIN 8" FORCE MAINS | STREAM | EQUIPMENT FAILURE FLOW TO SDRSD HAS BEEN DOWN SINCE 2/11/12 FOUND THE BEAK 8 AM TODAY CURRENTLY SHUT OFF TILL WE FIX 2/15/12 | WEATHER PERMITTING WASH DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-02-20 | 8:00A-11:45A | 5000 | US 50 FORCE MAIN | GROUND | DEFECTIVE PIPE KEEPS BLOWING HOLES IN THE BOTTOM. CAUGHT EARLY & SHUT OFF, FIXED QUICK | WASHED DOWN SOLIDS/ NEW 16' FM TO SDRSD
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-03-10 | 10:15P-2:00P | 1100 | 10623 MILLSTONE DR | GROUND | EQUIPMENT FAILURE CLEANOUT ON 3" FORCE MAIN FAILED APPROX 100 GAL SPILLED TO FIX THE CLEANOUT | WASH DOWN VAC'D OUT SOLIDS WITH CONTRACTOR VAC TRUCK
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-06-03 | 6:00P-7:00P | 500 | U S 50 @ SR 148 | GROUND | TWIN 8" FORCE MAIN TO SCRSD SEEPING ENOUGH TO MAKE A WET SPOT IN THE ROAD | WASH DOWN SOLIDS AND WILL REPAIR
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-06-04 | 7:30A-8A | 1000 | IMPORTING LIFT STATION | GROUND TO STREAM | RAIN; THE CSO @ THIS STATION WAS SCALE WITH CONCRETE APPROX 6WKS AGO 2.5' OF RAIN SHOWED THAT THE CEMENT PLUG DID NOT HOLD | WASH DOWN SOLIDS; WILL RE-DO CEMENT PLUG
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-06-13 | 1:00P-2:00P | 100 | 820 BEAUNA VISTA DR | GROUND TO STORM | THERMAL OVERLOADS ON PUMP FRIED WHICH KICKED THE MAIN BREAKER | WASH DOWN THE SOLIDS W/GARDEN HOSE
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-06-27 | 2:00P - 3:00P | 250 | 822 SUNNY DR | GROUND | BAD START RELAY BURNED UP BOTH PUMPS | WASH SOLIDS DOWN
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-07-26 | 1:00P-2:00P | 50 | 601 BUENA VISTA | GROUND | A TIMER THAT STARTS THE PUMPS FAILED INSIDE CONTROL PANEL, REPLACED W/NEW | WASH DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-07-30 | 11:00A-? | 5000 | AURORA CASKET | GROUND | CONTROL PANEL STRUCK BY LIGHTNING. DESTROYED INTERNAL COMPONENTS, WORKING TO GET THINGS BACK ON LINE ASAP | WASH DOWN SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-08-20 | 7:00A-4:00P | 500 | US 50 FORCE MAIN | GROUND | 8" FM TO SDRSD SPLIT APPROX 18" | WASHED DOWN THE AREA W/FIRE HYDRANT
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-08-27 | 10:00A | 5000 | 10944 MARSH RD | GROUND | FIRE IN CONTROL PANEL | WASHED DOWN SOLIDS AND WILL REBUILD PUMPS
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-11-27 | 1:00P-2:00P | 250 | 10442 HARMONY HILLS DR | GROUND | FIXING A LEAK ON 4" MAIN AT SERVICE TAP. OPENED FLUSH VALVE TO RELIEVE THE PRESSURE. | WASH DOWN ANY SOLIDS
IN0050903 | AURORA, CITY OF | DEARBORN | 2012-12-27 | 1:45P - 2:15P | 500 | 10944 MARSH RD. LS | GROUND | CONTROL BREAKER TRIPPED | RESET BREAKER AND WILL REPAIR PUMP
INJ063321 | GREENDALE MUNICIPAL STP | DEARBORN | 2012-05-21 | ? - 11:30A | 50000 | AIR RELEASE VALVE | GROUND | BROKEN AIR RELEASE VALVE | PUMPED MH; CLEANED AREA
INJ063321 | GREENDALE MUNICIPAL STP | DEARBORN | 2012-08-26 | 5:45A - 7:00A | 10000 | 8 INCH FORCE MAIN | DITCH, TANNER'S CREEK | CRACK IN FORCE MAIN | SHUT DOWN LS AND MADE REPAIRS TO FM
INJ063321 | GREENDALE MUNICIPAL STP | DEARBORN | 2012-10-04 | 3:00P-4:00P | 1000 | 1334 OBERTING RD | GROUND | FORCE MAIN BREAK | OPENED CHECK VALVES; LIMES SITE; CITY BUDGETING TO REPLACE PIPE IN NEAR FUTURE
IN0002160 | INDIANA MICHIGAN POWER, TANNER CK PLNT | DEARBORN | 2012-05-14 | 5;00P-? |  | CONDENSATE TANK OVERFLOW DRAIN VALVE | DRAIN PIPE TO TROUGH TO OHIO RIVER | BROKEN DRAIN VALVE | TANK WILL BE DRAINED TO REPAIR/REPLACE VALVE
IN0002160 | INDIANA MICHIGAN POWER, TANNERS CREEK PLANT | DEARBORN | 2012-10-21 | 10:10A - 10:30A | 1 | E-CRANE HYDRAULIC TRIDENT FLUID HOSE | CATCH PAN AND RIVER | PILOT PRESSURE HOSE RUPTURED | SHUT DOWN EQUIPMENT AND CONTAINED FLUID
IN0003131 | MGPI OF INDIANA, LLC | DEARBORN | 2012-06-22 | 10:45A - 11:00A | 200 | D ANNEX, 7 RIDGE AVE. | GROUND TO STORM SEWER TO OHIO RIVER | OPERATORS OVERFILLED TANKER WITH FUSEL OIL | SHUT OFF FLOW AND SOAKED UP AS MUCH AS POSSIBLE
IN0053759 | PICNIC WOODS WWTP | DEARBORN | 2012-01-18 | 8:00A-1:30P | 400 | LIFT STATION OLD ORCHARD SUB | UNNAMED TRIBUTARY OF SALT FORK CK | RAIN 2.75 AIR LOCK DISCHARGE LINE/FORCE MAIN | INSTALL AIR VALVE
IN0043168 | VALLEY RURAL UTILITY | DEARBORN | 2012-05-03 | 4:30P - 2:30A (5/4) | 19800 | LS 2 | HIDDEN VALLEY LAKE | RAIN 1.6" HIT BY LIGHTNING | REPAIRING PUMPS
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-01-17 |  |  | LS S. WEST ST., MH'S 3, 6, 13, 73, 76, 96, 80, 83, 81, 138 | MILLSTONE CREEK | RAIN 2.1" | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-01-23 |  |  | LIFT STATION ON S WEST ST MH 73,76 | MILLSTONE CREEK | RAIN .5" | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-01-23 |  |  | MH BEHIND 701 BENNETT | GROUND | BLOCKAGE IN LINE | SNAKED LINE
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-01-26 |  |  | S. WEST ST. LS MH'S 73,76 | MILLSTONE CREEK | RAIN 1.25"
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-03-23 |  |  | LIFT STATION ON S WEST ST | MILLSTONE CREEK | RAIN 2.25" | CLEAN AREA AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-03-30 |  |  | LIFT STATION ON S WEST ST | MILLSTONE CREEK | RAIN .75" | CLEAN AREAS AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-04-14 |  |  | LIFT STATION ON S WEST ST | MILLSTONE CREEK | RAIN 1.5" | CLEAN AREA AS NEEDED
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-06-01 | 8:00-8:20 | 2000 | FORCE MAIN @ WWTP | GROUND | BROKEN FORCE MAIN | RELEASE AREA WAS DRY GROUND AND SOAKED IN RELEASE AREA CHECKED FOR DEBRIS FOR AND CHECKED FOR RUNOFF NONE TO BE FOUND
IN0024830 | WESTPORT MUNICIPAL STP | DECATUR | 2012-10-10 |  |  | MH #74 A | MILLSTONE CREEK | BLOCKAGE BETWEEN MH 71 AND 72 | RELEASED BLOCKAGE; CLEAN AREAS AS NEEDED
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-01-16 |  |  | NEAR BEECH GROVE | WHITE RIVER | EQUIPMENT FAILURE WATER MAIN BROKE SOMEWHERE NEAR BEECH GROVE | INDIANA AMERICAN WATER WILL REPAIR
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-01-23 | 8:30A - 9:00A | 1000 | WHITE RIVER INTERCEPTOR MANHOLE | WHITE RIVER | RAIN .31 SNOW MELT | WILL BE GETTING THE MANHOLE BOLTED DOWN. WILL MONITOR THE SITUATION
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-03-01 | 9:24A - 1:00P | 1000 | HOYT & COWAN RD CSO 24 | BUCK CREEK | PLUGGED DISCHARGE PIPE | CLEANING CSO STRUCTURE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-03-13 | 11:00A-3:30P | 1732 | CSO 23 | BUCK CREEK | CREW WAS BEEN SENT OUT TO CLEAN THE CSO & REPAIR THE WEIR
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-05-14 | 11:00A-2:50P | 500 | CSO # 033 | WHITE RIVER | GREASE | CREWS WORKING TO CLEAR BLOCKAGE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-05-21 | 8:45A-10:00A | 100 | MH BEHIND MARSH PLAZA | GROUND | DEBRIS IN SANITARY LINE | CLEANED MH
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-06-16 | 3:00P-4:45P | 100 | PORT & COWAN RD | BUCK CREEK | DEBRIS | JET RODDED & MOVED DEBRIS OUT OF WAY
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-07-06 | 4:25A - 6:35A | 500 | CSO #1 LUICK AVE. | WHITE RIVER | DEBRIS IN SANITARY OUTFLOW FROM CSO STRUCTURE CAUSED OVERFLOW | WILL CLEAN SANITARY LINE
IN0025631 | MUNCIE MUNICIPAL STP | DELAWARE | 2012-07-28 | ? - 12:37P | 96000 | CSO 26 THOMAS DR | BUCK CREEK | SEWER PARTIALLY CLOGGED | JED RODDED SEWER TO REMOVE ROOTS
IN0023124 | CITY OF HUNTINGBURG | DUBOIS | 2012-10-19 | 9:30A-10:30A | 200 | FORCE MAIN AIR RELIEF VALVE CHESTNUT ST | STORM SEWER | EQUIPMENT FAILURE | PUMPED OUT PIT AND SHUT OFF VALVE WILL MONITOR TILL NEW VALVE RECEIVED
| CONSERVANCY DISTRICT IRELAND MADISON TWP | DUBOIS | 2012-02-22 | 3:00P-5:00P | 400 | 3824 W ST RD 56 FORCE MAIN | LAWN | 6" FORCE MAIN DAMAGE BY BORING EQUIPMENT INSTALLING FIBER OPTIC ALONG HWY 56 WEST OF JASPER | SHUT DOWN LIFT STATION FOR NEEDED REPAIRS
IN0058513 | HOLLAND DAIRIES, INC. | DUBOIS | 2012-08-25 | 9:00P - 1:15A |  | LS | RETAINMENT BERM | FIRE AT LS | OBTAINED PORTABLE PUMP AND WILL REPLACE DAMAGED PUMPS
IN0058513 | HOLLAND DAIRY INC | DUBOIS | 2012-05-13 | 3:00A-7:30A |  | LIFT STATION | RETAINMENT BERM | THE POWER FAILED 5/13/12 @ APPROX 3:00A & KICKED THE PUMPS OUT | THE BERM AROUND THE LIFT STATION PREVENTED ANY EFFLUENT FROM REACHING THE STREAM SUGAR CREEK
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2012-03-01 | 11:00A - 12:00P | 1200 | FORCE MAIN | DITCH | HIT FORCE MAIN WITH BACK HOE | SHUT VALVES AND USED EMERGENCY BYPASS FORCE MAIN AND TANKER UNTIL FIXED
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2012-03-27 | 12:00P-12:15P | 200 | SOUTH LIFT STATION | DITCH BEHIND RURAL KING | FIRE @ ACKERMAN OIL. WATER, OIL, FUEL MIXTURE FLOWED TO SOUTH LIFT STATION. SHUT LIFT STATION OFF TO PROTECT PLANT. | ABSORBENT ITEMS WERE PLACED IN DITCH. LIFT STATION WAS PUMPED INTO TANKER TRUCKS. LINE JETTED OF OIL RESIDUE.
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2012-07-15 | 12:30P-3:00P | 30 | PRIMROSE LANE BASEMENT | DITCH BEHIND 4 PRIMROSE LANE | ROOTS CLOGGING MH EFFLUENT | JETTED LINE FOUND POSSIBLE ROOTS COMING FROM 4 PRIMROSE LANE
IN0020834 | JASPER MUNICIPAL STP | DUBOIS | 2012-08-16 | 12:00A-12:30A | 5000 | TREATMENT PLANT | GROUND | CLEANED DIGESTER AND IN THE PROCESS OF RETURNING SLUDGE BACK TO THE DIGESTER, A HOSE COUPLER CAME OFF | CONTAINED SLUDGE ON PREMISES THEN VACUUMED SLUDGE UP AND PLACED INTO DRYING BED
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2012-01-03 | 8:00A - 12:00P |  | FORCE MAIN | GROUND | CRACK IN FORCE MAIN | REPLACED BAD PIPE WITH NEW AND 8" PRESSURE COUPLINGS
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2012-10-04 | 7:30A - 10:30A |  | 2" SERVICE LINE | GROUND | CRACK IN LINE | REPAIRED END WITH 2" CAP
IN0052698 | PATOKA LAKE REG. WAT. & SEW. D | DUBOIS | 2012-11-02 | 9:00A-11:00A |  | FORCE MAIN | GROUND | 8" FORCE MAIN HAD CRACK IN BELL | CUT OUT BAD PIPE AND REPLACED IT.
IN0038989 | BROADMORE ESTATES | ELKHART | 2012-02-29 |  | 500 | PLANT | GROUND | TOO MANY PINS ADDED TO LS | SCRAPED SLUDGE AND LIME AREA
IN0038989 | BROADMORE ESTATES | ELKHART | 2012-12-28 |  |  | TREATMENT FACILITY CLARIFIER THROUGH EAST POLISHING LAGOON BYPASS TO OUTFALL 001 | PINE CREEK | TEMP BYPASS INITITIATED DUE TO CAVE IN OF CONCRETE LINER ON EAST SIDE OF LAGOON. | ALL EFFLUENT IN COMPLIANCE WITH PERMIT
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2012-10-18 | 4:30P-7:30P |  | 2304 GRANT STREET | BASEMENT BACK-UP | ROOTS, GREASE AND RAGS | CLEANING CONTINUED ON OCT 19TH AND OCT 22ND IN THE AREA. RESIDENT WILL BE MADE AWARE OF OUR BASEMENT VALVE PROGRAM.
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2012-10-24 | 11:45A-12:30P | 481 | CSO 37 FRANKLIN & KRAU | ST JOSEPH RIVER | EFFLUENT LINE PLUGGED W/GREASE AND ROOTS | WE ARE ACTIVELY TAKING MEASURES TO HEIGHTEN AWARENESS IN OUR COMMUNITY.
IN0025674 | ELKHART MUNICIPAL STP | ELKHART | 2012-12-12 | 12:37P-2:00P | 4 | 512 HALLIE | FLOOR DRAINS | STAFF FOUND THE 8" SEWER MAIN PLUGGED WITH PAPER. | THE LINE WAS IMMEDIATELY CLEANED & THE BACK UP RESIDED.
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2012-02-11 | 6:15A-6:30A | 10000 | AERATION TANKS | GROUND | POWER FAILURE, EQUIPMENT FAILURE PLANT LOST 110 V POWER TO THE EFFLUENT PUMP SCADA PLC WHICH CONTROLS EFFLUENT PUMPS THE PUMPS SHUT DOWN ONCE THE UPS BATTERY BACK UP SYSTEM RAN OUT OF POWER | A BACKUP FLOAT SYSTEM WAS INSTALLED IN 2011 TO CONTROL EFFLUENT PUMPS AND SHUT DOWN THE RAW
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2012-04-11 | 10:30A-10:40A | 25 | SEWER MAIN | GROUND | WATER DEPT WAS INSTALLING A WATER TAP TO A RESIDENT AND HIT THE STATION FORCE MAIN @ 2400 COLLEGE AVE
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2012-08-14 | 1:00A - 2:00A | 60 | OAK RIDGE PARK TOILET AND FLOOR DRAIN | RESTROOM FLOOR | RAIN 1.14" | LOOKING INTO CHECK VALVE FOR RESTROOM SEWER LINE
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2012-08-14 | 12:00A - 12:30A | 1000 | AERATION TANKS | CONTAINED ON PLANT GROUND | RAIN 2.25" EFFLUENT PUMP STATION LOST POWER | TURNED OFF RAW SEWAGE PUMPS AND RESET PUMP STATIONS
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2012-11-02 | 7:45A - 8:30A | 100 | LS WET WELL | STORM SEWER | FAILED MOTHERBOARD PREVENTED PUMPS FROM STARTING | REPLACED MOTHERBOARD AND CLEANED AREA
IN0025755 | GOSHEN MUNICIPAL STP | ELKHART | 2012-11-27 | 7:00A-10:00A | 50 | SOUTH 9TH SEWER MAIN | GROUND | COLLAPSED SEWER MAIN RELEASED SEWAGE INTO THE GROUND. THE CONTAMINATED SOIL WAS REMOVED BY A VACTOR. | REPAIRED COLLAPSED SEWER MAIN
IN0021466 | NAPPANEE MUNICIPAL STP | ELKHART | 2012-07-04 | 7/5 |  | BASEMENT BACK UP 306 E. JOHN | BASEMENT | BLOCKAGE FOUND ON HARTMAN ST. | SEWER WAS JETTED
IN0032336 | CONNERSVILLE MUNICIPAL STP | FAYETTE | 2012-05-15 | 10:30A - 1:30P | 10 | 150' WEST OF MEMORIAL DRIVE | YARD | MAIN WAS OBSTRUCTED | APPLIED LIME AND ADDED ROOT CONTROL TO MAIN
IN0032336 | CONNERSVILLE MUNICIPAL STP | FAYETTE | 2012-10-10 | 8:55A - 1:00P | 5 | 401-403 W 32ND ST. FROM THE CLEANOUT | GROUND | ROOTS | JET CLEANED SEWER LINE TO ENSURE FULL CAPACITY; SPREAD LIME
IN0062553 | HERITAGE SPRINGS WWTP | FLOYD | 2012-06-08 | 9:45A-10:00A | 50 | LIFT STATION | GROUND | FLOAT STUCK IN OFF POSITION. REPAIRED AND PUT BACK IN SERVICE | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-01-26 | 11:00P - 11:27P | 810 | BASIN 13-5, MH 13-C47 | GROUND TO FALLING RUN CREEK | RAIN 1.69" | SEWER LINING PROJECT IN 2012
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-03-21 | 3:30P-5:15P |  | BASIN 35 PROSSER LIFT STATION | GROUND TO JACOBS CREEK | AIR RELEASE VALVE FAILED ON DISCHARGE LINE AT THE PROSSER LIFT STATION | CLEANED SITE AND ISOLATED AIR RELEASE VALVE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-03-23 | 2:42P-3:54P | 2000 | BASIN 39 | GROUND TO CHAPEL CREEK | RAIN 1.35" THE LIFT STATION PUMPS FAILED DUE TO RAGS WRAPPED AROUND IMPELLER. MAINTENANCE RETRIEVED PORTABLE PUMP AND TRIED TO PUMP DOWN WET WELL BUT WAS INUNDATED WITH RAIN WATER. ETC | AN INVESTIGATION IS UNDER WAY TO DETERMINE IF A POSSIBLE BREAK IN SEWER LINE OR MISSING MANHOLE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-03-23 | 2:15P-2:16P | 10 | BASIN 9 | GROUND | RAIN 1.35"
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-05-29 | 11:12A-1:30P | 20700 | JUNCTION OF BASIN 14-5& 14-6 | FALLING RUN CREEK | CONSTRUCTION RELATED, RAIN 2.91 | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-05-29 | 10:42A-1:18P | 62400 | BASIN 13-5 | TRIBUTARY TO FALLING RUN CREEK | CONSTRUCTION RELATED, RAIN 2.91 | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-05-29 | 9:48A-12:49P | 9050 | MH 16-31 | TRIBUTARY TO FALLING RUN CREEK | CONSTRUCTION RELATED, RAIN 2.91 | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-05-29 | 9:39A-12:49P | 19000 | MH 16-38 | TRIBUTARY TO FALLING RUN CREEK | CONSTRUCTION RELATED, RAIN 2.91 | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-05-29 | 10:17A-1:15P | 17800 | MH 13-58 | TRIBUTARY TO FALLING RUN CREEK | CONSTRUCTION RELATED, RAIN 2.91 | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-05-29 | 10:06A-12:55P | 169 | MH 13-108A9 | TRIBUTARY TO FALLING RUN CREEK | CONSTRUCTION RELATED, RAIN 2.91 | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-05-29 | 10:18A-1:15P | 4425 | BASIN 13-4 | TRIBUTARY TO FALLING RUN CREEK | CONSTRUCTION RELATED, RAIN 2.91 | NO DAMAGE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-06-28 | ? - 2:00P | 6000 | ROBERT E LEE LS | GROUND | AIR RELEASE VALVE FAILED AT DISCHARGE POINT | LIMED AREA, ORDERED REPLACEMENT
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-09-08 | 3:00A-8:40A | 77000 | MH # 8-11 | FALLING RUN CREEK | THIS SSO WAS A DIRECT RESULT OF THE FAILURE OF THE AUTOMATIC TRANSFER SWITCH AT THE WWTP NOT THE RAIN EVENT
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-09-08 | 5:00A-12:30P | 900000 | SSO #003 | FALLING RUN CREEK | POWER FAILURE WWTP WAS BYPASSED DUE TO FAILURE OF THE AUTOMATIC TRANSFER SWITCH
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-10-29 | 7:00A - 1:00P | 1500 | MH #43 BASIN 1A | STORM SEWER | RAGS IN MH | FLUSHED LINE
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-12-09 | 11:45P-2:00A | 17500 | SSO # 023 MH #13-C46 | FALLING RUN CREEK | RAIN 1.24 IN | SEWER LINING PROJECTS UNDER WAY
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-12-10 | 12:10A-2:00A | 8250 | SSO #023 MH #13-C46 | FALLING RUN CREEK | RAIN 1.24 IN. | SEWER LINING PROJECTS UNDER WAY
IN0023884 | NEW ALBANY MUNICIPAL STP | FLOYD | 2012-12-10 | 12:30A-1:50A | 4000 | BASIN # 14-6, MH#14-62 | FALLING RUN CREEK | RAIN 1.24 | SEWER LINING PROJECTS UNDER WAY
| TOWN OF GEORGETOWN | FLOYD | 2012-04-09 |  | 150 | 8172 AUTUMN COVE | AROUND LIFT STATION | POWER POLE HIT IN AN ACCIDENT CAUSING A POWER OFFSET INTO SYSTEM WHICH BURNED STARTERS IN STATION | STARTERS REPLACE, PUMPED SEWER TANKER TRUCK, SPREAD LINE DUST
IN0063771 | TOWN OF GEORGETOWN | FLOYD | 2012-06-20 |  | 2000 | MH | GEORGETOWN CREEK | MH BLOCKED WITH GREASE INSIDE SEWER MAIN | CLEARED BLOCKAGE, SPREAD LIME DUST
IN0054101 | WOODS OF LAFAYETTE | FLOYD | 2012-05-06 | 4:00P-9:30A | 20000 | ARNI'S LIFT STATION | TRIBUTARY TO LITTLE INDIANA CREEK | OVERFLOW DUE TO CLOGGED PUMPS ON CALL MAINTENANCE SERVICE AND RESPONDED AND UNSTOPPED PUMPS | CLEANED SITE
IN0043923 | WYMBERLY WOODS UTLS. | FLOYD | 2012-11-01 | 9:13P - 1:00P (11/2) |  | 2ND MH UPSTREAM FROM FOREST SPRINGS LS | DRAINAGE DITCH | GREASE | PUMPED MH; CLEANED AND LIMED AREA
IN0039390 | KINGMAN MUNICIPAL STP | FOUNTAIN | 2012-08-06 | 1:00P - 3:00P | 12000 | LS #2 W. 2ND ST. | UNNAMED TRIBUTARY STREAM TO MILL CREEK | POWER FAILURE
IN0039390 | KINGMAN MUNICIPAL STP | FOUNTAIN | 2012-09-08 | 9:00P-8:00A | 62000 | PRIMARY CLARIFIER | LAGOON | RAIN 1.1" I&I PROBLEMS | SURVEY TO DETERMINE ILLEGAL TIE INS
IN0039390 | KINGMAN MUNICIPAL STP | FOUNTAIN | 2012-10-23 | 2:40P - 4:00P | 136000 | CLARIFIER | UNNAMED TRIBUTARY OF MILL CREEK | RAIN | DIVERTED FLOW TO LAGOON- BYPASSING DISINFECTION BASIN
INP000188 | MASTERGUARD CORPORATION | FOUNTAIN | 2012-04-04 |  |  | MRS SYSTEM |  | REBEDDING MEDIA OF MRS SYSTEM AND REPAIRING INTERNAL LATERALS FOR THE VESSELS.
IN0024716 | VEEDERSBURG MUNICIPAL STP | FOUNTAIN | 2012-02-20 |  |  | MH #49&3 | GROUND | THIS MH HAD OVERFLOWED @ SOME POINT BECAUSE THERE WAS DEBRIS ON GROUND BUT WAS NOT VISUALLY SEEN WE WERE AT THIS MH MON 2/20/12 IN THE AFTERNOON & NOTICE THE GROUND @ THE MH | GOING TO INSTALL RISER MH IS SHALLOW WITH LITTLE CAPACITY
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2012-01-09 | 5:15P - 6:15P | 100 | 1129 MONROE ST | BASEMENT | GREASE | JETTED LINE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2012-02-12 | 11:30A-12:30P | 100 | 2612 COUNTRY CLUB DR | BASEMENT | EQUIPMENT FAILURE THIS HOME IS ON OUR VACUUM SYSTEM WHICH HAD A CONTROL VALVE MALFUNCTION & THIS CAUSE THE HOMEOWNER'S BACK | REPLACED CONTROL VALVE
IN0021667 | ROCHESTER MUNICIPAL STP | FULTON | 2012-02-23 | 6:00P-6:45P | 5 | 1109 PARK ROAD | HOMEOWNER'S BASEMENT | GREASE | CLEANED GREASE BLOCKAGE FROM SEWER LINE THAT FEEDS LIFT STATION
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2012-02-25 | 10:30A-11:30A | 10 | 1111 MONROE ST | BASEMENT | CONSTRUCTION RELATED | JETTED SEWER LINE BUT FOUND NO REASON FOR BACK UP ON SEWER LINE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2012-03-17 | 8:30A-9:30A | 5 | 312 E 14TH ST | BASEMENT |  | JETTED LINE AND FOUND BLOCKAGE AT 6 FOOT AREA JETTED A TOTAL OF 370 LIE BLOCKED W/RAGS, ROOTS, SAND
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2012-07-26 | 7:56P-9:00P | 1 | MH | COLLEGE STREET | OVERFLOW CAUSED BY GREASE BLOCKAGE IN SEWER LINE | RAN SEWER LINE, UNPLUGGED GREASE BLOCKAGE CLEANED AREA
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2012-08-31 | 2:53P-9:00A | 10 | 1306 HILL ST ROCHESTER, IN | BASEMENT | EQUIPMENT FAILURE HOMEOWNER MUST PLUG BASEMENT DRAIN PER CITY ORDINANCE | CLEANED AND JETTED LINE
IN0021661 | ROCHESTER MUNICIPAL STP | FULTON | 2012-12-03 |  | 1 | 1346 PARK ROAD | BASEMENT | RAGE, GREASE AND DEBRIS | CLEANED LINE
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2012-01-23 | 7:30A-8:00A | 250000 | HWY 64 EAST PLANT LOCATION | SHY DITCH | EQUIPMENT FAILURE PUMPS KICKED OUT DUE TO RAGS GETTING INTO HEADWORKS | PULLED PUMPS CLEANED OUT PUT BACK IN OPERATION PLANT IS BEING UPGRADED AT THIS TIME
IN0021687 | OAKLAND CITY MUNICIPAL STP | GIBSON | 2012-09-02 | 4:00A - 7:00A |  | PLANT INFLUENT HEADWORKS | SHY DITCH | LS HIT BY LIGHTNING | BYPASS PUMP TO PUMP STATION DOWN
IN0024392 | PRINCETON MUNICIPAL STP | GIBSON | 2012-03-08 | 10:30A - 8:35A (3/9) | 12600 | MH BETWEEN RACE & SEMINARY | RICHLAND CREEK | RAIN
| JONESBORO CITY OF | GRANT | 2012-01-17 | 7:50A-1:45P | 325000 | MH I-11 + I-18 | GROUND SATURATED CREEK FLOODING | RAIN 2.8 FLOOD CONDITIONS, GROUND SATURATED DUE TO SNOWFALL & RAIN | CLEAN MANHOLES & AROUND, SPREAD LIME
| JONESBORO CITY OF | GRANT | 2012-09-01 | 4:25P-6:05P | 530000 | I-1, I-3, I-11, I-18, I-19 | GROUND & CREEK FLOODING | RAIN 4.25 FLOOD CONDITIONS DUE TO EXCESSIVE AMOUNT OF RAINFALL IN SHORT PERIOD OF TIME OUR WASTEWATER IS SENT TO GAS CITY FOR TREATMENT | CLEANED MH & AROUND, ALSO SPREAD LIME
IN0060992 | SWEETSER, TOWN OF | GRANT | 2012-01-17 | 6:00A-4:15P | 15375 | KELLY DR LIFT STATION | GROUND TO STREAM | RAIN 3+ | RAN PUMPS ON MANUAL FOR AWHILE TO HELP DRAIN THE LIFT STATION FASTER
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2012-01-17 | 6:30A - 10:00A | 600 | NORTH LS, WEST LS | SCHWARTZ DITCH, JEFFERSON DITCH | RAIN 1.2"
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2012-07-15 | 12:45A-6:30A |  | NORTH LIFT STATION | SCHWARTZ DITCH | RAIN 1.8 | WORKED ON FLOAT
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2012-09-01 | 4:00P-5:30P | 300 | NORTH LIFT STATION | SCHWARTZ DITCH | RAIN 1.5
IN0036978 | UPLAND MUNICIPAL STP | GRANT | 2012-09-02 | 5:30A-9:00A | 420 | NORTH LIFT STATION | SCHWARTZ DITCH | RAIN 1.3
IN0022497 | CARMEL MUNICIPAL STP | HAMILTON | 2012-09-05 |  | 3000 | FM WEST OF MH 1140 | GROUND AND DITCH | CONTRACTOR BORED THROUGH SEWER MAIN; FIXED IT BUT DIDN'T SAY ANYTHING | CLEARED LINE AND CLEANED AREA
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-01-02 | 12:30P - 2:50P | 50000 | SMOCK CREEK GRAVITY INTERCEPTOR | SMOCK CREEK DITCH TO WHITE RIVER | 10 INCH EMERGENCY BYPASS PUMP CLOGGED WITH DEBRIS | REPAIRING 27 INCH GRAVITY SEWER
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-02-06 | 5:00A-7:00A | 10000 | ALLIONSVILLE RD LIFT STATION | CHEENEY CREEK | THE ALLIONSVILLE RD LIFT STATION IS CURRENTLY UNDER RENOVATION. BYPASS PUMPING HAS BEEN OPERATING SINCE 2/2/12. SOMETIME IN THE EARLY MORNING ON 2/6/12 ON PUMP FAILED & ANOTHER PUMPS | ONE NEW PUMP WAS INSTALLED & ALL THREE LARGE DUTY PUMPS WERE CLEANED LIME/SOIL WERE SPREAD IN THE OVERFLOW AREA.
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-02-07 | 9:00A-10:00A | 8000 | ALLIONSVILLE RD LIFT STATION | CHEENEY CREEK | EQUIPMENT FAILURE THE ALLIONSVILLE RD LIFT STATION IS CURRENTLY UNDER RENOVATION. BYPASS PUMPING HAS BEEN OPERATING SINCE 2/2/12 | STILL FENCE SOIL BARRIER & LIME ADSORBED MOST OF THE OVERFLOW THE CLOGS WERE QUICKLY REMOVED & THE PUMPS PLACED BACK IN SERVICE.
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-03-23 | 12:15A-7:30A | 640000 | ALLISONSVILLE RD LIFT STATION | CHEENEY CREEK | CONSTRUCTION RELATED, EQUIPMENT FAILURE THE ALLISONSVILLE RD LIFT STATION IS CURRENTLY UNDER RENOVATION THE NEW PLC CONTROL & ALARM SYSTEM FAILED @ APPROX 12:00A ON 3/23/12 PUMP WERE RE-STARTED & AUTOMATIC CONTROL ETC | CONTRACTOR RESPONDED TO THE FAILURE UPON NOTIFICATION
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-03-26 | 2:00P-8:00P | 10000 | 12175 VISIONARY WAY | STORM SEWER TO RETENTION POND | 10 IN SANITARY SEWER LOCATED @ REFERENCED ADDRESS DEVELOPED A BLOCKAGE. SEWER CLEANING CREW ARRIVED ON SITE @ 2:30P LINE WAS NOT FULLY CLEANED AND IN SERVICE TILL 8:00P | SEWER CLEANING CREW RESPONDED IMMEDIATELY. ETC
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-03-26 | ?-8:00A | 10000 | ALLISONSVILLE RD LIFT STATION | CHEENEY CREEK | ALLISONSVILLE RD LIFT STATION IS CURRENTLY UNDER RENOVATION ONE OF THE BYPASS PUMPS FAILED SOMETIME SUNDAY EVENING OR MON MORNING. | CONTRACTOR RESPONDED TO THE FAILURE UPON NOTIFICATION 3/26/12 WAS THE LAST DAY OF BYPASS PUMPING ETC
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-04-04 | 1:45P-2:00P | 2000 | 12000 BLOCK OF ALLIONSVILLE RD | SMOCK CREEK TO WHITE RIVER | CONSTRUCTION RELATED, EQUIPMENT FAILURE BYPASS PUMPING HAS BEEN SET UP ON THE SMOCK CREEK INTERCEPTOR SINCE 4/2/12 TO FACILITATE LINING OF 2,000 FT OF 27 IN | TOWN AND CONTRACTOR PERSONNEL RESPONDED TO THE OVERFLOW SITUATION IMMEDIATELY. ETC
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-04-05 | 10:00A-10:15A | 4000 | 12000 BLOCK OF ALLIONSVILLE RD | SMOCK CREEK TO WHITE RIVER | CONSTRUCTION RELATED, EQUIPMENT FAILURE BYPASS PUMPING HAS BEEN SET UP ON THE SMOCK CREEK INTERCEPTOR SINCE 4/2/12 TO FACILITATE LINING OF 2,000 FT OF 27 IN. | TOWN & CONTRACTOR PERSONNEL RESPONDED TO THE OVERFLOW SITUATION IMMEDIATELY
IN0055484 | CHEENEY CREEK WWTP | HAMILTON | 2012-08-29 | 12:32P - 12:47P | 50000 | HAGUE RD LS | CHEENEY CREEK | CONTRACTOR TURNED POWER OFF TO ALL PUMPS WHEN ATTEMPTING TO ISOLATE POWER TO PUMP #5 | CREW RESTARTED ALL PUMPS
IN0055280 | EAGLETOWN ESTATES MOBILE HOME | HAMILTON | 2012-09-03 |  |  | PLANT | LITTLE EAGLE CREEK | BYPASSING POLISHING POND FOR CLEANING | STILL MEETING PERMIT LIMITS
IN0055280 | EAGLETOWN/LITTLE CREEK ESTATES | HAMILTON | 2012-10-01 |  |  | FINAL EFFLUENT/TREATMENT PLANT | LITTLE EAGLE CREEK | CEASED BYPASSING POLISHING TANK AND BACK TO NORMAL OPERATIONS | ALL BYPASSED WATER TREATED AND ALL SAMPLING PERMIT LIMITATIONS MET
| HAMILTON S.E. UTILITIES, INC. | HAMILTON | 2012-06-18 | 8:30P-11:00P | 1000 | MH IC-2C-727.00 INTRACOASTAL SUB | GROUND | PUMP AND BREAKER FAILURE | REPLACE PUMP AND BREAKER
| HAMILTON S.E. UTILITIES, INC. | HAMILTON | 2012-09-28 | 8:00A-8:15A | 200 | MH 755-1-00A.00 12301 E 116TH ST | GROUND | VFD OVERLOAD IN L.S. PANEL | RESET VFD
| HAMILTON S.E. UTILITIES, INC. | HAMILTON | 2012-12-22 | ? - 8:00P | 2500 | 11109 NEWBURY PORT MH IC-2C-727.00 | GROUND | PLC FAILURE | REPLACE PLC; INSTALL BACK UP FLOAT MODE SYSTEM PLANNED
IN0020168 | NOBLESVILLE WASTEWATER UTILITY | HAMILTON | 2012-05-13 | 12:30-16:00 |  | AIR RELIEF VALVE ASSET # 117 NEAR 7932 DOVES CT | GROUND | AIR RELIEF VALVE FAILURE | REPLACE AIR RELIEF VALVE; TAKING SAMPLES
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2012-02-12 | 11:30A - 2:00P (2/14) | 400000 | SECONDARY | CONTACT TANK | END OF CLEANING OF TERTIARY POND
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2012-03-23 | 8:45A-12:15P |  | SECONDARIES | OUTFALL |  | ANNUAL CONTACT TANK CLEANING DONE AND BACK IN LINE BEFORE HAVE TO START FEEDING CHLORINE
IN0031071 | SHERIDAN MUNICIPAL STP | HAMILTON | 2012-08-26 | 11:30A-12:00P |  | SECONDARIES | CONTACT TANK | END OF CLEANING OF TERTIARY POND
IN0022306 | TOWN OF ATLANTA | HAMILTON | 2012-07-20 | 12:15-12:25 | 3500 | FORCE MAIN LEAK | GROUND | FORCE MAIN LEAK WAS SEEN BY A PERSON WALKING & REPORTED IMMEDIATELY | LIFT STATION WAS SHUT OFF IMMEDIATELY. THE RELEASE WAS GREY WATER WITH NO SOLIDS WATER QUICKLY SOAKED INTO GROUND
IN0059544 | WESTFIELD MUNICIPAL STP | HAMILTON | 2012-04-25 | ? - 3:00P | 3000 | 15590 TOWNE RD | GROUND | BROKEN AIR RELIEF VALVE | SHUT DOWN STATION AND REPLACED VALVE AND FITTINGS
IN0002925 | COVANCE LABS | HANCOCK | 2012-06-28 | 10:44A - 10:46P | 600 | UV BUILDING PRIOR TO ENTERING DISCHARGE PIPE | LEARY DITCH | UV BULBS TRIPPED RESULTING IN TEMPORARY LOSS OF DISINFECTION | CLOSED VALVES; REOPENED WHEN BULBS REGAINED POWER
IN0058009 | CUMBERLAND MUNICIPAL STP | HANCOCK | 2012-01-28 | 7:00A-7:30A | 1000 | 311 S 500 W MANHOLE | DOE CREEK | LIFT STATION PUMP CLOGGED MOTOR STARTER FAILURE, ALARM FAILURE A MINIMAL AMOUNT OF GREY WATER WAS BUBBLING THROUGH LID OF MANHOLE EST 500-1000 | FIXED THE LIFT STATION WITHIN 30 MINS OF OVERFLOW SHUT OFF OTHER IN FEEDING LIFT STATIONS TO STOP ADDITION FLOW. WALKED UP & DOWN DOE CREEK & DID NOT SEE ANYTHING
IN0058009 | CUMBERLAND MUNICIPAL STP | HANCOCK | 2012-05-06 | 4:05P-4:15P | 500 | MH NEXT TO NORTH PLANT LS | GROUND NEXT TO CREEK | BAD CONNECTION @ LIFT STATION ELECTRICAL PANEL ALARM SYSTEM FAILED | CALLED ELECTRICIAN TO FIX ELECTRICAL PANEL CALLED ALARM CO TO FIX ALARM SYSTEM
IN0051691 | EASTWAY DEVELOPMENT | HANCOCK | 2012-09-07 | 11:00P-10:00A | 90 | S AERATION BASIN | GROUND | BLOCKAGE INTO CLARIFIER | WILL BE PUMPING DOWN AERATION & REMOVING DEBRIS
IN0042358 | NEW PALESTINE WWTP | HANCOCK | 2012-08-07 | 10:00A-10:20A | 500 | MH # 5-6 | YARD | BAD LIFT STATION FLOATS | FIXED LIFT STATION. WASHED DOWN & VACUUMED SPILL AREA
IN0059013 | WESTERN HANCOCK UTILITIES | HANCOCK | 2012-04-24 | 11:20A-1:30P | 500 | AIR/VACUUM RELIEF MANHOLE | SMALL AREA IN FARM FIELD TO THE EAST | METAL BAND ON CLAMP BROKE ALLOWING SEWAGE TO FLOW AROUND THE VALVE & SQUEEZE OUT OF THE MH | WE USED OUR VACUUM TRUCK TO STOP THE OVERFLOW & PUMP DOWN THE MH; REPLACED CLAMP
IN0059013 | WESTERN HANCOCK UTILITIES | HANCOCK | 2012-05-02 | 6:47P-9:00P | 100 | MH E 12 ON ROCKINGHAM LANE | AREA AROUND MH & IN THE CURB NEARBY | THE MAIN SEWER WAS CLOGGED ON ROCKINGHAM LANE | CLEARED LINE AND RAN CAMERA
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2012-01-10 | 10:00A -1:00P | 200 | PRIVATE LATERAL 6 W. TILDEN AVE | GROUND | INFRASTRUCTURE IMPROVEMENTS BLOCKED LATERAL | EXPOSED AND REPAIRED LINE
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2012-05-01 | 4:18P - 5:30P | 150000 | CSO TANK OUTFALL 005 | WHITE LICK CREEK | RAIN 1.1" | PLANT FLOW MAXIMIZATION MAINTIANED DURING EVENT
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2012-05-02 | 3:45P - 4:00P | 3000 | 200 S GREEN ST | GROUND, STORM SEWER | BOTH PRIMARY SOURCES FAILED | INFLUENT CHANNEL GATE CLOSED MANUALLY TO ALLOW FLOWS TO GO INTO CSO STORAGE TANK
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2012-09-06 | 11:50A - 12:45P | 100 | 1080 N GREEN ST MH | GROUND | GREASE IN LINE | REMOVED DEBRIS, FLUSHED AREA
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2012-09-07 | 9:23P - 3:40A (9/8) | 4000000 | CSO TANK OUTFALL 005 | WHITE LICK CREEK | RAIN 2.1" | PLANT FLOW MAXIMIZATION MAINTAINED DURING EVENT
IN0021245 | BROWNSBURG MUNICIPAL STP | HENDRICKS | 2012-11-18 | 9:30P-11:30P | 100 | 538 NELSON DR BASEMENT SUMP TO STORM LINE | WHITE LICK CREEK | OBSTRUCTION IN SEWER LINE DUE TO ROOTS & DEBRIS | JET/VAC TRUCK WAS UTILIZED TO CLEAR ROOTS & DEBRIS.
IN0020079 | DANVILLE MUNICIPAL STP | HENDRICKS | 2012-11-10 | 2:00P-3:30P | 4500 | MH 122 ON SUNSET DR | GROUND | MAIN SEWER LINE PLUGGED WITH SANITARY DEBRIS | VAC/JET SEWER LINES VAC & CLEANED YARD
IN0057614 | HENDRICKS COUNTY RSD | HENDRICKS | 2012-08-17 | ?-1100 |  | MH EAST OF BULLARD CREEK LIFT STATION | BULLARD CREEK | CONTROL SYSTEM FAILURE CAUSING PUMPS TO NOT OPERATE AUTOMATICALLY | BBC PUMP SERVICE CALLED ON SITE FOR CONTROL SYSTEM REPAIRS ALSO HAVE 6" DIESEL PUMP ON SITE AS BACKUP
| MARSH CORPORATION | HENDRICKS | 2012-02-01 | 3:00P-4:30P | 2400 | FORCE MAIN IN CREEKBED @ STAFFORD ROAD BRIDGE | CLARKS CREEK | CONSTRUCTION RELATED DPW SEWER DEPT WAS NOTIFIED ON 2/2/12 @ 9AM THE FORCE MAIN CROSSING CLARKS CREEK DOES NOT HAVE MUCH COVER | GORDAN PLUMBING WAS NOTIFIED & MADE REPAIRS TO THE FORCE MAIN
| MARSH CORPORATION | HENDRICKS | 2012-02-07 | 4:00A-4:00P | 3600 | MANHOLE NORTH OF MARSH LIFT STATION | GROUND AND CLARKS CREEK | EQUIPMENT FAILURE LIFT STATION PUMP CONTROLLER FAILED NOT ALLOWING THE PUMPS TO COME ON IN AUTOMATIC | GORDON PLUMBING WAS NOTIFIED TO MAKE REPAIRS NO PREVENTIVE ACTION PLAN HAS BEEN SUBMITTED TO TOWN OF PLAINFIELD
| MARSH CORPORATION | HENDRICKS | 2012-12-09 | 12:00A-2:45P | 8000 | M H NORTH OF MARSH L S | GROUND & CLARKS CREEK | GREASE BLOCKAGE IN SEWER LINE. ON CALL OPERATOR FOR TOWN NOTICED OVERFLOW AND CONTACTED GORDON PLUMBING TO UNSTOP SEWER. | GORDON PLUMBING RESPONDED TO ON CALL OPERATOR PHONE CALL IN A TIMELY MANNER.
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2012-03-01 |  |  | 154 BRIXTON WEST DR., 467 WOODLAND DR. | GROUND TO WHITE LICK CREEK | 8" FORCE MAIN BREAK; PRESSURE CHANGE CAUSED SECOND BREAK | SHUT DOWN LS AND FIXED FORCE MAIN; WILL LIME AND RE-SEED AREA
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2012-12-03 |  |  | 164 BRIXTON WEST DR | GRASSY SWALE | 8 INCH FORCE MAIN BREAK | DUG UP AND FIXED FORCE MAIN
IN0020401 | PITTSBORO MUNICIPAL STP | HENDRICKS | 2012-12-12 |  |  | WWTP CLARIFIERS | CREEK | SCUM SOLIDS & FOAMING ACCUMULATED ON THE OUTER RING OF CLARIFIER. THE FOAM & SOLIDS WERE FREEZING UP AND NOT EXITING SLUDGE BOX CORRECTLY | CAUSE OF FOAMING IS UNKNOWN. CUT FLOWS TO TANKS, SCRAPED EXCESS SOLIDS INTO SCUM BOXES
IN0062456 | PLAINFIELD MUNICIPAL STP | HENDRICKS | 2012-04-05 |  |  | FORCE MAIN | GROUND | THE FORCE MAIN FOR THE MORES MEADOW SUBDIVISION WAS DAMAGED BY DIRECTIONAL BORING. ETC | REPAIRED FORCE MAIN
IN0021202 | PLAINFIELD NORTH WWTP | HENDRICKS | 2012-09-07 | 11:15P-3:45P |  | DEERFIELD PARK LIFT STATION | GROUND | RAIN 3.5 INFILTRATION IN SYSTEM | MONITOR STATION
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2012-01-16 | 8:30A - 9:15A | 500 | 365 SOUTH CR 550 EAST, AVON STATION HILL SUBD FORCE MAIN | GROUND | BROKEN FORCE MAIN | CLEANED AREA AND REPAIRED FORCE MAIN
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2012-02-12 | 12:40P - 12:47P | 2338 | 243 SOUTH COUNTY RD WASTE LINE OVERFLOW | RETENTION POND THEN CREEK | FROZEN WASTE SOLIDS BLOCKED LINE AFTER VALVE WAS OPENED | PUMP RETENTION POND AND CLEANED AREA
IN0051632 | WEST CENTRAL CONSERVANCY DIST | HENDRICKS | 2012-10-11 | 5:58P - 7:15P | 300 | MH | GROUND | GREASE | JETTED LINE AND CLEANED AREA
IN0055131 | SOUTH HENRY REGIONAL SEWER DIS | HENRY | 2012-10-01 | 10:00A-1:09A | 5000 | EASTSIDE OF ST RD 3 ACROSS FROM MR FUEL TRUCK PLAZA HOLWAGER DR & ST RD 3 | GROUND | BORING COMPANY PUTTING IN SEWER LINES FOR NEW FUEL TRUCK STOP HIT 3" SEWER LINE & 6" SEWER LINE. LINE WAS LOCATED. | SHUT OFF PUMP STATION @ FLYING J TRUCK PLAZA TO STOP SEWAGE FROM SPILLING ON THE GROUND WHEN POSSIBLE. CALLED A CONTRACTOR TO COME IN & FIX THE LINE.
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2012-01-17 | 5:40A-7:15P |  | OUTFALL 002 | BRUNK DITCH | RAIN 1.2" | PLANNED REDESIGN & RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2012-01-17 | 1:00P-6:30P (1/19) |  | SURGE BASIN | POLISHING PONDS | RAIN 1.2" | PLANNED REDESIGN & RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2012-01-26 | 2:30P - 10:00P |  | SURGE BASIN | POLISHING PONDS | RAIN 1.3" | PLANNED REDESIGN & RECONSTRUCTION OF PLANT
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2012-01-26 | 10:35A - 2:20A (1/27) |  | OUTFALL 002 | BRUNK DITCH | RAIN 1.3"
IN0021091 | GREENTOWN MUNICIPAL STP | HOWARD | 2012-09-07 | 11:15P-12:50A |  | OUTFALL 002 | BRUNK DITCH | RAIN 2.2"
IN0020532 | RUSSIAVILLE MUNICIPAL STP | HOWARD | 2012-05-04 | 11:30-11:35 | 100 | DRYING BED @ RUSSIAVILLE WWTP | GROUND | DRYING BED OVERFLOWED | USED VACTOR TO REMOVE SLUDGE; CLEANED AREA
IN0020532 | RUSSIAVILLE MUNICIPAL STP | HOWARD | 2012-06-29 | 5:15P - 5:35P | 6000 | OUTFALL 002 & MH UPSTREAM OF WWTP | GROUND AND HONEY CREEK | RAIN 1.1" POWER OUTAGE | STAFF RESTARTED INFLUENT PUMPS
IN0020532 | RUSSIAVILLE MUNICIPAL STP | HOWARD | 2012-09-07 | 8:00P - 11:30P | 42000 | MH IMPLANT THAT DRAINS TO RAW STATION | GROUND AT WWTP AND HONEY CREEK | RAIN 2.5" I&I | MAXIMIZED PUMPING AND TREATMENT TO THE PLANT TO MINIMIZE OVERFLOW
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2012-03-21 | 1:45P - 4:45P | 3100 | MH GIS I07_W002 | DITCH - STORM SEWER | BROKEN FORCE MAIN AND GREASE | BYPASS PUMPED; VACUUMED AREA; WILL FIX PIPE
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2012-05-01 |  | 1 | FORCE MAIN 6" DUCTAL IRON | GROUND | CRACK IN PIPE | SECTION TO BE REMOVED AND REPLACED
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2012-10-15 | 9:40A - 9:50A | 10 | AIR RELIEF VALVE BOX OF FORCE MAIN | GROUND | AIR RELIEF VALVE RUSTED APART AT SHUT OFF | USED VAC TRUCK TO CLEANED GROUND; INSTALLING NEW VALVE
IN0024473 | SEYMOUR MUNICIPAL STP | JACKSON | 2012-11-21 | 1:00P - 2:00P | 75 | MH @ US 50 AND BUSH ST. | US 50 | SEWER LINE PLUGGED | CLEANED LINE
IN0051331 | STARVE HOLLOW SRA | JACKSON | 2012-06-23 | 2:00A - 10:30A | 1000 | SLUDGE HOLDING TANK | GROUND | OPERATOR WASTED EXCESS LIQUEUR INTO SLUDGE HOLDING TANK AND FORGOT TO TURN VALVE OFF | PUMPED SOME OFF HOLDING TANK INTO WINTER STORAGE TANK
IN0053201 | NIPSCO RM SCHAHFER GENERATING STATION | JASPER | 2012-03-19 | 9:30A-11:20A |  | SEWAGE TREATMENT PLANT (STP) | GROUND AREA ADJACENT TO STP | THE OVERFLOW CONDITION WAS TRACKED TO EQUIPMENT FAILURE IN A REMOTE AREA MEN'S RESTROOM | IMMEDIATE ACTION WAS TO CONTAIN THE FLOW TO THE AREA SURROUNDING THE STP, INITIATE SEARCH TO FIND THE SOURCE OF THE INCREASED FLOW AND CONTRACT THE NIPSCO EMERGENCY ETC
IN0053201 | NIPSCO RM SCHAHFER GENERATING STATION | JASPER | 2012-04-18 | 9:00A-11:00A |  | SEWAGE TREATMENT PLANT | GROUND AREA ADJACENT TO STP | OPERATOR ERROR COMBINED WITH EQUIPMENT FAILURE | CONTAINED SPILL BY PUTTING MORE PUMPS IN SERVICE TO LOWER VOLUME AND STOP FLOW
IN0053201 | NIPSCO, BAILEY GENERATING STATION | JASPER | 2012-03-24 | 3:15P-3:20P |  | 2723 E 1500 N WHEATFIELD, IN | AREA ADJACENT TO 17/18 LIFT STATION | CONSTRUCTION RELATED OCCURRED WHEN A LINE CLEANOUT ADJACENT TO A LIFT STATION WAS STRUCK BY A PIECE OF EQUIPMENT AND THE LINE WAS BROKEN APPROX 1' ETC | ADDITIONAL CLEANUP ACTIVITIES ARE CURRENTLY UNDERWAY
IN0039101 | WATER SERVICE CO OF INDIANA | JASPER | 2012-02-06 | 5:30P-6:00P | 5 | 9467 BAHAMA DR | GROUND | RAGS IN SEWER MAIN RESTRICTING FLOW | PUT LIME DOWN AROUND DOWN PIPE. JETTED SECTION OF SEWER MAIN
IN0039101 | WATER SERVICE CO OF INDIANA | JASPER | 2012-03-27 | 16:00-17:00 | 10 | 11933 MONTEGO LN | GROUND | RAGS IN SEWER MAIN RESTRICTING FLOW THE SEWER MAIN WAS JETTED OUT AND THE FLOW RETURNED TO NORMAL | APPLIED LIME AROUND SEWER LATERAL STUB
IN0050211 | BEAR CREEK FARMS WWTP | JAY | 2012-01-17 | ?AM-2:00P | 2500 | COMMISSARY GREASE TRAP | BEAR CREEK DITCH | RAIN 1.59" BLOCKAGE IN GREASE TRAP | BOD,TSS SAMPLE TAKEN IN BEAR CREEK DITCH DOWN STREAM OF PLANT OUTFALL CLEAN GREASE TRAP
IN0024406 | REDKEY MUNICIPAL STP | JAY | 2012-07-17 | 12:00P-7:30P |  | MH CSO # 8 | STORM SEWER, STREAM | CONSTRUCTION RELATED BACKED UP SEWER LINE | VAC TRUCK FROM CULY CONSTRUCTION & EXCAVATING INC
IN0024406 | REDKEY MUNICIPAL STP | JAY | 2012-09-13 | 2:00P - 5:30P | 210 | CSO #8 | STREAM | GREASE FROM BELL AQUACULTURE | BELL AQUACULTURE IS DOING PRETREATMENT
IN0066168 | TOWN OF SALAMONIA | JAY | 2012-09-14 | 7:00P-12:00P |  | OUTFALL 001 | PERRY DITCH | RAIN; DISCHARGE DUE TO THE PONDS BEING @ CAPACITY. DISCHARGE TO DRY STREAM TO PREVENT BREECHING OF LAGOON LEVY. | REDUCED DISCHARGE RATES
IN0024210 | FORD BUILDING & LUMBER WWTP | JEFFERSON | 2012-07-01 | 8:00P - 2:00P (7/2) |  | PLANT | STREAM | RAIN 2" POWER OUTAGE | WILL RESTORE POWER
IN0020702 | HANOVER MUNICIPAL STP | JEFFERSON | 2012-01-17 | 11:00A-14:00 |  | 259 E 1ST ST | UNNAMED DRAINAGE DITCH | RAIN 3+ "
IN0020702 | HANOVER MUNICIPAL STP | JEFFERSON | 2012-07-01 | 7:00P - 8:30P |  | 259 1ST ST MH | CROWE CREEK | RAIN 2"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-01-09 | 2:00P - 3:00P | 100 | FRANK'S DR | CROOKED CREEK | BROKEN SEWER MAIN | REPLACED WITH 8" DUCTILE AND CLEANED AREA
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-01-17 | 3:30A-8:05P | 1570000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 1.6"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-01-23 | 3:40A-3:20P | 920000 | WASTEWATER TREATMENT PLANT | OHIO RIVER | RAIN .83" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-01-26 | 5:50P - 2:20P (1/27) | 1030000 | PLANT | OHIO RIVER | RAIN .5" | BLENDED WITH FINAL EFFLUENT AND SAMPLED
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-01-27 | 2:00AM-5:00A | 0.04 | WELL'S DR LIFT STATION | DEAN BRANCH CREEK | RAIN 1.5 | CLEANED UP AREA AROUND MH AND LIFT STATION
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-02-04 | 10:45A-1:10P | 1000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 0.4 | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-02-29 | 5:00A-3:00P | 600000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 1.1" | NONE
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-03-23 | 3:45P-7:30A | 590000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 1.42"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-03-30 | 11:15P - 2:25A (3/31) | 156000 | PLANT | OHIO RIVER | RAIN .71"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-03-30 | 11:15P-2:25A | 237 | WASTEWATER TREATMENT PLANT | OHIO RIVER | RAIN .71"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-04-04 | 3:00P-5:40P | 35000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 0.35"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-04-05 | 7:30A-3:40P | 811000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 0.6"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-04-08 | 2:15P-3:15P |  | 1928 LANIER DR | BASEMENT
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-05-04 | 10:50P-3:00A | 8 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 1.1"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-05-13 | 1:10P-6:20P | 280000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 1.1" | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-05-29 | 9:00A-11:20A | 100000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 0.64
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-06-01 | 3:30P-10:20A | 150000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | HEAVY RAIN | LTCP
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-07-01 | 9:30P - 9:50P |  | HEREFORD DAME LS | HEREFORD LAKE OVERFLOW STREAM | POWER LOSS TRIPPED BOTH PUMPS | RESET BOTH PUMPS AND WILL INSTALL AND DIALER SYSTEM
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-09-08 | 8:00A-11:30P | 3000 | MH S SR 7 (HANGING ROCK HILL) | CROOKED CREAK | RAIN 2.4" | CLEANED UP AREA AROUND MH & WASHED DOWN STORM DRAIN
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-10-01 | 6:00P-10:40P | 440000 | WATER POLLUTION CONTROL FACILITY | OHIO RIVER | RAIN 1.36"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-10-15 | 4:30P - 8:30P | 500 | MH #4-F1-11 | STORM SEWER | MH PLUGGED WITH GREASE | CLEANED MH AND FLUSHED 1000' OF SEWER MAIN
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-11-10 | 12:25P-2:35P | 37880 | VAUGHN DR L S | OHIO RIVER | STATION OVERFLOWED DUE TO ELECTRIC PROBLEM ON DUKE ENERGY'S SIDE AT SUB STATION | CLEANED AREA AROUND OVERFLOW
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-11-12 | 6:44P-8:30P |  | STATE STR. & BLACKMORE STR | STORM SEWER | BLOCKAGE IN GRAVITY LINE. | FLUSHED & CLEANED LINE.
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-12-09 | 8:35P-4:50A | 1117000 | WPCF | OHIO RIVER | RAIN 1.34"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-12-20 | 11:25A - 3:35P | 180000 | PLANT | OHIO RIVER | RAIN .69"
IN0025666 | MADISON MUNICIPAL STP | JEFFERSON | 2012-12-26 | 8:10A - 1:00P | 3000 | PLANT | OHIO RIVER | RAIN .55" SNOW
IN0056049 | JENNINGS NORTHWEST REGIONAL UT | JENNINGS | 2012-09-03 | 8:30A-8:00P | 5500 | LOT 384 FORCE MAIN | GROUND | 8" FORCE MAIN WAS BLOCKED DUE TO THE AIR RELIEF VALVE WORKING INCORRECTLY | PRESENT AIR RELIEF VALVE HAS BEEN PUT ON A SCHEDULE TO BE CHECKED WEEKLY. THE AFFECTED GROUND WAS CLEANED UP & LIME PUT ON THE AFFECTED GROUND
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-01-17 | 1:00P-1:45P | 23000 | NORTHEAST LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 1.1"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-01-17 | 10:30A-1:30P | 10000 | SOUTHWEST LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 1.1" SEWER DRAINAGE BASIN RECEIVED APPROX 1.1 RAIN IN 4 HR
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-01-17 | 10:40A-12:50P | 5000 | NORTHWEST LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 1.1
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-01-17 | 11:00A-12:30P | 4000 | NORRIS AVE LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 1.1 IN 4 HR, MUSCATATUCK RIVER FLOW INCREASED DRY WEATHER
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-03-23 | 11:15P-2:30A |  | NORRIS AVE LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 2.9"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-03-23 | 11:30P-2:00A |  | NORTHWEST LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 2.9"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-03-23 | 11:00P-3:10AM |  | NORTHEAST LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 2.9"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-03-24 | 12:00A-1:30P |  | SOUTHWEST LIFT STATION | UNNAMED DRAINAGE SWALE | RAIN 2.9"
IN0020451 | NORTH VERNON MUNICIPAL STP | JENNINGS | 2012-10-05 | 11:00P - 11:30P |  | NORTHWEST LS | UNNAMED DRAINAGE SWALE | POWER FAILURE AT LS; RAIN
IN0022314 | BARGERSVILLE MUNICIPAL STP | JOHNSON | 2012-01-11 | (1/12) |  | 135 LS | GROUND | BLOWN FUSE | CHANGED FUSE AND WILL MONITOR
IN0022314 | BARGERSVILLE MUNICIPAL STP | JOHNSON | 2012-11-12 | 1:30P-2:15P | 150 | MH 300 OLD S STREET | STORM SEWER | SEWER HAD BACKED UP & CAUSED OVER FLOW. RUN VAC TRUCK & JETTED LINE UNTIL CLOGGED WAS REMEDIED. | RUN VAC TRUCK & JETTED LINE UNTIL CLOGGED WAS REMEDIED.
IN0021181 | FRANKLIN MUNICIPAL STP | JOHNSON | 2012-06-28 |  |  | SANITARY SEWER LINE/HOSPITAL ROAD | STORM SEWER/YOUNG'S CREEK | HOLE IN SANITARY LINE WAS LEAKING TO COUNTY CORRUGATED PIPE ALSO WITH HOLE | EXCAVATED AREA AND REPAIRED PIPE
| GREENWOOD, CITY OF | JOHNSON | 2012-01-03 | 10:00A - 10:25A |  | 4356 OLIVE BRANCH RD | GROUND | PUMP OVERHEATED AND ALARM FAILED | CLEANED AREA AND WILL CHECK ALARM
| GREENWOOD, CITY OF | JOHNSON | 2012-01-12 | 3:04P- 3:45P |  | 315 LAWNWOOD | BASEMENT | BLOCKAGE IN MAIN SEWER LINE HOME OWNER'S CLEANED UP BASEMENT | JETTED LINE OPEN
| GREENWOOD, CITY OF | JOHNSON | 2012-01-27 | UNK-7:30P |  | MH 83A AREA 29C | GROUND | STOPPED IN MAIN SEWER LINE | CLEANED UP AROUND MANHOLE
| GREENWOOD, CITY OF | JOHNSON | 2012-01-30 | 10:15A-10:45A |  | LINE HAD BLOCKAGE | BASEMENT | VACTOR CLEAN LINE 407 LINE HAD BLOCKAGE OWNER CLEANED UP BASEMENT. | WE PERFORM ROUTINE MAINTANCE TO CLEAN LINES
| GREENWOOD, CITY OF | JOHNSON | 2012-02-25 | ?-7:00P |  | MANHOLE #3 AREA 10 | GROUND AND STREAM | BROKEN SEWER LINE | BYPASS PUMPED TO DOWN STREAM MANHOLE WHILE WE OPEN LINE
| GREENWOOD, CITY OF | JOHNSON | 2012-03-01 |  |  | MH | GROUND | STOPPAGE IN MAIN | JETTED LINE OPEN, WILL TV
| GREENWOOD, CITY OF | JOHNSON | 2012-03-27 | 6:51P-7:45P |  | 239 VICTORY LANE | INSIDE HOUSE | HAD STOPPAGE IN LINE BETWEEN MH # 34 & #35 AREA 22C | ROOT SAWED LINE
| GREENWOOD, CITY OF | JOHNSON | 2012-04-09 | ? - 6:00P |  | WESTMINSTER VILLAGE APTS | STORM SEWER TO FOUNTAIN CREEK | WEST MINISTER VILLAGE APTS IS A PRIVATE SEWER SYSTEM. SYSTEM BACKED UP THEY HAVE A SANITARY MAN HOLE W/OVERFLOW PIPE THAT DUMPS
| GREENWOOD, CITY OF | JOHNSON | 2012-06-08 | 11:00A-11:45A |  | 1601 E. MAIN ST. MH | CONFINED ON GROUND/STORM SEWER | PROPERTY OWNER INSTALLED FENCE POST THROUGH PRIVATE SERVICE LINE, CAUSING SURCHARGE FROM MH | STORM SEWER DAMNED OFF. WASTE WATER RECOVERED AND RETURNED TO SANITARY SYSTEM GROUND AND STORM PIPES WERE CLEANED.
| GREENWOOD, CITY OF | JOHNSON | 2012-06-25 | ? - 9:00A | 20 | 1221 TREE TOP LANE MH | GROUND | BLOCKAGE IN LINE BETWEEN MH'S 106 & 107 | JETTED LINE OPEN; TELEVISING LINE TO SEE IF IT NEEDS TO BE REPAIRED OR REPLACED
| GREENWOOD, CITY OF | JOHNSON | 2012-07-09 | UNKNOWN-1:30P | 25 | 1103 N SR 135 | GROUND | GREASE IN MAIN SEWER LINE | JETTED LINE & CLEAN UP AROUND CLEAN OUT WITH VAC TRUCK
| GREENWOOD, CITY OF | JOHNSON | 2012-07-13 | 10:30A-11:30A |  | FORCE MAIN | OPEN DITCH | FORCE MAIN LEAK | USED 2 VACTOR'S # 2 PUMPER TRUCKS FROM FLUID WASTE TO KEEP WET WELL PUMPED DOWN WHILE WE MADE REPAIRS
| GREENWOOD, CITY OF | JOHNSON | 2012-07-30 | ?-8:45A | 10 | MH | GROUND | STOPPAGE IN MAIN SEWER LINE | JETTED & CLEANED LINE VAC & CLEANED UP AROUND MH
| GREENWOOD, CITY OF | JOHNSON | 2012-08-10 | 10:30A - 1:30P | 1000 | 4420 FOX RIDGE FORCE MAIN | GROUND | RUPTURED 6" FORCE MAIN | PUT IN NEW PIPE AND CLEANED WITH VAC TRUCK
| GREENWOOD, CITY OF | JOHNSON | 2012-09-04 | 9:00P-9:45P | 100 | MH | STORM SEWER | BLOCKAGE OF GREASE IN MAIN LINE | CLEAN LINE & STORM LINE CLEAN UP AROUND MH
| GREENWOOD, CITY OF | JOHNSON | 2012-09-07 | 11:30P - 12:40A (9/8) |  | MH | PLEASANT RUN CREEK | RAIN 3" RAIN INDUCED INFLOW | LOCATING SOURCE OF INFLOW
| GREENWOOD, CITY OF | JOHNSON | 2012-09-08 | 8:00A-5:00P |  | MH | STORM SEWER | HAD A BLOCKAGE IN SEWER MAIN | JETTED OPEN LINE, CLEANED STORM LINE VAC AROUND MH 82
| GREENWOOD, CITY OF | JOHNSON | 2012-09-30 | 7:00P-8:15P |  | 756 SABLE RIDGE LA | GROUND, SIDEWALK | HAD STOPPAGE IN MAIN LINE. ROOTS FROM TREE BY MH | JETTED LINE OPEN; VAC & SPRAYED DOWN SIDEWALK & STREET GUTTER.
| GREENWOOD, CITY OF | JOHNSON | 2012-10-25 | ?-11:00P |  | 537 SHADY LANE M H | GROUND | STOPPAGE IN MAIN SEWER LINE. CLEAN UP AROUND M H W/ VAC TRUCK | JETTED LINE OPEN. CLEAN UP AROUND M H W/ VAC TRUCK
| GREENWOOD, CITY OF | JOHNSON | 2012-11-06 | ?-11:45A |  | EMERALD LAKES DRIVE | GROUND | TREE PLANTED NEXT TO MH ROOTS GREW DOWN LINE THROUGH MH. | REMOVED ROOTS, JETTED LINE OPEN
| GREENWOOD, CITY OF | JOHNSON | 2012-11-21 | 6:10P-7:00P |  | 689 HILLCREST DR | BASEMENT | BLOCKED SEWER MAIN | JETTED LINE OPEN
| GREENWOOD, CITY OF | JOHNSON | 2012-12-24 | 11:00P |  | GREENWOOD ESTATES TRAILER PARK PRIVATE SYSTEM | GROUND | BLOCKED CLEAN OUT | JETTED OPEN; WILL CONTACT PARK OWNERS
IN0042366 | PRINCES LAKE MUNICIPAL STP | JOHNSON | 2012-08-06 | 5:00P-5:30P | 300 | PRINCESS LAKE MAIN LIFT STATION | AREA SURROUNDING LOCATION | DURING DAILY INSPECTION STAFF ON SITE FORGET TO TURN PUMP CONTROLS TO AUTO POSITION LEADING TO EVENTUAL OVERFLOW OF STATION | SPOKE TO STAFF ABOUT THE ISSUE
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2012-01-17 | 11:15A-12:30P |  | FROM N CLARIFIER + DITCH | BREWER DITCH | RAIN | PLANT WAS IN STORM MODE WE HAVE HAZEN & SAWYE PC WORK ON A EVALUATION
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2012-03-24 | 12:30A-? |  | CLARIFIERS & WEST OF DITCH | BREWER DITCH | RAIN 2.61" | PLANT WAS IN STORM MODE.
IN0021415 | WHITELAND MUNICIPAL STP | JOHNSON | 2012-04-01 | ?-5:35P |  | LOST SOLIDS OUT OF WEST CLARIFIER | BREWER DITCH | RAIN .75" RETURN PUMP # 2 WAS AIR LOCKED | BLEED PUMP AND GOT IT BACK TO NORMAL PUMPING
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2012-03-08 | 11:00A - 11:30A | 500 | CLEAN OUT 315 E FIRST ST. | YARD | BLOCKAGE IN LATERAL | JETTED LINE
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2012-04-23 | 19:50-20:10 | 100 | BACKUP INTO BASEMENT | CONTAINED IN CONCRETE BASEMENT | BLOCKAGE IN LINE | JETTED LINE
IN0039276 | BICKNELL MUNICIPAL STP | KNOX | 2012-09-24 | 11:35-12:05 | 100 | MH 63 ALONG ALEXANDER ST BETWEEN 5TH & 6TH | STORM WATER DITCH RUNNING PARALLEL TO 6TH ST | A BLOCKAGE IN LATERAL 1-10 BTW MH 63 & 80 CAUSED A BACK UP IN MH 80. NO HOMES WERE EFFECTED | LINE WAS JETTED NUMEROUS TIMES TO REMOVE DEBRIS & BLOCKAGE. AREA WHERE OVERFLOW OCCURRED WERE WASHED DOWN & LIME WITH AGRICULTURAL LIME.
IN0062685 | SANDBORN WWTP | KNOX | 2012-03-02 | 15:00-05:30 | 500 | 125 MAPLE ST FORCE MAIN( DISCHARGE LINE) | GROUND | DETERMINED IT TO BE A LEAK IN DISCHARGE LINE FROM WASTEWATER TREATMENT PLANT WATER WAS FULLY TREATED & DISCHARGE TO OUTFALL | EXPOSED DISCHARGE LINE & REPAIRED
IN0053783 | MEADOWS ACRES MOBILE HOME PARK | KOSCIUSKO | 2012-03-13 |  |  | CLEAN OUT | GROUND | BROKEN LINE | SEWER LINE JETTED AND REPAIRED
| TOWN OF NORTH WEBSTER | KOSCIUSKO | 2012-03-16 |  |  | MH | STREET & ROADSIDE | SYSTEM EXPERIENCED A PLUG THAT RESULT IN A BACK UP @ MH | PERSONNEL RESPONDED TO CALL OUT AND JETTED THE LINE ETC
IN00221172 | TOWN OF SYRACUSE | KOSCIUSKO | 2012-03-19 |  |  | FORCE MAIN | GRASS YARD | PROPERTY OWNER CALLED & REPORTED THE LEAK COMING TO THE SURFACE IN THEIR YARD | DIGGING UP THE FORCE MAIN TO MAKE A REPAIR
| TOWN OF WINONA LAKE | KOSCIUSKO | 2012-06-18 | 10:00P-10:35P | 700 | LIFT STATION | GROUND | ELECTRIC FAILURE AT LIFT STATION | CLEANED UP. WE ARE IN THE PROCESS OF INSTALLING A SCADA SYSTEM ON ALL ARE LIFT STATIONS
IN0045802 | TURKEY CREEK RSD | KOSCIUSKO | 2012-10-14 | ?-8:30A |  | TREATMENT PLANT | RECEIVING STEAM | NORTH CLARIFIER RETURN LINE PLUGGED | SHUT CLARIFER DOWN, UNPLUGGED RETURN
IN0024805 | WARSAW WWTP # 1 | KOSCIUSKO | 2012-01-23 | UNKNOWN-10:00A | 1000 | 1501 FISHER AVE MANHOLE | STORM SEWER | EQUIPMENT FAILURE THE HOMEOWNER SAID IT HAD BEEN OVERFLOWING FOR A COUPLE OF WKS SLOWLY. THE HOMEOWNER THOUGHT IS WAS STORM WATER & DIDN'T NOTIFY US TILL TODAY. WE HAD THE OVERFLOW STOPPED WITHIN AN HR | WE WILL SPREAD LIME ON THE GROUND & CHECK THE STORM OUTFALL TO ENSURE DEBRIS IS CLEANED UP
IN0060917 | WARSAW WWTP # 2 | KOSCIUSKO | 2012-08-23 | 1:20P-1:35P | 9250 | FORCE MAIN | GROUND | DURING THE INSTALLATION OF A NEW FORCE MAIN A CAP CAME OFF OF THE EXISTING 10" FORCE MAIN. A VALVE WAS CLOSED TO STOP THE FLOW AND THE TRENCH WAS CLEANED OUT WITH A VAC TRUCK | A VALVE WAS CLOSED TO STOP THE FLOW AND THE TRENCH WAS CLEANED OUT WITH A VAC TRUCK
IN0060917 | WARSAW WWTP # 2 | KOSCIUSKO | 2012-10-01 | 21:30-22:45 | 300 | 2605 HOLIDAY DR | GROUND | A BLOCKED SEWER LINE WAS DETERMINED TO BE THE CAUSE OF THE OVERFLOW. | THE LINE WAS JETTED & CLEARED OF THE BLOCKAGE. THE AREA AROUND THE MH WAS CLEANED
IN0060917 | WARSAW WWTP # 2 | KOSCIUSKO | 2012-11-16 | 12:30-15:00 | 1000 | 841 S UNION ST | BASEMENT OF A DENTAL OFFICE | THERE WAS A ROOT BLOCKAGE IN THE LINE WHICH CAUSED A BACKUP INTO THE BASEMENT OF A DENTAL OFFICE. | THE BLOCKAGE WAS REMOVED AND FLOW IN THE PIPE WAS RESTORED. THE DENTAL OFFICE HAS A CLEAN UP CREW IN THE BASEMENT.
IN0060917 | WARSAW WWTP # 2 | KOSCIUSKO | 2012-11-25 | 10:43A-12:10 | 150 | 2605 HOLIDAY DR | GROUND | BLOCKED SEWER LINE | CLEARED BLOCKAGE. THE AREA AROUND THE MH WAS CLEANED. LIME WAS APPLIED TO THE GROUND THE MH
IN0024805 | WARSAW WWTP #1 | KOSCIUSKO | 2012-09-19 | ? - 4:02P |  | 1501 ST RD 15 SOUTH | STORM SEWER | BLOCKAGE IN LINE | STORM CATCH BASIN CLEANED WITH VAC TRUCK
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-01-04 | 1:22P 2:12P | 25 | 122/126 PHILLIPS AVE | BASEMENT | DEBRIS IN MAIN | FLUSHED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-01-09 | 11:17A - 11:36A | 20 | 325 SPRINGLAND | BASEMENT | DEBRIS IN MAIN | JETTED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-01-23 | 4:00P - 12:25A (1/24) | 50 | 522 S. CALUMET BASEMENT | BASEMENT | MAIN WAS PLUGGED | RELIEVED SURCHARGE AND REPAIRED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-02-05 | 1:40P-2:50P | 30 | 2544 WABASH ST | BASEMENT FLOOR | SANITARY DIST RECEIVED A CALL FROM THE HOMEOWNER STATING THEY BACKUP INTO THE BASEMENT | SANITARY DIST CREW RESPONDED TO THIS ADDRESS @ 2:10P ON 2/5/12 & FOUND MAIN SEWER TO THIS ADDRESS WAS PLUGGED WITH DEBRIS ETC
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-02-10 | 11:18A-11:58A | 15 | 426 BUTLER ST | BASEMENT | SANITARY DISTRICT RECEIVED A CALL FROM THE HOMEOWNER @ 11:18A ON 2/10/12 AND FOUND THE MAIN SEWER WAS PLUGGED WITH RODS AND GREASE | SANITARY DISTRICT CREW RESPONDED TO THIS ADDRESS @ 11:43A ON 2/10/12
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-02-11 | 8:40A-10:00A | 400 | 130 BUTLER ST | BASEMENT FLOOR | SANITARY DISTRICT RECEIVED A CALL FROM THE HOMEOWNER @ 8:40A ON 2/11/12 STATING THEY HAD BACKUP INTO THE BASEMENT | SANITARY DISTRICT CREW RESPONDED TO THIS ADDRESS @ 8:45A ON 2/11/12 AND FOUND THE SEWER MAIN PLUGGED WITH GREASE ETC
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-02-12 | 12:45P-2:27P | 40 | 1901 EAST BARKER AVE | BASEMENT FLOOR | SANITARY DIST RECEIVED A CALL FROM THE HOMEOWNER @ 12:45P ON 2/12/12 STATING THEY HAD BACKUP INTO THE BASEMENT. PRIVATE CONTRACTOR WORKING ETC | SANITARY DIST CREW RESPONDED TO THIS ADDRESS @ 1:28P ON 2/12/12 AND FOUND THE SEWER MAIN PLUGGED
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-02-16 | 4:40P-5:23P | 2 | 319 EAST 11TH ST | BASEMENT FLOOR | SANITARY DIST RECEIVED A CALL FROM THE HOMEOWNER @ 4:40P ON 2/16/12 STATING THEY HAD BACKUP INTO THE BASEMENT LINE IS 6' VCP & AND IS QUESTIONABLE IF IT IS PRIVATE SEWER | SANITARY DIST CREW RESPONDED TO THIS ADDRESS @ 4:40P ON 2/16/12 AND FOUND THE SEWER PLUGGED WHILE CLEANING LINE CREW ALLEVIATED PLUG BY 5:23P
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-02-28 | 8:25A-9:47A | 10 | 526 FIR ST | BASEMENT FLOOR | SANITARY DISTRICT RECEIVED A CALL FROM THE HOMEOWNER @ 8:25A ON 2/28/12 STATING THEY HAD BACKUP INTO THE BASEMENT | SANITARY DISTRICT CREW RESPONDED TO THIS ADDRESS @ 9:20A ON 2/28/12 AND FOUND THE SEWER LINE PLUGGED. ETC
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-02-29 | 10:38A-12:10P | 200 | 107 SOUTH COURT | GROUND | SANITARY DISTRICT RECEIVED A CALL FROM THE HOMEOWNER @ 10:38A ON 2/29/12 STATING WATER WAS BUBBLING OUT OF THE MANHOLE LOCATED IN THE BACKYARD | SANITARY DISTRICT CREW RESPONDED TO THIS ADDRESS @ 11:30A ON 2/29/12 AND FOUND THE SEWER MAIN PLUGGED WITH ROOTS CREW ALLEVIATED PLUG BY 12:10 PM 2/29/12
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-04-02 | 1:23P-2:08P | 100 | CLEAN OUT IN YARD | STORM CATCH BASIN TO TRAIL CREEK | SANITARY DISTRICT RECEIVED A CALL FROM A WATER DEPT EMPLOYEE ABOUT SEWAGE OVERFLOWING FROM A PRIVATE HOME | SANITARY DISTRICT CREW RESPONDED
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-04-04 | 11:55A-12:45P | 2 | 121 STINSON COURT | BASEMENT FLOOR | SANITARY DISTRICT RECEIVED CALL @ 11:55A ON 4/4/12 FROM PROPERTY OWNER REPORTING SEWAGE ON BASEMENT FLOOR | SANITARY DISTRICT CREW RESPONDED
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-04-05 | 10:30A-11:00A | 150 | 409 YORK ST | BASEMENT FLOOR | BLOCKAGE | SANITARY DISTRICT CREW RESPONDED
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-04-08 | 1:45P - 2:20P | 223854 | FILTER BUILDING | TRAIL CREEK | POWER OUTAGE STOPPED INFLUENT FLOW TO BUILDING | RESTARTED CLEAR WELL PUMPS
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-04-12 | 6:32P-8:18P |  | 901 W COOLSPRING AVE | BASEMENT FLOOR | PLUGGED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-04-23 | 12:32P-1:36P | 30 | 208 E BARKER AVE | BASEMENT | ROOTS | CREW ALLEVIATED PLUG
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-05-10 | 9:01A - 10:00A | 200 | 211 W 9TH ST | BASEMENT FLOOR | DEBRIS/ROOTS | CREW ALLEVIATED PLUG
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-06-24 | 7:32A - 9:20A | 25 | 1954 LAKESHORE DR MH | GROUND | DEBRIS | ALLEVIATED PLUG AND CLEANED MH
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-07-09 | 10:42A - 2:45P | 50 | 1509 LAKESHORE | GROUND | PRIVATE MATTER | HOMEOWNER WILL CALL PLUMBER
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-07-23 | 7:45A-2:00P | 5 | CLARK LIFT STATION FORCE MAIN | GROUND | CRACK IN FORCE MAIN | REPAIRED FORCE MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-07-31 | 4:54A-5:40A | 15 | 714 TREMONT ST | BASEMENT FLOOR | GRASS & LEAVES | UNPLUGGED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-09-18 | 8:51A - 10:02A |  | 325 SPRINGLAND RD | BASEMENT | DEBRIS PLUG IN MH | MH JETTED AND CLEANED
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-09-27 | 12:02P-1:15P | 10 | 217 CHARLES ST | BASEMENT FLOOR | SANITARY DIST RECEIVED CALL FROM SEWER CONTRACTOR THAT 217 CHARLES ST IS EXPERIENCING BACK-UP IN BASEMENT | JETTED AND CLEANED MAIN LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-10-29 | 9:30A - 10:30A | 3 | 230 COOK ST. | BASEMENT FLOOR | DEBRIS IN MAIN | FLUSHED LINE
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-12-24 | 4:40P - 10:00P | 750 | 606 WOODLAND AVE | FLOOR | COLLAPSED DISTRICT MAIN | REPAIRED MAIN
IN0023752 | MICHIGAN CITY SANITARY DIST. | LA PORTE | 2012-12-26 | 7:00P - 8:00P | 1000 | WOODLAND & GREENWOOD | STREET TO STORM SEWER TO TRAIL CREEK | TEMPORARY PIPING ON STREET FOR PREVIOUS BYPASS DAMAGED | SET UP ADDITIONAL BARRICADES
| ALL AMERICAN CAMPGROUND | LAGRANGE | 2012-05-07 | ?-3:30P | 10000 | METER PIT STRUCTURE | GROUND | THE CONNECTION OF THE FLOW METER CAME APART | THE WATER TYPE OF STEEL WRAP AROUND CLAMP WAS REQUIRE ON RE-INSTALL
IN0060097 | LAGRANGE CO REGION B UTILITY DISTRICT | LAGRANGE | 2012-04-11 | 4:05A-6:30A | 6000 | LIFT STATION #1 @ 10640 W/4755 | GROUND | POWER FAILURE | STAND BY GENERATOR USED TO POWER STATION
IN0062014 | REGION A | LAGRANGE | 2012-03-07 | ? - 3:00P (3/7) | 50 | 5995 S 030 W | GROUND | SEEPING AIR RELIEF VALVE | PUMPED MH AND REPLACED AIR RELIEF VALVE
IN0062014 | REGION A | LAGRANGE | 2012-05-29 | 12:30P | 100000 | REGION A EFFLUENT | LITTLE ELKHART | SURGE TANK PLUGGED UP | WORK VALVE REGULARLY
IN0021229 | TOWN OF WOLCOTTVILLE | LAGRANGE | 2012-05-15 | 12:30A-7:30A | 182000 | WASTEWASTER TREATMENT PLANT | EFFLUENT PIPE TO RIVER | PIPE WAS CRACKED | THIS IS TREATED WATER THAT IS ON ITS AWAY TO THE DISCHARGE POINT IN TO THE LITTLE ELKHART RIVER
IN0000205 | ARCELOR MITTAL IND HARBOR E | LAKE | 2012-04-06 | (4/7) |  | INTERNAL OUTFALL 701 | TERMINAL LAGOON |  | TREATED BY SAND FILTERS AND DISCHARGED TO INDIANA HARBOR SHIP CANAL THROUGH OUTFALL 011
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2012-01-05 | 2:20P -3:20P |  | 12545 PARRISH AVE | GROUND | BROKEN FORCE MAIN
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2012-05-07 | 2:00A - 10:15A |  | MH 941A, LS 5, MH 1033, MH 395 | GROUND | RAIN 4.5"
| CEDAR LAKE COLLECTION SYSTEM | LAKE | 2012-05-27 | 11:00A - 4:00P |  | LS #11 | GROUND | FORCE MAIN BREAK
| CITY OF HOBART | LAKE | 2012-01-23 | 3:20A-12:18P |  | LIFT STATION #2 | CREEK LEADING | RAIN .91 HEAVY RAIN AND MELTED SNOW | ATTEMPTING TO LOCATE SOURCES OF I & I
| CITY OF HOBART | LAKE | 2012-01-23 | 3:20A-12:18P |  | 3RD & WISCONSIN | LAKE GEORGE | RAIN .91 HEAVY RAIN AND SNOW MELT | ATTEMPTING TO LOCATE SOURCES OF I & I
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-03-23 | 7:40A-8:45P | 13000 | VIKING VILLAGE LIFT STATION | DEEP RIVER | RAIN 2" | UPON SOME INVESTIGATION ON 3/25/12 IT APPEARS THAT THERE MAY BE A HOLE IN THE SANITARY LINE THAT RUNS UNDER THE DITCH. ETC
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-04-21 | 4:10P-4:45P |  | 2434 UNION ST | BASEMENT | MH BACKED UP INTO BASEMENT | CLEANED AND ROOT CUT LINE
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-04-22 | 3:00P-3:34P |  | 3999 PARK AVE | BASEMENT | MH BACKED UP INTO BASEMENT | CLEANED AND ROOT CUT LINE
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-06-12 | 3:10P-3:55P |  | 408 LIVERPOOL RD | BASEMENT | MH IN ALLEY EASEMENT BACKED UP WITH GREASE | CLEANED LINE AND WILL CAMERA
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-06-21 | 2:00P - 9:30A (6/22) | 58500 | TEXAS ST LS | DITCH ALONG I-65 | PUMP ONE HAD BAD START CAPACITOR, PUMP TWO WOULD NOT PRIME | REPLACED START CAPACITOR AND CLEANED VACUUM SYSTEM IN BOTH PUMPS; APPLIED LIME
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-07-18 | 11:05P-1:30A | 7250 | VIKING VILLAGE LIFT STATION WET WELL | DEEP RIVER | POWER FAILURE, RAIN | RENTED GENERATOR
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-07-20 | UNKNOWN-9:40A |  | WET WELL | DEEP RIVER | EQUIPMENT FAILURE PUMP OVERLOADS TRIPPED | APPLIED LIME TO EFFECTED AREA
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-07-24 | 8:45A-9:15A |  | 2507 PARKE ST | BASEMENT | ROOTS | JETTED LINE
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-10-12 | 3:00P-3:20P | 200 | INTERSECTION OF 29TH & NEW JERSEY | STORMWATER MH LEADING TO DEEP RIVER | RAIN; BLOCKAGE | JETTED LINE & NOTICED PEACES OF ROOT & RAGS ON NOZZLE, LINE IS OPEN & FLOWING.
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-10-25 | ? - 11:20A | 100 | MH EAST END OF RIVERDALE | GROUND | GREASE | JETTED LINE
INJ063592 | CITY OF LAKE STATION | LAKE | 2012-12-23 | 5:10P - 6:30P |  | 2710 DECATUR ST. | BASEMENT | GREASE IN MH | CLEANED GREASE OUT OF LINE
IN0039331 | DYER MUNICIPAL STP | LAKE | 2012-01-23 | 12:30A - 11:20P | 1813000 | SECONDARY CLARIFIERS | CHLORINE CONTACT CHAMBER | RAIN .55" | REMIXED WITH TERTIARY TREATED EFFLUENT
IN0039331 | DYER MUNICIPAL STP | LAKE | 2012-05-07 | 1:00A-5:00A | 1447000 | SECONDARY CLARIFIERS BEFORE TERT FILTERS | CHLORINE CONTACT CHAMBER | RAIN 1.63" | BYPASSED FLOW REMIXED WITH TERTIARY TREATED EFFLUENT
IN0039331 | DYER MUNICIPAL STP | LAKE | 2012-08-26 | 10:00P-10:00A | 413000 | SECONDARY CLARIFIERS BEFORE TERT FILTERS | CHLORINE CONTACT CHAMBER | RAIN 1.0
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-01-09 |  |  | 1020 HAMILTON | GROUND | BLOCKAGE IN MAIN LINE | JETTED LINE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-01-09 | 5:45A - 8:45A |  | 9115 OAK & 9317 OAK | GROUND | BLOCKAGE IN MAIN LINE | JETTED LINE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-01-09 | 10:00A - 11:15A |  | 8512 & 8502 MAPLE | BASEMENT | GREASE | JETTED LINE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-01-21 | 7:45A-12:15P |  | #7 DIGESTER | 84 IN DRAIN | FEED VALVE NOT CLOSING IN AUTO | I CLOSED THE FEED VALVE MANUALLY AND MADE ADJ TO THE PUMP TO STOP THE OVERFLOW
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-01-23 | 00:45:00-23:50:00 | 9100000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | RAIN DUE TO A RAIN EVENT AND MELTING SNOW FROM WARM TEMPS WE HAD TO OPEN THE 84" BYPASS GATE 15% TO LOWER THE WEIRS IN THE FINAL CLARIFY DUE TO HI FLOWS GATE WAS CLOSED\ 100% @11:50P EST AMOUNT BYPASS WAS 9.1MG
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-02-03 | 15:15-18:15 | 60 | RESIDENCE @ 885 FLOYD ST | BASEMENT | CONSTRUCTION RELATED SEWER BACKUP INTO A RESIDENTIAL BASEMENT DUE TO A CLOGGED SEWER MAIN | JETTED SEWER MAIN & RESTORED SEWER SERVICE INVEST THE AREA TO DETERMINE IF ADDITIONAL CORRECTIVE ACTION IS NEEDED
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-02-03 | 12:30P - 2:30P |  | 27TH CHASE AIR RELIEF VALVE | GROUND | MALFUNCTION IN AIR RELIEF VALVE CAUSED LEAKAGE IN FORCE MAIN | PUMPS DEACTIVATED TO STOP LEAK; ACTION TAKEN TO REPAIR AIR RELIEF VALVE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-02-08 | ? -10:15A | 5 | 3600 W 3RD AVE | GROUND | RAIN THE LIFT STATION @ OUR DEWATERING BLDG FACILITY OVERFLOWED w/ABOUT 5 GAL OF FOAM ONTO THE GROUND | THE SITE WAS CLEANED UP WE WILL CONTINUE TO MONITOR OUR PUMPS @ THE LIFT STATION
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-02-20 | 7:30A-9:05A |  | 3612 EAST 10TH AVE | BASEMENT AREA | PRIVATE SEWER BACKUP RESULTED FROM A BLOCKAGE FORMED IN THE MAIN SEWER LINE | MAIN SEWER LINE WAS JETTED OUT AND VACTORED OUT TO REMOVE THE BLOCKAGE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-03-14 | 5:10P-6:00P | 50 | 7109 E 1ST AVE GARY IN 46406 | BLDG FLOOR | RAIN PRIVATE SEWER BACKUP RESULTED FROM A BLOCKAGE FORMED IN THE MAIN SEWER LINE | MAIN SEWER LINE WAS CLEANED TO REMOVE BLOCKAGE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-03-23 | 21:10-02:56 | 9000000 | 3600 WEST 3RD AVE | GRAND CALUMET RIVER | RAIN DUE TO A RAIN EVENT & ONLY HAVING 3 OUT OF 5 SCREWS IN SERVICE WE HAD TO OPEN THE 84" BYPASS GATE 10% TO LOWER THE WEIRS | PLANS ARE UNDERWAY TO GET @ LEAST 1 MORE SCREW RUNNING
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-05-07 | 4:10A - 9:10A | 3400000 | FINAL CLARIFIERS | GRAND CALUMET RIVER | RAIN .81" | 84" GATE OPENED 15%
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-05-14 | 2:30P-5:00P | 75 | MH | GROUND | THERE WAS A BLOCKAGE IN THE SEWER LINE | SEWER WAS RODDED/JETTED OUT FROM THE NORTH & SOUTH TO REMOVE THE BLOCKAGE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-05-23 | 10:20A-10:55A | 15 | LIFT STATION/ DEWATERING BLDG | GROUND | FOAMING CONDITION OCCURRED AND IT EXITED THE VAULT AREA ONLY MINIMUM REMNANTS OF SLUDGE PRESENT | INSTALL NEW LEVEL SENSOR & CONTROLLER
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-05-30 | 7:15A-10:30A | 50 | PRIVATE RESIDENCE | BASEMENT | EQUIPMENT FAILURE PRIVATE RESIDENT REPORTED WATER/SEWAGE BACKED UP IN BASEMENT ONTO THE FLOOR | SEWER LINE WAS RODDED OUT & JETTED OUT TO REMOVE BLOCKAGE IN THE LINE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-06-17 | 1:00A -07:15A | 4200000 | 3600 W 3RD AVE | GRAND CALUMET RIVER | RAIN .72" OPENED 84" BYPASS GATE 40%
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-06-18 | 5:20A-5:30A | 50 | PRIVATE RESIDENCE | BASEMENT | RAIN 0.7" | BY THE TIME PERSONNEL ARRIVED @ ADDRESS THE LIQUID LEVEL HAD DECREASED IN THE SEWER. NO ACTION WAS NECESSARY
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-06-30 | 1:30A - 5:40A | 2600000 | PLANT | GRAND CALUMET RIVER | RAIN; OPENED BYPASS GATE 5%
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-07-06 | 12:30P-1:30P | 75 | 4687 DELAWARE | BASEMENT | RAIN 0.70" | BLOCKAGE IN THE MAIN SEWER LINE WAS VACTORED/JETTED OUT AND LINE FREED UP
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-07-07 | 12:45P-1:50P | 200 | 719 W 51ST PL | BASEMENT FLOOR | RAIN 0.1" | SEWER LINE RODDED OUT AND JETTED OUT TO REMOVE BLOCKAGE IN THE LINE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-07-18 | 11:24P-5:30A |  | PRIVATE RESIDENT 767 GRANT ST | BASEMENT | RAIN 1.5 PRIVATE SEWER LINE BACKUP WAS A DIRECT RESULT OF A BLOCKAGE IN MAIN SEWER LINE DUE TO A CAVE IN | REMOVED WATER FROM MH, REPAIR OF MAIN SEWER LINE IN PROGRESS
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-07-20 | 12:15A - 1:10A |  | PLANT | GRAND CALUMET RIVER | POWER FAILURE | CLOSED MAIN GATE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-08-03 | 13:20-14:30 | 25 | RESIDENCE @ 500 N TIPPECANOE | BASEMENT | SEWER BACKUP INTO A RESIDENTIAL BASEMENT DUE TO A CLOGGED SEWER MAIN | JETTED SEWER MAIN & RESTORED SEWER SERVICE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-08-05 | 4:30P-9:15A |  | MH | GROUND | POWER FAILURE | VACTORED OUT WELL TO BRING LIQUID LEVEL DOWN IN THE MAIN SEWER LINE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-08-10 | 7:06P - 9:06P | 30 | 749 RANDOLPH | BASEMENT | CLOGGED SEWER MAIN | JETTED SEWER
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-08-27 | 12:30A - 4:45A | 2900000 | PLANT | GRAND CALUMET RIVER | RAIN OPENED BYPASS GATE 10%
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-09-08 | 12:00A - 1:50A | 1000000 | PLANT | GRAND CALUMET RIVER | RAIN; WISEMAN SCREEN TRIPPED AND DID NOT RESET | OPENED BYPASS GATE 5-10% TO LOWER THE WEIRS TO FINAL CLARIFIERS
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-09-09 | 6:30P-8:30P | 100 | 7029 ASH PLACE | BASEMENT | SEWER BACK UP INTO BASEMENT DUE TO CLOGGED SEWER MAIN | JETTED SEWER MAIN AND RESTORED FLOW
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-09-20 | 4:51P - 5:05P | 75 | MH 2118 WISCONSIN ST | GROUND | SEWER BACK UP | JETTED SEWER MAIN
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-10-20 | ?-8:00 | 150 | NEAR AERATOR 4, 4600 W 3RD AVE | GROUND | MLSS WAS BEING TRANSFERRED FROM AERATOR 6 TO AERATOR 4 VIA PUMP. THE DISCHARGE HOSE DEVELOP A HOLE & MLSS LEAKED ONTO THE GROUND | A VACTOR TRUCK WAS USED TO VACTOR UP MLSS THAT HAD SPILLED ONTO THE GROUND
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-10-24 | 8:45A-10:50A |  | 3600 WEST 3 RD AVE | CONTACT CHAMBER | RAIN, EXPERIENCED MECHANICAL MALFUNCTION ON HYPOCHIORITE FEED PUMP SUPPLY LINE. | CHANGED CHEMICAL FEED PUMP WHILE RUPTURED LINE WAS BEING REPLACED ON UNIT THAT WAS ON LINE
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-10-29 | 11:10A-11:30A |  | 7001 EAST 1ST AVENUE | BASEMENT FLOOR | RAIN; MAIN SEWER BACKUP RESULTING FROM PARTIAL BLOCKAGE DUE TO ROOT INTRUSION. | MAIN SEWER LINE WAS CLEANED, ROOTS REMOVED & LINE TELEVISED.
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-11-01 | 9:30A - 10:15A |  | PLANT | CONTACT CHAMBER | DISCHARGE HOSE PLACED IN EFFLUENT CHAMBER IN #7 TANK BECAUSE OF MISCOMMUNICATION | REROUTED HOSE TO CLARIFIER IN #7 INTERMEDIATE TANK.
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-12-10 | 1300-1630 | 200 | 5851 CYPRESS DRIVE | GROUND | MAIN SEWER LINE WAS IMPACTED WITH A HEAVY GREASY SUBSTANCE. | VACTORED MAIN SEWER LINE &REMOVED GREASY SUBSTANCE.
IN0022977 | GARY SANITARY DISTRICT | LAKE | 2012-12-10 | 1515-1715 | 10 | 5207 EAST 13TH AVE | GROUND | MAIN SEWER LINE CONTAINED A HEAVY GREASY SUBSTANCE. | VACTORED MAIN SEWER LINE & REMOVED GREASY SUBSTANCE.
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-01-23 | 10:00A - 4:15P | 300000 | TERTIARY BUILDING BYPASS VALVE | CHLORINE CONTACT TANK | RAIN .34" HIGH SECONDARY EFFLUENT TURBIDITY AND FLOW RESULTED IN HIGH LEVEL ALARM NECESSITATING BYPASS | FILTER BACKWASH FREQUENCY WAS INCREASED TO RELIEVE SOLIDS LOADS TO FILTERS.
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-02-29 | 2:22A - 9:58A | 6650000 | TERTIARY BUILDING BYPASS VALVE | CHLORINE CONTACT TANK | RAIN .37" HIGH SECONDARY FLOW RESULTED IN HIGH LEVEL ALARM FOR TERTIARY FILTER INFLUENT CHANNEL NECESSITATING PARTIAL BYPASS | FILTER BACKWASH FREQUENCY INCREASED TO RELIEVE LOADING TO FILTERS; BLENDED WITH FINAL EFFLUENT AND TESTED
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-04-16 | 3:20A - 6:20A | 6050000 | TERTIARY BUILDING | GRAND CALUMET RIVER | RAIN .45" OPERATOR DID NOT ANTICIPATE INCREASED FLOW | ADDITIONAL FILTERS WERE WASHED
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-05-04 | 4:45A-11A | 11 | 5143 COLUMBIA AVE | GROUND CALUMET RIVER | POWER FAILURE , RAIN .93 | RETURN TERTIARY FILTERS TO NORMAL OPERATION ASAP
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-05-31 | 10:10P-5:30A | 2940000 | TERTIARY FILTER BYPASS VALVE | GRAND CALUMET RIVER | RAIN 0.64 HIGH SECONDARY FLOW RESULTED IN A HIGH LEVEL ALARM FOR TERTIARY FILTER INFLUENT CHANNEL NECESSARY THE PARTIAL BYPASS OF THE TERTIARY FILTER BLDG | TERTIARY FILTER BACKWASH FREQUENCY INCREASED TO RELIEVE LOADING TO FILTERS
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-06-17 | 2:40A-6:30A | 7900000 | TERTIARY FILTER BYPASS VALVE | GRAND CALUMET RIVER | RAIN .077" HI SECONDARY FLOW RESULTED IN A HI LEVEL ALARM FOR TERTIARY FILTER INFLUENT CHANNEL NECESSITATING THE PARTIAL BYPASS | TERTIARY FILTER BACKWASH FREQUENCY INCREASED TO RELIEVE LOADING TO FILTERS
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-07-19 | 12:30A-6:00A | 10800000 | TERTIARY BLDG BYPASS VALVE | GRAND CALUMET RIVER | POWER FAILURE, RAIN 1.31 HI SECONDARY EFFLUENT FLOW & NUMEROUS ELECTRICAL OUTAGES RESULTED IN A HI LEVEL ALARM FOR THE TERTIARY INFLUENT CHANNEL NECESS THE PARTIAL BYPASS OF THE TERTIARY FILTER BLDG | FILTER BACKWASH FREQUENCY INCREASED TO RELIEVE LOADING TO FILTERS
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-07-19 | 8:12A-11:36A | 6800000 | TERTIARY BLDG BYPASS VALVE | GRAND CALUMET RIVER | POWER FAILURE, RAIN 0.91 HI SECONDARY EFFLUENT FLOW RESULTED IN A HI LEVEL ALARM FOR THE TERTIARY INFLUENT CHANNEL NECESS THE PARTIAL BYPASS OF THE TERTIARY FILTER BLDG | FILTER BACKWASH FREQ INCREASED TO RELIEVE LOADING TO FILTERS
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-07-24 | 7:00A - 10:00A |  | 5143 COLUMBIA AVE | GRAND CALUMET RIVER | POWER FAILURE | REQUEST BETTER RESPONSE FROM NIPSCO. MAXIMIZE FLOW TO PREVENT FLOODING
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-08-10 | 6:55A - 11:15A | 7700000 | TERTIARY BUILDING BYPASS | GRAND CALUMET RIVER | RAIN .57" HIGH FLOW, TURBIDITY, FAILURE OF FILTER #5 ISOLATING VALVE REQUIRED PARTIAL BYPASS OF TERTIARY FILTER BUILDING | FILTER BACKWASH FREQUENCY INCREASED; #5 FILTER OPERATED IN MANUAL
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-08-27 | 12:30A-6:35A | 11200000 | TERTIARY BYPASS VALVE | GRAND CALUMET RIVER | RAIN 1.16 HI SECONDARY EFFLUENT FLOW & TURBIDITY RESULTED IN A HI LEVEL ALARM FOR THE FILTER INFLUENT CHANNEL LEVEL, NECESSITATING THE PARTIAL BYPASS OF THE TERTIARY BLDG | FILTER BACKWASH FREQUENCY INCREASED
IN0023060 | HAMMOND MUNICIPAL STP | LAKE | 2012-12-20 | 3:10P -12:00A (12/21) | 18100000 | TERTIARY BYPASS VALVE | GRAND CALUMET RIVER | HIGH SECONDARY EFFLUENT FLOW AND TURBIDITY RESULTED IN HIGH LEVEL ALARM FOR INFLUENT CHANNEL | FILTER BACK WASH FREQUENCY INCREASED; BLENDED WITH FINAL EFFLUENT AND SAMPLED,
| HIGHLAND SANITARY DISTRICT | LAKE | 2012-07-18 | 10:15-11:15P |  | MH #3005 @ HOMESTEAD JPARK 4693 GAL | STORM SEWER | RAIN 2.69 THE OVERFLOW WAS RECORDRED BY FLOWMETERS LOCATED @ THE RESPECTIVE LOCATIONS. TOTAL RELEASED 92,753 GAL
| HIGHLAND SANITARY DISTRICT | LAKE | 2012-09-11 | 9:00A-9:50A | 20 | SANITARY MH #603 | STORM SEWER, BASIN ON NORTH SIDE | ROOT CLOG | SEWER WAS JETTED & ROOT CUT
IN0061344 | HOBART, CITY OF | LAKE | 2012-09-05 |  |  | 6TH & MAIN ST. | DUCK CREEK | SANITARY SEWER BACK UP | CLEANED SEWER AND INVESTIGATING SOURCE OF I&I
IN0061344 | HOBART, CITY OF | LAKE | 2012-09-24 |  |  | 2779 E. 62ND PLACE | UNNAMED TRIBUTARY | BROKEN SECTION OF SANITARY PIPE ALLOWED INFILTRATION OF SANITARY TO ADJACENT STORM WATER LINE | REHABILITATING SUBDIVISION SANITARY LINES
IN0061344 | HOBART, CITY OF | LAKE | 2012-10-11 | ? - 8:45P |  | MH 704-063 | HIDDEN LAKE | BLOCKAGE IN MAIN SEWER | CLEANED MAIN SEWER
| LAKE DALECARLIA RWD | LAKE | 2012-07-26 | 1:30P |  | 4665 MAIN ST. LOWELL | GROUND | CONTRACTOR DOING EXCAVATION HOT PRESSURE SEWER MAIN | SHUT MAIN. CLEANED AREA. REPAIRED MAIN
INJ035548 | MERRILLVILLE CONSERVANCY DIST. | LAKE | 2012-10-17 | 3:00P - 3:20P | 100 | 6250 BROADWAY MH 628 | TURKEY CREEK | LINE BLOCKAGE | HIGH PRESSURE JETTING TO CLEAN LINE
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2012-01-13 | 9:44A-12:00P | 500 | 406 YORK RD | BASEMENT | EQUIPMENT FAILURE BASEMENT BACK-UP SEWER LINE ON YORK PLUGGED | WE JETTED SEWER LINE ON YORK ROAD
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2012-01-22 | 4:40P-6:00P |  | 137 NAPLES CT | BASEMENT | BASEMENT BACK-UP SEWER LINE ON NAPLES DR WAS PLUGGED | JETTED WESTBOUND INSIDE MANHOLE @ 2525 DR & ALSO JETTED N FOR 100 FT @ SAME MH
IN0024457 | SCHERERVILLE MUNICIPAL STP | LAKE | 2012-01-27 | 7:00P-8:30P |  | 2701 HUGEL HILL | BASEMENT | EQUIPMENT FAILURE | WE RODDED SEWER LINE ON SPRINGHILL FROM 2532 SPRINGHILL TO 401 YORK ROAD
IN0000221 | STATE LINE ENERGY, LLC | LAKE | 2012-02-10 | 4:00A - 1:00P | 423000 | 103RD ST. & LAKE MICHIGAN | SHEET FLOW TO GROUND AND DRAIN TO COAL PILE RUNOFF | INTERNAL SCREEN FAILURE IN #3 DEWATERING BIN PLUGGED INLET LINES TO CLARIFIERS | REMOVE BOTTOM ASH SOLIDS FROM SETTLING CLARIFIER AND UNPLUG INLET LINES
IN0000221 | STATE LINE ENERGY, LLC | LAKE | 2012-02-13 | 9:30A - 11:30A | 180000 | 103RD ST. & LAKE MICHIGAN | SHEET FLOW TO GROUND AND DRAIN TO COAL PILE RUNOFF | INLET TO "A" CLARIFIER STILL PLUGGED WITH SOLIDS | WILL WATER JET INLET LINES
IN0058343 | TOWN OF WINFIELD | LAKE | 2012-05-07 | (5/8) |  | 10528 ERIE DR. SEWER MAIN | GROUND | GRAVITY SEWER MAIN LEAK CAUSED BY CONSTRUCTION | SNAKED SEWER MAIN TO OPEN LINE
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2012-04-03 | 12:40?-13:24? | 40 | MANHOLE 21 | GROUND | PARTIAL OBSTRUCTION IN SEWER MAIN RESTRICTING NORMAL SEWER FLOW | CREW IN ROUTE TO JET OUT SEWER MAIN. LIME WILL BE APPLIED TO THE GROUND AROUND THE MANHOLE
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2012-04-23 | 7:30A-8:10A | 2000 | WASTEWATER TREATMENT PLANT | GROUND | FOUND RAGS IN NORTH A/B DISCHARGE PIPING | APPLIED LIME TO AREA REMOVING RAGS FROM NORTH BASINS
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2012-05-07 | 6:45A-7:15A | 100 | 1822 SANDY BEACH DR SEWER MAIN BACKUP | BASEMENT | RAIN 2.75 LIFT STATION "F" WAS @ HIGH LEVEL | AN ADDITIONAL PUMP WAS SETUP @ THE LIFT STATION
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2012-05-07 | ?-9:30A | 50 | 2155 GREEN VALLEY DR SEWER MAIN BACKUP | BASEMENT | RAIN 2.75 | AN ADDITIONAL PUMP WAS SETUP @ THE LIFT STATION F
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2012-05-07 | 2:30A-9:30A | 100 | 1254 BRANDYWINE SEWER MAIN BACKUP | SHOWER DRAIN | RAIN 2.75 | AN ADDITIONAL PUMP WAS SETUP @ THE LIFT STATION F
IN0037176 | TWIN LAKES UTILITIES | LAKE | 2012-05-07 |  |  | 2153 AND 2156 SEWER MAIN BACKUP | BASEMENT FLOOR DRAINS | RAIN 2.75 | AN ADDITIONAL PUMP WAS SETUP AT LIFT STATION "F"
IN0031127 | WINFIELD ELEM. WWTP | LAKE | 2012-10-23 | 12:30P-1:30P |  | M H PRIOR TO WWTP | GROUND NEXT TO WWTP | PLUGGED SEWER MAIN | CLEANED LINE & REMOVED OBSTRUCTION
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2012-07-06 | 1500-2100 | 20000 | 22 & M ST LIFT STATION | LEATHERWOOD CREEK | POWER FAILURE. STORM RELATED DAMAGE TO COMMERCIAL POWER TO LIFT STATION | REPAIRED STATION
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2012-08-16 | 2300-1200 | 50000 | LIFT STATION 004 | LEATHERWOOD CREEK | POWER FAILURE, RAIN 1.41 STORM BLEW A TREE DOWN ON POWER LINE TO LIFT STATION POWER OUT TILL DUKE ENERGY COULD MAKE REPAIRS | WE WILL CLEAN UP ANY DEBRIS FROM DISCHARGE
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2012-08-19 |  | 5000 | BACKWASH STORAGE TANK 001A | UNNAMED DITCH TO EAST FORK WHITE RIVER | WHILE BACK WASHING SAND FILTERS OPERATORS OVERFLOWED THE TANK | WE WILL MONITOR THE AREA & CLEAN UP AREA AS NECESSARY
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2012-09-28 | 1515-1630 | 20000 | SPIDER CREEK L S 007 | SPIDER CREEK | CAP ON DISCHARGE LINE CHECK VALVE CAME OFF | CREW RESPONDED TO ALARM & MADE REPAIRS; PUT STATION BACK IN SERVICE
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2012-10-23 | 1500-1600 | 5000 | RILEY BLVD L S 002 | BAILY BRANCH OF PLEASANT RUN CREEK | SEWER MAIN GOING INTO STATION STOPPED UP CAUSING SHORT TERM OVERFLOW LINE OPENED, & FLOW RESTORED | LINE OPENED, & FLOW RESTORED
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2012-12-20 | 7:00A - 12:30P | 200000 | SPIDER CREEK LS #007 | SPIDER CREEK | RAIN .64" PUMPS KNOCKED OUT BY ELECTRICAL PROBLEMS | REPAIRS MADE AND ONE PUMP WORKING
IN0025623 | BEDFORD MUNICIPAL STP | LAWRENCE | 2012-12-21 | 0830-1130 |  | SPIDER CREEK LS 007 | SPIDER CREEK | THE REPLACEMENT PUMP WE PUT IN THE DAY BEFORE FAILED THEN THE OTHER PUMP KICKED OUT ALLOWING OVERFLOW | BOTH PUMPS WERE PULLED AND REPAIRS PERFORMED STATION BACK ON LINE
IN0024953 | HARDIN RIDGE RED AREA WWTP | LAWRENCE | 2012-05-07 | 0800-0900 | 5000 | LIFT STATION AND AERATION TANKS AT PLANT LOCATION | PLANT GROUNDS | RAIN | WILL CLEAN UP AROUND PLANT WHERE WATER WENT
IN0030236 | SPRING MILL STATE PARK | LAWRENCE | 2012-12-05 | 10:10A - 10:10A | 25 | LIFT STATION | GROUND | AIR LOCK IN FORCE MAIN | REMOVED AIR AND RESUMED PUMPING
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2012-01-12 |  | 1000 | 511 W. WASHINGTON ST | BASEMENT | CLOGGED SEWER | JETTED LINE
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2012-02-28 | 11:00A-1:00P | 100 | CLEAN OUT IN ALLEY BEHIND 609 W WASHINGTON | GROUND | SEWER OBSTRUCTED WITH ROOTS BEHIND 609 W WASHINGTON ST | JETTED LINE WITH VAC-TRUCK
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2012-03-07 |  | 100000 | SEWER LINE | BILLS CREEK | CLEANED 10" LINE @ 11TH ST RD 9 FOUND TWO HOLES IN THE LINE CREEK WATER IS FLOWING INTO THE 10" SEWER LINE | MEETING WITH CONTRACTOR @ 12:00 P 3/7/12 TO RESOLVE THE PROBLEM
IN0020044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2012-04-05 |  |  | PLANT | GROUND | SCRAPPER ARM ON WEST CLARIFIER SHEARED PIN. | DRAINING CLARIFIER TO FIND PROBLEM
IN002044 | ALEXANDRIA MUNICIPAL STP | MADISON | 2012-07-09 |  | 50 | 414 N WALNUT | BASEMENT | CITY SEWER LINE OBSTRUCTED. JETTED AND CLEANED LINE | JETTED AND CLEANED LINE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-11 | 4:00P - 6:07P | 779000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .48" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-13 | 0445A-0730A | 1200 | #15 CHANNEL INTO # 16CHANNEL | CONTACT TANK | POWER FAILURE CITY LOST A POWER GRID FOR APPROX 2.5 HR | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-13 | 0610-0615 | 40000 | PRIMARY CLARIFIERS | WHITE RIVER | POWER FAILURE | ONCE POWER WAS RESTORED THE OPERATOR RESET ALL PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-17 | 12:45A-1:15A |  | PRIMARY CLARIFIERS | WHITE RIVER | POWER FAILURE, FAILED TO MAXIMIZE FLOW | NEW LIFT STATION PUMPS WERE TAKE OUT OF AUTO MODE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-18 | 0650-0735 | 19300 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.08 RAIN EVENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-22 | 11:23P - 5:25P (1/24) | 26400000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .88" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-23 | (2/7) |  | #1 AERATION BASIN | #2 AERATION BASIN | NEW HEADS ON DIFFUSERS TO BE INSTALLED | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-25 |  |  | MH | STREET | BLOCKAGE | RESTORED FLOW AND CLEANED AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-26 | 4:35A - 4:20A (1/28) | 30000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .8" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-01-30 | 1500-1500 |  | PRIMARY CLARIFIER #2 | CLARIFIERS 1,2,3 | PRIMARY CLARIFIER TAKEN OUT OF SERV & DRAINED SO MAINT STAFF CAN REPAIR CHAIN FOR SHORT FLIGHTS. OUR FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-02-07 | 8:00A - 2:00 (2/25) |  | OLD SYSTEMN AERATION BASIN #1 | OS AERATION BASIN #2 | REPLACING AIR DIFFUSERS IN OS #1 | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-02-27 | 8:00A - 3:00P (3/2) |  | CEMENTECH SLUDGE AUGER |  | SLUDGE AUGER STOPPED | WILL REPAIR; NO RELEASE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-02-29 | 0340-0855 | 4600000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .58"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-02 |  | 9800000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .73"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-02 | 12:30P-1:15P | 1000000 | RAW WET WELLS | WHITE RIVER | POWER FAILURE, RAIN .75" FAILURE TO MAXIMIZE 1st EVENT-OPERATOR DID NOT HAVE SELECTOR SWITCH IN AUTO FOR OLD RAW PUMP | 2ND EVENT NEW LIFT STATION PUMP 3 FAULTED OPERATOR WAS DOING MAINT ETC
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-08 | 9:00A - 3:00P (3/22) |  | STAND BY GENERATOR #1 |  | BAD BREAKER ON SWITCH GEAR | NEW BREAKER ORDERED AND WILL BE INSTALLED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-08 | 0840-1650 | 7.7 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .73"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-09 | 0800-1500 |  | PRIMARY CLARIFIER # 3 | CLARIFIERS 1,2,4 | EQUIPMENT FAILURE TOOK PRIMARY CLARIFIER #3 OUT OF SERVICE TO REPAIR SHORT FLIGHTS AND CONDUCT PREVENTATIVE MAINT ON LONG FIGHTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-15 | 0800-1500 |  | NO RELEASE |  | GRIT AUGER #2 @ PRIMARY PLANT IS BROKEN | MAINTENANCE PERSONNEL ALONG WITH MK BETTS WILL REPLACE BROKEN ANGER W/A NEW ANGER
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-15 | 14:00-15:00 |  | WASTING TANK # 3 | AERATION BASINS | # 3 WASTING TANK MOTOR WENT BAD | NEW MOTOR HAS BEEN ORDERED AND WILL BE INSTALLED UPON ITS ARRIVAL BY ELECTRICAL AND MAINT STAFF
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-20 | 8:00A - 3:00 (3/22) |  | PRIMARY CLARIFIER #4 | CLARIFIERS 1,2,3 | #4 TAKEN OUT OF SERVICE TO STRAIGHTEN LONG FLIGHTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-23 | 2315-2220 | 15600000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .37"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-23 | 12:59P-9:12P | 10000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.62"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-24 | 5:00P - 3:00P (3/31) |  | NEW RAW WET WELL LS | OLD RAW WET WELL | GRINDER #2 WENT DOWN AT NEW RAW LS. #3 OUT FOR SERVICE. | DIVERTED FLOW TO OLD RAW LS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-27 | 16:00-15:00 |  | PRIMARY CLARIFIER # 3 | CLARIFIER'S 1,2,3 | TOOK PRIMARY CLARIFIER # 3 OUT OF SERVICE TO DETERMINED WHY SHORT FLIGHTS AREN'T TURNING OUR FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-03-30 | 0605-0740 | 970000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .25"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-08 | 4:00P - 3:00P (4/20) |  | PRIMARY CLARIFIER | CLARIFIER 2,3,4 | INSPECTING SHORT FLIGHTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-14 | 14:15-17:43 | 460000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .67"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-16 | 06:20-10:25 | 3800000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .41"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-16 | (4/27) |  | WEST OS AERATION BASIN | EAST AERATION BASIN | REPLACING DIFFUSER CAPS | FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-18 | 3:00P -3:00P (4/20) |  | SCREW PUMP #2 |  | REPAIRING MOTOR DRIVE BELT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-25 | 9:47P - 10:30P | 56000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .19" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-27 | 12:51P-2:15P | 50 | CATCH BASIN | STREET | EQUIPMENT FAILURE SEWER FULL OF CUPS AND STICKS | BYPASS PUMP VAL UP AREA OF OVERFLOW RESTORE FLOW
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-28 | 11:42-12:45 | 408000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .21"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-04-30 | 18:45-23:40 | 14200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .58"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-01 | 14:17-18:00 | 10300000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.32"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-02 | 1:05P-1:30P | 500 | MH 2800 W 18TH | STREET | GREASE BLOCKAGE | JETTED TO RESTORE FLOW BY PASS PUMP SWEEP UP AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-02 | 10:00A - 3:00P |  | PRIMARY CLARIFER #3 | CLARIFERS 1, 2, 4 | #3 TAKEN OUT OF SERVICE TO STRIGHTEN LONG FLIGHTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-04 | 9:44P-2:34A | 2300000 | PRIMARY CLARIFIERS | WHITE RIVER | POWER FAILURE, RAIN .77"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-06 | 16:00-15:00 |  | PRIMARY CLARIFIER # 2 | CLARIFIERS 1,3,4 | EQUIPMENT FAILURE PRIMARY CLARIFIER # 2 TAKEN OUT OF SERVICE TO STRAIGHTEN AND REPAIR LONG FLIGHTS. OUR FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-07 | 0842-0912 | 3100000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .94"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-09 | 5/23 |  | TEN DAY NOTICE |  | STAFF INSTALLING NEW VFD DRIVE UNIT | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-14 |  |  | NO RELEASE | 10 DAY NOTICE | PRIMARY EFFLUENT METER 49 SEAMS TO BE LAGGING PARTIAL FLUME FLOW ON NORMAL FLOW DAY IT'S ABOUT 2 MGD SHORT | ELECTRICIANS THINK TRANSDUCERS NEED BE REPLACED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-16 | 0900-1500 |  | CEMENT TECH |  | CEMENT TECH CAKE MIXER BROKEN AUGER | MK BETTS ENGINEERING ON SITE TO REPAIR AUGER FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-25 | 1834-2219 | 4800000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .67"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-29 | (6/5) |  | SECONDARY PLANT GRIT SWEEP | OLD SYSTEM PLANT CLARIFIERS | GRIT SWEEP WILL BE TAKEN OUT OF SERVICE TO REPAIR SWING ARMS | FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-05-29 | 0612-1025 | 5600000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .63"
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-07 | 7:35A - 8:30A | 1000 | 8" SLUDGE LINE | GROUND | LINE HIT DURING CONSTRUCTION | SHUT VALVE AND DIVERTED FLOW; CLEANED AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-07 |  |  | NO RELEASE CEMENT TECH MIXER |  | CEMENT TECH CONVEYOR TRACK BROKE | MK BETTS ON SITE TO REPAIR BROKEN TRACK FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-14 | 14:00-? |  | 2 WEST OS PRIMARY | #1 EAST PRIMARY CLARIFIER | LOST WEAR STRIPS THAT CAUSED SOME FLIGHT DAMAGE | WE WILL CHANGE OUT DAMAGED FLIGHTS AND REPLACE WEAR STRIPS ALSO WE WILL DO ANNUAL PM'S
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-19 | 0700-1500 (7/10) |  | BIG BLOWER/SECONDARY PLANT | N/A | BIG BLOWER @ SECONDARY PLANT MAIN PLANT WILL BE OUT OF SERVICE TO INSTALL VFD DRIVE UNIT. 10 DAY NOTICE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-28 | 8:15A - PM (7/6) |  | #1 EAST PRIMARY CLARIFIERS | WEST OS PRIMARY CLARIFIERS | LOST WEAR STRIPS | PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-29 | 4:20P - 8:08P | 5200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .91" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-29 |  |  | 72" SECONDARY FEED LINE | CONSTRUCTION HOLE | GROUND SHIFT DURING CONSTRUCTION CAUSED LEAK IN JOINT | LEAK CONTAINED AND WILL BE PUMPED DOWN; FINAL EFFLUENT NOT AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-29 | 4:30P - 5:30P | 500000 | RAW WET WELL | WHITE RIVER | LEVEL SENSOR FAILURE. FAILURE TO MAXIMIZE. | SWITCHED LEVEL SENSORS AND IMMEDIATELY MAXIMIZED.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-06-30 | 5:40A - 8:15A | 3700000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .58" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-06 | 6:25A - 6:53A | 200000 | PRIMARY CLARIFIERS | WHITE RIVER | POWER FAILURE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-13 | 1830-1500 (7/16) |  | NO RELEASE METER 49 EFFLUENT TO AERATION | WHITE RIVER | METER 49 EFFLUENT TO AERATION STOPPED READING DUE TO LOSS OF SIGNAL | ELECTRICIANS WERE CALLED IN TO ASSESS THE SITUATION AND DETERMINED WHY THE METER LOST SIGNAL
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-14 | 10:40P-12:42A | 1500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.13" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-16 | 10:15A-10:45A | 500 | MH AT 6542 PARK RD | DITCH | EQUIPMENT FAILURE AFTER PUMPING MH DOWN WE DISCOVERED ETC | SHUT OFF VALE BYPASS PUMP VAC DITCH SPREAD LIME
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-16 | 2:00P-10:30A | 10000 | #14 CSO INDIANA AVE | WHITE RIVER | 14 HAS BEEN GOING OFF AND ON SINCE 7/16/12. WHEN WE WENT TO CHANGE OUT PART OF THE THROTTLE PIPE WE FOUND THAT IT WAS GOING | VAC TRUCK NOW KEEPING UP WITH THE FLOW. FLUID WASTE ALSO ON SITE. SEWER CLEANING HAS BEEN GOING ON IN THE AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-19 | 11:08A-2:30P | 8700000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .77 RAIN EVENT
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-25 | 9:00A-? |  | NEW RAW SEWAGE LIFT STATION | OLD RAW SEWAGE LIFT STATION | COMPUTER PRG ISSUE CAUSED THE LIFT STATION TO SHEET DOWN THEN NOT FUNCTION PROPERTY | WE DECIDED TO RUN OUR OLD LIFT STATION UNTIL PRG COULD GET ON SITE TO FIX THE PROBLEM ETC
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-27 | 3:33P-7:55P | 5200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .96
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-27 | 2:00P-2:35P | 1000 | SEWER | POND | SEWER CLOGGED W/ TOWELS TAP LEAKING | BYPASS PUMP JET TO RESTORE FLOW HAVE TAP REPAIRED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-07-30 | 1600-1500 |  | PRIMARY CLARIFIER # 2 | CLARIFIERS 1,3,4 | PRIMARY CLARIFIER #2 TAKEN OUT OF SERVICE TO STRAIGHTEN AND REPAIR CRACKED LONG FLIGHTS OUT FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-04 | 7:40A-7:43A | 3000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .05" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-06 | 1500-1500 (8/10) |  | PRIMARY CLARIFIER # 3 | CLARIFIERS 1,2,4 | PRIMARY CLARIFIER # 3 TAKEN OUT OF SERVICE TO REPLACE DRIVE CHAIN & STRAIGHTEN LONG FLIGHTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-07 | 2127-2200 | 2000 | EFFLUENT BYPASS CHANNEL | WHITE RIVER | BLEW A FUSE ON CONTROL TRANSFORMER WHICH CONTROL EFFLUENT PUMP | ELECTRICIANS CAME IN & REPLACED FUSE & FLOW WAS RESTORED TO NORMAL
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-08 | 0800-1500 |  | PRIMARY CLARIFIER # 4 | CLARIFIERS 1,2,3 | PRIMARY CLARIFIER # 4 TAKEN OUT OF SERVICE TO INSPECT GEARS & STRAIGHTEN LONG FLIGHTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-09 | 0113-0314 | 24000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 2.29 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-16 | 1800-2320 | 7000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .70 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-21 | 0700-1500 (8/24) |  | FINAL CLARIFIER # 5 | CLARIFIERS # 3,4,6 | FINAL CLARIFIER #5 TAKEN OUT OF SERVICE FOR ANNUAL PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-23 | 0800-2100 |  | FINAL CLARIFIER # 6 | CLARIFIERS # 3,4,5 | EQUIPMENT FAILURE # 6 TAKEN OUT OF SERVICE FOR ANNUAL PREVENTATIVE MAINTENANCE
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-27 | 1009-1120? | 1100000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .34 | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OUR OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-28 | 0900-1500 |  | FINAL CLARIFIER # 4 | FINAL CLARIFIERS 3,5,6 | EQUIPMENT FAILURE FINAL CLARIFIER # 4 TAKEN OUT OF SERVICE FOR ANNUAL PREVENTATIVE MAINTENANCE.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-29 | 11:30A - 11:45A | 1000 | SOUTH BIO TOWER | GROUND | PUMPS 6 AND 7 KICKED OUT WHILE IN SERIES MODE | RESET PUMPS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-08-30 | 7:30A-? PM |  | #3 SECONDARY CLARIFIER | # 4-5-6 CLARIFIERS | EQUIPMENT FAILURE ANNUAL PM'S | CONTINUED PM'S
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-02 | 1704-2149 | 7200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.49 | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OUR OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-04 | 1740-2030 | 2900000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .68 | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OUR OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-04 |  |  | #1 OS SECONDARY CLARIFIER | #2 OS SECONDARY CLARIFIER | FOUND LEAK IN CENTER WELL SEAL | TAKE CLARIFIER DOWN FOR REPAIR
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-06 | 2118-2325 | 1800000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .34" | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OUR OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-07 | 1:36P-7:26P | 4500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.2" | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OUR OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-07 | 2045-1505 | 17400000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 2.5 | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OUR OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-12 | 1500-1500 (9/18) |  | PRIMARY CLARIFIER # 4 | CLARIFIERS 1,2,3 | PRIMARY # 4 TAKEN OUT OF SERVICE TO REPLACE DRIVE GEAR AND INSPECT FLIGHTS
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-15 |  | 100 | 1021 N 300 B MH | DITCH | POWER FAILURE | VACUUMED AREA AND SPREAD LIME
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-17 | 9:30-4:00A | 5500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .59" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-18 | 0830-1500 |  | NEW RAW LS | OLD RAW LS | NEW LS WILL BE DOWN TO VAC OUT DEBRIS IN CHANNEL | GRIT HAS SETTLED. EFFLUENT NOT AFFECTED.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-19 | 12:30P-? |  | NO RELEASE CEMENT TECH MIXER |  | CEMENT TECH MIXER CONVEYOR TRACK BROKE | MK BETTS ENGINEERING ON SITE TO MAKE REPAIRS. FINAL EFFLUENT WILL NOT BE AFFECTED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-20 | 2:00P - 8:00A (9/25) |  | NO RELEASE | WHITE RIVER | SLC PROCESSOR SHORTED AND LOST POWER | REPLACED WITH BACK PROCESSOR AND POWER SUPPLY
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-21 | 2037-0135 (9/22) | 4000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .67 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-24 | 1000-1500 |  | PRIMARY CLARIFIER # 1 | CLARIFIERS 2, 3, 4 | PRIMARY CLARIFIER # 1 TAKEN OUT OF SERVICE TO REPAIR DRIVE GEAR FOR SHORT FLIGHTS.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-09-27 | 10/11 |  | MAIN BREAKER @ PRIMARY PLANT | WHITE RIVER | 10 DAY NOTICE; EATON ELECTRIC WILL BE TESTING THE INTERLOCKING ZONE FOR THE MAIN BREAKERS @ OUR PRIMARY PLANT. | POWER WILL BE TRANSFERRED FROM 1 BREAKER TO THE OTHER.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-01 | 2205-2220 | 2600000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .60" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-04 | 12:27P-1:06P | 13000 | 028 CHESTERFIELD L S | WHITE RIVER | POWER FAILURE, EQUIPMENT FAILURE FAILED UPS INSIDE CHESTERFIELD DRIVE PANEL. | ELECTRICIANS HARD WIRED PUMPS AROUND PANEL BY PASS WAS STOPPED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-04 | 1600-1610 | 40 | NEW SYSTEM RETURN PIT MH | GROUND | DUE TO A POWER FAILURE @ OUR SECONDARY TREATMENT PLANT THE RETURN PUMPS STOPPED WHICH CAUSED THE FLOW TO BACK UP AND OUT OF THE MH | THE AFFECTED AREA WAS VACUUMED & LIME WAS APPLIED
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-05 | 12:28P - 4:15A (10/6) | 14100000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.38" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-14 | 2030-2351 | 4000000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .37 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-17 | 6:48P-10:30P | 4300000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .33 RAIN EVENT | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-18 | 6:18A-9:55A | 3500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .34 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-19 | 3:30P-6:14P | 2800 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .38 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-23 | 1047-2040 | 11200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.44 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-30 | 1304-1335 | 278000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .43" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-10-31 | 0800-1500 |  | METER 49 EFFLUENT TO AERATION | NO RELEASE | METER 49 EFFLUENT TO AERATION STOPPED READING DUE TO CONNECTION ISSUES. | ELECTRICIANS ARE ON SITE TO EVALUATE & DIAGNOSE PROBLEM
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-11-01 | 9:00A-15:00 |  | CEMENT TECH MIXER |  | CEMENT TECH MIXER NEEDED HYDRAULIC VALVE REPLACED. | MAINTENANCE IS REPLACING VALVE. FINAL EFFLUENT WILL NOT BE AFFECTED.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-11-02 | 10:00A - 11:30A | 200 | OLD CLARIFIER #2 | GROUND | DIGGERS HIT OLD CONDUIT WHICH WENT TO OLD CLARIFIER #2 | CAPPED LINE. PUMPED DITCH AND LIMED AREA
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-11-05 | 1:30P - 3:30P | 300 | NON-POTABLE PLANT WATER SUPPLY LINE | EXCAVATION HOLE | DIGGERS HIT WATER SUPPLY LINE | WILL REPAIR LINE. FINAL EFFLUENT NOT AFFECTED.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-11-12 | 0351-1230 | 8700000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN 1.10" | FLOW WAS BEING MAXIMIZED IN CONJUNCTION WITH OUR OPERATIONAL PLAN.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-11-21 | 12/10 |  | OLD RAW WET WELL | PRIMARY GRIT TANKS | TEN DAY NOTICE. TIE IN OF NEW WET WEATHER PUMP STATION TO EXISTING RAW LINE | WILL BE DONE ON DRY DAY WITH STAND BY PUMPING.
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-12-04 | 1:32P - 3:50P | 1800000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .42" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-12-07 | 5:27P-9:16P | 1200000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .54 | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-12-09 | 1152-1530 | 8500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .66" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-12-20 | 8:54A - 1:30P | 5500000 | PRIMARY CLARIFIERS | WHITE RIVER | RAIN .5" | FLOW BEING MAXIMIZED IN CONJUNCTION WITH REVISED OPERATIONAL PLAN
IN0032476 | ANDERSON MUNICIPAL STP | MADISON | 2012-12-26 | 4:40P - 5:00P | 500 | MH | STREET | DEBRIS IN LINE | BYPASSED PUMPED, VAC AREA AND RESTORED PLOW
INM022560 | CHESTERFIELD MUNICIPAL STP | MADISON | 2012-01-17 | 7:45A-9:45A | 132000 | CSO 028 | WHITE RIVER | RAIN 1" ANDERSON WASTEWATER HAD A PUMP FAILURE @ LIFT STATION | PUMP WAS REPAIRED BY ANDERSON WASTEWATER
INM022560 | CHESTERFIELD MUNICIPAL STP | MADISON | 2012-05-01 | 6:10P-7:20P | 75000 | CSO 028 | WHITE RIVER | EQUIP FAILURE, RAIN 1.32 ANDERSON WASTE WATER HAD A PUMP FAILURE AT THERE LIFT STATION. | PUMP WAS REPAIRED BY ANDERSON
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-01 |  | 1700000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATIONS AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. BLENDED WITH FINAL EFFLUENT AND SAMPLED.
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-02 |  | 1010000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATIONS AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. BLENDED WITH FINAL EFFLUENT AND SAMPLED.
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-03 |  | 995000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATIONS AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. BLENDED WITH FINAL EFFLUENT AND SAMPLED.
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-04 |  | 645000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATIONS AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. BLENDED WITH FINAL EFFLUENT AND SAMPLED.
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-05 |  | 164000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATIONS AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. BLENDED WITH FINAL EFFLUENT AND SAMPLED.
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-17 | 7:00A | 5260000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN .97" DISCHARGE WAS NOT DISINFECTED. NO OTHER DAMAGE DONE | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-18 | 12:01A-10:00A | 4340000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-19 | 12:01A- | 3250000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN. TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE | OPERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXIMIZE CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-20 |  | 2330000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-21 |  | 1420000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-22 |  | 3204000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-23 | 12:01A-? | 4880000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN .27" TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE | OPER STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSS. TO MAXI CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-24 |  | 3450000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-25 |  | 3250000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-26 |  | 5260000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-27 | 12:07A-? | 4430000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-28 | 12:01A-? | 3730000 | EQ BASIN/OUTFALL # 101 | BIG DUCK CREEK | RAIN.06 | TURNED OF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-29 |  | 3000000 | EQ BASIN/OUTFALL # 101 | BIG DUCK CREEK | RAIN .01 | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-01-31 | 12:01A-? | 1943000 | EQ BASIN/OUTFALL # 101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXI CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-01 | 12:01A-? | 1347000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK |  | TURNED OFF AERATION AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPERATIONAL STRATEGY FOR EQ IS TO KEEP BASIN EMPTY ASAP TO MAXI CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-02 | 12:01A-? | 8340000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK |  | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-02 | 12:01A-? | 830000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXI CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-04 | 12:01A- | 1620000 | EQ BASIN/OUTFALL # 101 | BIG DUCK CREEK | RAIN 0.28 TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXIMIZE CAPTURE DURING WET WEATHER | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPRERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXIMIZE CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-05 | 12:01A- | 740000 | EQ BASIN/OUTFALL # 101 | BIG DUCK CREEK | RAIN .02 | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPRERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXIMIZE CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-07 | 12:01A- | 400000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE OPERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXIMIZE CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-08 | 12:01A-11:00P | 440000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPRERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXIMIZE CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-08 | 12:01A- | 700000 | EQ BASIN/OUTFALL # 101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE. OPERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXI CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-02-16 | 10:00P-? | 710000 | EQ BASIN/OUTFALL # 101 | BIG DUCK CREEK | RAIN .24 | TURNED OFF AERATION AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE /OPERATIONAL STRATEGY FOR EQ BASIN IS TO KEEP BASIN EMPTY AS POSSIBLE TO MAXI CAPTURE DURING WET WEATHER
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-03-25 |  | 1196000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-03-26 |  | 930000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION AND MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-03-27 |  | 2930000 | EQ BASIN/OUTFALL #101 | BIG DUCK CREEK | RAIN | TURNED OFF AERATION & MIXING TO EQ CELL THAT OVERFLOWED TO ALLOW CONTENTS TO SETTLE
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-08-22 | ?-12:00P | 1000 | CSO # 125 | LITTLE DUCK CREEK | VISUAL INSPECTION REVEALED SIGNS OF INTERMITTENT TRICKLE OVER LAST SEVERAL DAYS | CLEANED SEWERS UPSTREAM & DOWNSTREAM CSO
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-13 | 8:00A - | 1800000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-14 | 12:00A - | 1700000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-15 | 12:00A - | 1700000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-16 | 12:00A - | 1700000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-17 | 12:00A - | 2000000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-18 | 12:00A - | 2000000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-19 | 12:00A - | 2400000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-20 | 12:00A - | 2000000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-21 | 12:00A - | 2500000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-22 | 12:00A - | 2400000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-22 | 8:15A - 6:15P | 820000 | CSO 14 AT LS | LITTLE DUCK CREEK | RAIN .77" LS PUMP FAILED; BACK UP PUMP WAS BEING REPAIRED | RENTED EMERGENCY PUMP; REPAIRING PUMP
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-23 | 12:00A - | 2600000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-24 | 12:00A - | 2400000 | SECONDARY CLARIFIER EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | BYPASSING TERTIARY; WILL REPLACE PUMP; WILL MEET LIMITS
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-25 | 12:01A - 1:00P | 1000000 | SECONDARY EFFLUENT | CHLORINE DISINFECTION TANK | TERTIARY FILTER SPENT BACKWASH WATER PUMP FAILED | REPLACED PUMP
IN0032719 | ELWOOD MUNICIPAL STP | MADISON | 2012-09-26 | 9:00A - 2:00P | 1000 | MH | GROUND | RAIN .48" CLOG IN SEWER DOWNSTREAM FROM MH | CLEANED SEWER
IN0049026 | FALL CREEK RSD STP | MADISON | 2012-06-29 | 3:33P - 6:07P |  | PLANT EFFLUENT | STREAM | PRIMARY AND BACK UP POWER SOURCES OFF DUE TO STORM | NO UV DISINFECTION DURING THIS TIME
IN0049026 | FALL CREEK RSD STP | MADISON | 2012-07-13 | ?-7:00A |  | REFORMATORY LIFT STATION | AREA AROUND THE OVERFLOW | EQUIPMENT FAILURE HORNER ELEC HAS BEEN WORKING ON CONTROL PANEL SINCE FRI & STILL WORKING ON IT | ADD BACK UP HI LEVEL FLOORS
IN0049026 | FALL CREEK RSD STP | MADISON | 2012-07-31 | ?-7:00A |  | REFORMATORY LIFT STATION | AREA AROUND THE OVER BASIN | HORNER ELEC HAS BEEN WORKING ON CONTROL PANEL SINCE FRI AND IS STILL WORKING ON IT | ADD BACK UP HI LEVEL FLOATS
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2012-01-17 | 7:00A-6:00P |  | SSO 003 | PIPE CREEK | RAIN 4.0
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2012-05-01 | 4:00P-? |  | SSO 003 | PIPE CREEK | RAIN 2"
IN0020028 | FRANKTON MUNICIPAL STP | MADISON | 2012-09-08 | 1:00A-9:00A |  | SSO 003 & OVERFLOW POINT NORTH OF 308 N JOHN ST | PIPE CREEK | RAIN 2.5"
INM022560 | TOWN OF CHESTERFIELD | MADISON | 2012-09-07 | 9:30P-1:43A | 200000 | CSO 028 | WHITE RIVER | RAIN 3.50 ANDERSON WASTEWATER TREATMENT HAD A LIFT STATION THAT COULD NOT KEEP UP WITH RAIN FALL. | HAD TO WAIT FOR PUMPS TO CATCH UP
INM022560 | TOWN OF CHESTERFIELD | MADISON | 2012-10-04 | 12:28P-1:06P | 13000 | CSO-028 | WHITE RIVER | ANDERSON WASTE WATER HAD A UPS FAILURE @ L S | ANDERSON CAME IN TO FIX THE PROBLEM
IN0023183 | BELMONT AWT | MARION | 2012-01-10 | 3:30P - 4:00P | 200 | PLANT | GROUND | OVERFLOWED DRAIN WHILE FINAL CLARIFIERS WERE BEING DRAINED | CLOSED DRAIN VALVES AND CLEANED AREA
IN0023183 | BELMONT AWT | MARION | 2012-01-17 | 1:20P-5:40P | 8060000 | 2700 S BELMONT AVE OUTFALL 007 | WHITE RIVER | RAIN | ALL AVAIL EQUIP WAS OPERATING & EQUALIZATION BASIN USED FOR STORAGE
IN0023183 | BELMONT AWT | MARION | 2012-01-20 | 1:30A-4:15A | 5000 | 2700 S BELMONT TREATMENT PLANT | GROUND, STORM SEWER AND EAGLE CREEK | HIGH PRESSURE SECONDARY WATER LINE BROKE | WILL EXPOSE LINE AND REPAIR LEAK
IN0023183 | BELMONT AWT | MARION | 2012-01-20 | 1:30A-1:45A | 1000 | 2700 S BELMONT TREATMENT PLANT | PARKING LOT & EAGLE CREEK | TERTIARY WATER LINE BROKE & FINAL EFFLUENT FLOODED A PARKING LOT & & DRAIN THAT RUNS TO EAGLE CREEK | WILL EXPOSE LINE AND REPAIR LEAK
IN0023183 | BELMONT AWT | MARION | 2012-01-26 | 10:15P - 1:00A (1/27) | 77000000 | OUTFALL 007 | WHITE RIVER | RAIN | ALL EQUIP OPERATING AND EQ BASIN USED FOR STORAGE
IN0023183 | BELMONT AWT | MARION | 2012-02-09 | 1:30A-2:30A | 5000 | 2700 S BELMONT TREATMENT PLANT | GROUND, STROM SEWER & EAGLE CREEK | A HIGH PRESSURE SECONDARY WATER LINE BROKE & SECONDARY EFFLUENT POURED ON TO ROAD & DRAIN THAT RUNS TO EAGLE CREEK | UPON DISCOVERY OF THE LEAK THE OPERATORS TRIED TO TROUBLE SHOT & STOPPED THE LEAK ETC
IN0023183 | BELMONT AWT | MARION | 2012-03-06 | 3:30P-4:00P | 1000 | 2700 S BELMONT, TREATMENT PLANT | GROUND @ CONSTRUCTION SITE | CONSTRUCTION RELATED APPROX 1000 GAL OF PRIMARY TREATED WATER OVERFLOWED THE PRIMARY LINE AT THE PIG RETRIEVAL SITE DRAIN | AN OPERATOR WAS ALERTED TO WATER ON THE CONSTRUCTION SITE NEAR THE PIG RETRIEVAL SITE ETC
IN0023183 | BELMONT AWT | MARION | 2012-04-01 | 7:00A - 7:15A | 4000 | OUTFALL 007 | WHITE RIVER | RAIN | MAXIMIZED FLOW
IN0023183 | BELMONT AWT | MARION | 2012-05-01 | 10:15P-4:20A | 7761000 | OUTFALL 007 | WHITE RIVER | RAIN | ALL AVAIL EQUIPMENT WAS OPERATING AND THE EQUALIZATION BASINS WERE USED FOR STORAGE
IN0023183 | BELMONT AWT | MARION | 2012-05-24 | 7:30P-7:45P | 3000 | TREATMENT PLANT | GROUND @ CONSTRUCTION SITE | CONSTRUCTION RELATED THE PLANT VALVING WAS CHANGED DURING THE SHUT DOWN WHEN PRIMARY EFFLUENT FLOW WAS RETURNED TO THE AWT IT WAS RESTRICTED | THE VALVES WERE PLACED IN THE CORRECT POSITION FOR BOTH SIDES OF THE AWT TO BE IN LONG MIX.
IN0023183 | BELMONT AWT | MARION | 2012-08-05 | 6:40P - 7:55A (8/6) | 19000 | OUTFALL 007 | WHITE RIVER | RAIN; DISCOVERED WHILE REVIEWING WET WEATHER OVERFLOW METER DATA | ALL EQUIMPMENT RUNNING AND EQ BASINS USED FOR STORAGE
IN0023183 | BELMONT AWT | MARION | 2012-08-05 | 6:40A-6:55A | 3000 | TREATMENT PLANT | ROAD | RAIN. DURING A THUNDERSTORM WE LOST SOME OF THE WET WELL LEVEL INDICATION DUE TO LIGHTING. | WE DIVERTED FLOW INTO THE SOUTH PRIMARIES & THE STORAGE BASINS
IN0023183 | BELMONT AWT | MARION | 2012-08-07 | 12:05P - 12:15P | 500 | PLANT | STREAM AND STORM SEWER | LEAKED FROM WATER CANNON DURING CLEANING OPERATION | WATER CANNON TAKEN OUT OF SERVICE AND WILL BE REPAIRED
IN0023183 | BELMONT AWT | MARION | 2012-08-09 | 10:28P - 2:00A (8/10) | 1693000 | OUTFALL 007 | WHITE RIVER | RAIN | ALL EQUIPMENT OPERATING
IN0023183 | BELMONT AWT | MARION | 2012-08-09 | 2:20P - 2:22P | 6000 | PLANT | GROUND AND STORM SEWER TO EAGLE CREEK | DRAIN WATER FROM INCINERATION BUILDING OVERFLOWED MH DURING BYPASS PUMP OPERATION | FLOW STOPPED WHEN CONTRACTOR STARTED BYPASS PUMPS
IN0023183 | BELMONT AWT | MARION | 2012-09-01 | 19:18-19:28 |  | OUTFALL 007 | WHITE RIVER | RAIN ANS INFLUENT PUMP # 3 FAILED | ALL AVAILABLE EQUIPMENT WAS OPERATING. THE EQ BASINS WERE USED FOR STORAGE AND FILLING SOUTH PRIMARY FOR STORAGE
IN0023183 | BELMONT AWT | MARION | 2012-09-02 | 20:00-23:15 |  | OUTFALL 007 | WHITE RIVER | RAIN | ALL AVAILABLE EQUIPMENT WAS OPERATING. THE EQ BASINS AND SOUTH PRIMARY WERE USED FOR A STORAGE
IN0023183 | BELMONT AWT | MARION | 2012-10-05 | 11:50P-4:20A | 7721000 | 2700 S BELMONT AVE | WHITE RIVER | RAIN | ALL AVAILABLE EQUIPMENT WAS OPERATING & THE EQUALIZATION BASIN WERE USED FOR STORAGE.
IN0023183 | BELMONT AWT | MARION | 2012-10-05 | 4:52P-4:58P |  | 2700 S BELMONT AVE | WHITE RIVER | RAIN | ALL AVAILABLE EQUIPMENT WAS OPERATING & THE EQUALIZATION BASIN WERE USED FOR STORAGE.
IN0023183 | BELMONT AWT | MARION | 2012-11-19 | 1:15-1:45 | 1000 | 2700 S BELMONT TREATMENT PLANT | GROUND AT HEADWORKS | THE OVERFLOW OCCURRED WHEN ONE OF THE TWO OPERATING BAR SCREENS BECAME INOPERABLE. | OTHER SCREENS WERE STARTED & THE HIGH CHANNEL LEVEL WAS REDUCED.
| CITY OF LAWRENCE UTILITIES | MARION | 2012-10-25 | 11:10A-11:25A | 750 | 4804 KATHERINE DR FORCE MAIN | STORM SEWER & GROUND | A PRESSURE BREAK BLOW OUT IN THE CAST IRON FORCE MAIN | SHUT DOWN LIFT STATION. USED VACTOR TO SUCK UP SEWAGE FROM BREAK.
IN0023183 | CWA AUTHORITY | MARION | 2012-01-03 | 7:23A - 7:10P | 1750 | 6125 GRANDVIEW | LOT | BYPASS FAILURE AT CONSTRUCTION OF NEW BELMONT NORTH LS
IN0023183 | CWA AUTHORITY | MARION | 2012-01-05 | 7:00P - 7:40P | 30 | PLANT | GROUND | SEAL ON VALVE FAILED | STOPPED LEAK, CLEANED AREA, WILL REPAIR VALVE
IN0023183 | CWA AUTHORITY | MARION | 2012-01-05 | 7:13P - 8:51P | 15 | 4402 BARNOR | LOT | DEBRIS | CLEANED BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-01-08 | 2:52P - 5:08P | 9964 | 3919 COOPER LANE | DITCH - CROOKED CREEK | DEBRIS | CLEANED SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-01-12 | 8:51P-11:00P | 3150 | 2 S WHITCOMB AVE | PAVED AREA/STREET | RAIN .06 DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-01-18 | 12:21P-1:33P | 352 | 3934 CATALINA CT | PAVED AREA/STREET | DEBRIS | CLEAN SEWER BLOCKAGE REMOVE DEBRIS FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-01-24 | 2:54P - 5:15P | 30 | 6543 COTTON CREEK CT. | LOT | PRIVATE CONTRACTOR DAMAGE | EXCAVATE AND REPAIR SEWER
IN0023183 | CWA AUTHORITY | MARION | 2012-01-31 | 1:42P-3:13P | 20 | 9228 BUDD RUN DR | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-02-01 | 3:30P-4:45P | 20 | 2269 N CENTENNIAL ST | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-02-02 | 1:39P-5:40P | 1177 | 6742 DONINGTON CIR | LOT/YARD/FIELD | PRIVATE CONTRACTOR DAMAGE IPL'S CONTRACTOR BORED THROUGH PRIVATE LATERAL, SANITARY MAIN NOT HIT | EXCAVATE & REPAIR SEWER
IN0023183 | CWA AUTHORITY | MARION | 2012-02-08 | 12:57P-2:29P | 20 | 7919 WEDGEFIELD DR | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-02-10 | 9:32P-10:16P | 20 | 9135 RYMARK DR | CUSTOMER HOME/BLDG | OTHER DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-02-15 | 9:11A-3:00P | 2500 | 11600 FALL CREEK RD | PAVED AREA/STREET | LS FORCE MAIN RUPTURE | EXCAVATE & REPAIR SEWER
IN0023183 | CWA AUTHORITY | MARION | 2012-02-15 | 1:11P - 2:49P | 20 | 986 N MITTHOEFER RD | HOME | DEBRIS | CLEANED BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-02-17 | 9:25P-11:14P | 20 | 9421 TOWER LN | CUSTOMER HOME/BLDG | OTHER DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-03-02 | 18:40-21:05 | 1139000 | 2700 BELMONT AVE | WHITE RIVER | RAIN | ALL AVAIL EQUIPMENT WAS OPERATING AND THE EQUALIZATION BASINS WERE USED FOR STORAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-03-08 | 1:25P-3:40P | 8000000 | 2700 S BELMONT AVE | WHITE RIVER | RAIN | ALL AVAILABLE EQUIPMENT WAS OPERATING AND THE EQUALIZATION BASIN WERE USED FOR STORAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-03-08 | 12:40P-12:50P | 300 | 5764 COBURN AVE | LOT/YARD/FIELD | RAIN .68"
IN0023183 | CWA AUTHORITY | MARION | 2012-03-09 | 10:06P-12:45A | 50 | 702 GREENLEE DR | LOT/YARD/FIELD | RAIN 0.10 DEBRIS MH COVER HAD BEEN REMOVED AND DEBRIS THROWN IN MH TOOK OUT PLASTIC SLIDE AND WOOD | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-03-09 | 3:09P-6:30P | 19635 | 6300 S CONCORD ST | LOT/YARD/FIELD | LS FORCE MAIN RUPTURE | EXCAVATE & REPAIR SEWER EXCAVATE SOIL
IN0023183 | CWA AUTHORITY | MARION | 2012-03-13 | 9:44A-2:22P | 10863 | 10980 FALL CREEK RD | STORM STRUCTURE | LS FORCE MAIN RUPTURE | EXCAVATE & REPAIR SEWER EXCAVATE SOIL
IN0023183 | CWA AUTHORITY | MARION | 2012-03-14 | 2:00A-2:05A | 100 | 2700 S BELMONT, TREATMENT PLANT | GROUND @ CONSTRUCTION SITE | CONSTRUCTION RELATED APPROX 100 GAL OF PRIMARY SLUDGE CAME TO THE SURFACE OF THE GROUND OVER A PRIMARY SLUDGE LINE. | THE OPERATOR OPENED THE TANK VALVES AND REDUCED LINE PRESSURE. ETC
IN0023183 | CWA AUTHORITY | MARION | 2012-03-23 | 2:10P-5:36P | 46127000 | 2700 S BELMONT AVE | WHITE RIVER | RAIN | ALL AVAILABLE EQUIPMENT WAS OPERATING AND THE EQUALIZATION BASINS WERE USED FOR STORAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-03-26 | 12:57P-1:52P | 20 | 5015 UNIVERSITY AVE | CUSTOMER HOME/BLDG | OTHER DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-03-29 | 11:30A-1:05P | 20 | 6413 N COLLEGE AVE | CUSTOMER HOME/BLDG | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-03-29 | 5:21P-6:35P | 10 | 1109 LAUREL ST | SPILL CONTAINED | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-04-02 | 5:28P-7:26P | 10 | 5722 LIBERTY CREEK DR E | LOT/YARD/FIELD | DEBRIS | CLEAN SEWER BLOCKAGE EXCAVATE SOIL
IN0023183 | CWA AUTHORITY | MARION | 2012-04-05 | 5:19P-9:30P | 1226 | 7099 MICHIGAN ROAD | LOT/YARD/FIELD | DEBRIS | CLEAN SEWER BLOCKAGE EXCAVATE SOIL
IN0023183 | CWA AUTHORITY | MARION | 2012-04-06 | 6:40P-8:05P | 5 | 6185 NORWALDO ASSET ID # 690283 697889 | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-04-10 | 3:05P-4:20P | 20 | 4136 W 37TH ST | LOT/YARD/FIELD | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-04-17 | 8:08P-9:40P | 90 | 5437 HONEY MANOR DR | PAVED AREA/STREET | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-04-18 | 12:44P-2:44P | 20 | 2140 E 86TH ST ASSET ID #903830 903829 | SPILL CONTAINED | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-05-01 | 12:30P-1:30P | 5 | ASSET ID 952553 | LOT/YARD/FIELD | PRIVATE PROBLEM UNKNOWN OWNERSHIP OF MH DID CLEAN UP FOR HEALTH AND SAFETY IN AREA | REMOVE DEBRIS FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-05-01 | 11:23A-1:09P | 5 | ASSET ID 751172 | LOT/YARD/FIELD | RAIN 1.2" | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-05-01 | 10:20P-12:41P | 2523 | 5520 S STATE AVE ASSET ID # 530491 | DITCH | RAIN 1.5" | REPAIR LIFT STATION
IN0023183 | CWA AUTHORITY | MARION | 2012-05-01 | 8:26P-8:40P | 68 | ASSET 904808 | LOT/YARD/FIELD | RAIN 1" | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-05-02 | 12:45A-10:10P |  | 8414 HARRINGTON ASSET ID # LS410 | CUSTOMER/HOME/BLDG | POWER FAILURE, RAIN 1.5" | REPAIR LIFT STATION
IN0023183 | CWA AUTHORITY | MARION | 2012-05-17 | 10:52P-11:49P | 25 | 4402 N ARLINGTON AVE | PAVED AREA/STREET | GREASE | CLEAN SEWER BLOCKAGE REMOVE DEBRIS FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-05-17 | 2:34P-1:02P | 2634 | 8098 TOWNSHIP LINE RD | LOT/YARD/FIELD | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-05-23 | 4:49P-7:00P | 25 | 1901 N FRANKLIN RD | CUSTOMER HOME/BLDG | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-05-24 | 10:53P-12:26A | 3634 | 4114 KENNETH ASSET ID # 150073 | LOT/YARD/FIELD | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-05-30 | 3:13P-1:40P | 5000 | 4599 WEST PERIMETER RD ASSET ID # 750024 | SPILL CONTAINED | EQUIPMENT FAILURE LS ALARM FAILURE | FLUSH AREA EXCAVATE SOIL
IN0023183 | CWA AUTHORITY | MARION | 2012-06-07 | 9:35P-9:44P | 25 | 2732 SATURN DR | HOME | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-06-09 | 3:20P-5:10P | 5 | 45 BEACHWAY DR. | LOT/YARD/FIELD | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-06-10 | 10:36A-12:35P | 20 | 5550 MARNETTE ST. | LOT/YARD/FIELD | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-06-12 | 10:31P - 12:40A (6/13) | 630 | 8651 W 82ND ST | LOT | GREASE | CLEAN BLOCKAGE, FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-06-13 | 5:40P-2:08A | 496 | 9000 CORPORATION DR | LOT/YARD/FIELD | PRIVATE CONTRACTOR DAMAGE. CONTRACTOR DIRECTIONAL BORED THROUGH FORCE MAIN | EXCAVATE & REPAIR SEWER
IN0023183 | CWA AUTHORITY | MARION | 2012-06-15 | 8:25P-9:56P | 25 | 4313 TOWNE CT | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-06-16 | 4:35P-6:02P | 255 | 9219 FOREST WILLOW DR | STORM STRUCTURE | LS VALVE MALFUNCTION ISOLATE AIR RELEASE VALVE | EXCAVATE SOIL
IN0023183 | CWA AUTHORITY | MARION | 2012-07-02 | 11:08A - 12:37P | 20 | 10328 E. 30 TH ST | CUSTOMER HOME | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-07-17 | 8:36P-10:00A | 30 | 7164 E 86TH ST FORCE MAIN | DITCH | PRIVATE CONTRACTOR DAMAGE | EXCAVATE & REPAIR SEWER
IN0023183 | CWA AUTHORITY | MARION | 2012-07-20 | 2:28P-4:11P | 101 | ASSET ID # 636460 | STORM STRUCTURE | ROOTS AND GREASE | REMOVE DEBRIS, FLUSH AREA CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-08-03 | 12:15P-5:24P | 302 | 5150 DECATUR BLVD ASSET #ID LS208 740043 | LOT/YARD/FIELD | PRIVATE CONTRACTOR DAMAGE | EXCAVATE & REPAIR SEWER
IN0023183 | CWA AUTHORITY | MARION | 2012-08-08 | 3:51P-4:42P | 100 | 4352 N MITTHOFFER ASSET ID # 480748 | DITCH | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-08-08 | 3:52P-4:42P | 98 | ASSET ID # 480670 | DITCH | OTHER GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-08-11 | 5:21P - 6:49P | 50 | 3508 MOELLER | LOT | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-08-15 | 1:33P-2:20P | 5 | ASSET ID # 904575 904567 | CUSTOMER HOME/BLDG | OTHER DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-08-23 | 9:23A-11:30A | 5 | 406 LIMESTONE ST | SPILL CONTAINED | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-08-30 | 5:28P-7:20P | 328 | ASSET ID # 930436 | DITCH | OTHER DEBRIS | CLEAN SEWER BLOCKAGE FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-09-01 | 8:00P - 8:20P | 15 | 3912 WASHINGTON BLVD | BASEMENT | RAIN I&I
IN0023183 | CWA AUTHORITY | MARION | 2012-09-08 | 10:27A-1:30P | 536 | 5058 W RAYMOND ST. | LOT/YARD/FIELD | ROOTS AND GREASE | CLEAN SEWER BLOCKAGE FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-09-10 | 10:11A-2:15P | 715 | 1521 CRUFT ST | LOT/YARD/FIELD | DEBRIS | REMOVED DEBRIS, CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-09-13 | 4:55P-7:18P | 25 | 3013 ASHLAND AVE | LOT/YARD/FIELD | DEBRIS | REMOVED DEBRIS, CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-09-17 | 3:28P-10:30P | 3298 | 5050 E WASHINGTON ST | COMBINED SEWER OUTFALL/PLEASANT RUN | VANDALS THREW MONITOR DOWN IN FLOW LINE PLUS 7.5 GALLON BUCKETS OF RIP RAP IN MH CAUSING BLOCKAGE | REMOVE DEBRIS; INSTALL BOLT DOWN LID
IN0023183 | CWA AUTHORITY | MARION | 2012-09-22 | 11:49A-1:58P | 20 | 8125 SARGENT RIDGE | LOT/YARD/FIELD | RAIN 1.03" I&I | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-09-30 | 9:35P-12:30P | 25 | 5902 HARBISON AVE | STORM STRUCTURE | GREASE | CLEAN SEWER BLOCKAGE; REMOVE DEBRIS
IN0023183 | CWA AUTHORITY | MARION | 2012-10-02 | 8:48A-10:05A | 5641 | 4037 GUION LN | STORM STRUCTURE | DEBRIS | CLEANED SEWER BLOCKAGE, FLUSHED AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-10-06 | 5:00P-8:26P | 25 | 8120 RUCKER RD | LOT/YARD/FIELD | RAIN 1.24 GREASE | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-10-11 | 2:07P - 2:50P | 25 | 5640 WINSHIP | FIELD | DEBRIS | FLUSH AREA, CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-10-17 | 11:20A-3:25P | 2393 | 5781 TICONDEROGA LN | DITCH | GREASE | CLEAN SEWER BLOCKAGE REMOVE DEBRIS
IN0023183 | CWA AUTHORITY | MARION | 2012-11-05 | 3:00P-5:58P | 2087 | 5546 W 43RD ST | LOT/YARD/FIELD | GREASE | CLEAN SEWER BLOCKAGE REMOVE DEBRIS
IN0023183 | CWA AUTHORITY | MARION | 2012-11-15 | 1:25P-2:31P | 20 | 6704 GRANNER CT | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-11-16 | 7:46P-9:45P | 20 | 4911 PRIMROSE AVE | CUSTOMER HOME/BLDG | OTHER ROOTS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-11-17 | 10:31P-12:05A | 20 | 10230 MEADOWLARK DR | CUSTOMER HOME/BLDG | OTHER DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-11-22 | 8:49P - 1:04A (11/23) | 249 | 6935 CHAUNCEY DR. | LOT | GREASE | FLUSHED AREA, CLEANED SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-11-23 | 11:59A-1:40P | 25 | 3603 MAYFLOWER DR | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-11-24 | 9:05A-11:35A | 25 | 8844 HOLLOWOOD DR | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-11-25 | 10:18P-12:48A | 20 | 6733 KINGMAN DR | CUSTOMER HOME/BLDG | DEBRIS | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-12-04 | 12:50P - 7:30P | 391 | 6829 GUNNERY RD. | STREET | PRIVATE CONTRACTOR DAMAGE | CONTRACTOR REPAIRED
IN0023183 | CWA AUTHORITY | MARION | 2012-12-04 | 9:45A - 10:50A | 25 | 2002 W. 86TH ST | HOME | GREASE | CLEANED SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-12-05 | 7:26A - 8:53A | 10 | 3509 E. SUMNER AVE | LOT | DEBRIS | REMOVED DEBRIS, FLUSHED AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-12-06 | 10:50A-12:36P | 207 | 11253 E 38TH ST | STORM STRUCTURE | DEBRIS | FLUSH AREA CLEAN SEWER BLOCKAGE REMOVE DEBRIS
IN0023183 | CWA AUTHORITY | MARION | 2012-12-10 | 11:20A-2:38P | 193 | 2105 YANDES ST | PAVED AREA/STREET | GREASE | CLEAN SEWER BLOCKAGE FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-12-10 | 9:50A-1:00P | 186 | 11691 FALL CREEK RD | LOT/YARD/FIELD | GREASE | CLEAN SEWER BLOCKAGE FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-12-14 | 9:00A-10:30A | 20 | 6621 CHERBOURG CIR | STORM STRUCTURE | DEBRIS | CLEAN SEWER BLOCKAGE FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-12-14 | 8:37P-10:41P | 20 | 10009 MEADOWLARK DR | CUSTOMER HOME/BLDG | GREASE | CLEAN SEWER BLOCKAGE
IN0023183 | CWA AUTHORITY | MARION | 2012-12-18 | 10:00A-1:02P | 178 | 5175 E 65TH ST | PAVED AREA/STREET | LS FORCE MAIN RUPTURE | EXCAVATE & REPAIR SEWER FLUSH AREA
IN0023183 | CWA AUTHORITY | MARION | 2012-12-30 | 11:16P-1:10A | 20 | 3708 N BRENTWOOD AVE | CUSTOMER HOME/BLDG | DEBRIS SNOW MELT | CLEAN SEWER BLOCKAGE
IN0023183 | SOUTHPORT AWT | MARION | 2012-05-06 | 2:30A-2:45A | 100 | PRIMARY CLARIFIER | GROUND AROUND CONTAINMENT AREA | THE DRAIN ON A SIDE BOX OF THE GREASE CONCENTRATOR BECAME PLUGGED AND BACKED UP A GREASE TOWER | THE MATERIAL WAS QUICKLY CLEANED UP AND THE AREA HOSED DOWN. ETC
IN0023183 | SOUTHPORT AWT | MARION | 2012-07-24 | 1:30P-1:35P | 1000 | TREATMENT PLANT | ROAD | THE OPERATOR WAS HAULING A GREASE TOWER AND OVERFILLED THE DUMP TRUCK IT IS EST THAT A 1000GAL OF PRIMARY TREATED WATER & GREASE MIX MAIN WATER | THE SPILL WAS CONTAINED IN A DEPRESSION IN THE PAVEMENT
IN0023183 | SOUTHPORT AWT | MARION | 2012-08-13 | 2:22P - 2:23P | 6000 | 3800 W. SOUTHPORT RD | GROUND | POWER OUTAGE, PROCESS PUMPS WENT DOWN | CLEAN UP SITE
IN0023183 | SOUTHPORT AWT | MARION | 2012-10-10 | 8:45P-8:59P |  | 3800 W SOUTHPORT RD TREATMENT PLANT | GROUND SURROUNDING THE GRIT BLDG | HALF OF THE GRIT REMOVAL SYSTEM WAS ISOLATED FOR MAINT ACTIVITIES. COULD NOT HANDLE ADDITIONAL VOLUME | RAW PUMP REMOVED FROM SERVICE AND RAW FLOW SENT TO BELMONT. CLEANED AREA
| TOWN OF SPEEDWAY | MARION | 2012-09-10 | 10:00P-11:00P |  | 1038 MAIN ST CHARLIE BROWNS | BASEMENT | RAIN A FEW INCHES OF WATER IN BASEMENT
| TOWN OF SPEEDWAY | MARION | 2012-09-10 | 10:00P-12:00A | 100 | CHAPEL HILL LIFT STATION | STORM SEWER | RAIN 2.9" | CLEAN UP AREA & SPREAD LIME ON DISTURBED AREA
| TOWN OF SPEEDWAY | MARION | 2012-09-10 | 10:40P-11:30P |  | 405 ARTHUR AVE | BASEMENT | RAIN 2.9" 4" OF WATER IN BASEMENT & IN 52 MIN ALL WATER DRAINED DOWN.
IN0020427 | BREMEN MUNICIPAL STP | MARSHALL | 2012-04-09 | 4:00P-? |  | BIO-TOWERS | YELLOW RIVER | PRE-APPROVED MAINTENANCE TO TOWERS | RECAULKING ONE TOWER AT A TIME
IN0021298 | CULVER MUNICIPAL STP | MARSHALL | 2012-01-09 | 1:00P - 1:10P | 15000 | MH COOLIDGE & WASHINGTON | STORM SEWER | GREASE | JETTED LINE
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2012-01-15 | 0700-0745 | 1000 | LIFT STATION 2 | GROUND | PUMPS TRIPPED | STP OPERATORS CHECKING LIFT STATION EVERY 2 HR TILL 1/17
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2012-01-17 | 8:00A -12:00P | 15000 | LIFT STATION 17, 34 | GROUND | RAIN 1.25 | STP OPERATOR AND UTILITY FIELD STAFF USING PUMP & TANKER TRUCK
IN0021539 | NAVAL SURFACE WARFARE CENTER | MARTIN | 2012-04-08 | 18:53-19:20 | 3000 | LIFT STATION 2 | GROUND | PUMPS APPARENTLY TRIPPED DUE TO AN OVERLOAD. | AREA WAS INSPECTED NO EVIDENCE OF DAMAGE
IN0035726 | BLOOMINGTON N (BLUCHER POOLE) | MONROE | 2012-05-07 | 9:00P - 12:15A (5/8) | 16248 | 9922, 9926 RUSGAN & RAMBLE | CASCADE CREEK | RAIN 1.68" | AREA CLEANED OF DEBRIS
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2012-01-17 | 10:00A-12:15P | 47520 | MANHOLE 4742 | GROUND & CLEAR CREEK | RAIN 1.23"
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2012-01-17 | 1/18 | 432375 | MH 6, 9382, 9933, 9940, 3600 | CLEAR, SINKING, JACKSON CREEK | RAIN 1.23" | CLEANED AREA, UNDER AO
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2012-01-23 | 3:15A-6:30A | 936000 | GRIMES LANE MH 6 | CLEAR CREEK | RAIN .64" | THE AREA WAS CLEANED OF DEBRIS
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2012-05-07 | 10:00P - 3:40A (5/8) | 180983 | MH 6290, 9983 | CLEAR CREEK, JACKSON CREEK | RAIN 1.68" | AREA CLEANED OF DEBRIS
IN0035718 | BLOOMINGTON S (DILLMAN ROAD) | MONROE | 2012-12-07 | 9:30A-11:00A | 90 | 2700 BLOCK E ST MH 2013 | JACKSON CREEK | BLOCKAGE IN 10" LINE. | THE AREA WAS CLEANED OF DEBRIS.
IN0045187 | CASLON WWTP | MONROE | 2012-07-07 | 10:00A-12:00P | 1000 | FOUR WINDS LIFT STATION | GROUND | BREAK IN THE FORCE MAIN APPROX 100 FT FROM THE LIFT STATION | HAD TODD'S SEPTIC SERVICE KEEP THE LIFT STATION PUMPED DOWN WHILE REPAIRS WERE MADE
IN0045187 | CASLON WWTP | MONROE | 2012-08-18 | 3:00P-3:30P | 1000 | FOUR WINDS LIFT STATION FORCE MAIN | GROUND | BREAK IN THE FORCE MAIN APPROX 50 FT FROM THE LIFT STATION | HAD TODD'S SEPTIC SERVICE KEEP THE LIFT STATION PUMPED DOWN WHILE REPAIR WERE MADE
IN0045187 | CASLON WWTP | MONROE | 2012-10-18 | 8:30A-10:00A | 1000 | FOUR WINDS L S | GROUND | BEAK IN THE FORCE MAIN APPROX. 180 FT FROM THE L S | PUMPED OUT THE REMAINDER OF SEWAGE IN THE DISCHARGE PIPE, SO A SECTION OF THE PIPE COULD BE REPLACED.
IN0045187 | CASLON WWTP | MONROE | 2012-12-10 | 8:45A-9:20A | 1000 | FOUR WINDS FORCE MAIN | GROUND | BREAK IN THE FORCE MAIN APPROX. 700 FT FROM THE L S. CRACK IN PIPE. | HAD TODD'S SEPTIC SERVICE PUMP THE SEWAGE OUT OF THE REPAIR TRENCH AND INSTALLED A FULL SEAL CLAMP
| EASTERN RICHLAND SEWER CORP. | MONROE | 2012-03-26 | 5:00P-8:00P |  | LIFT STATION ON BREWSTER COURT IN BLOOMINGTON/ELLETTSVILLE IN AREA | ON THE GROUND | GOT A VACTOR TRUCK TO SUCK OUT EXCESS SEWAGE FROM LIFT STATION AND AREA EFFECTED. WAS NOT NEEDED | CALLED ELECTRICIAN TO REPAIR THE POWER TO THE PUMP @ THE LIFT STATION
| EASTERN RICHLAND SEWER CORP. | MONROE | 2012-05-07 | 9:00P-2:00A |  | LIFT STATION ON BREWSTER COURT, MH 132 | ON THE GROUND | RAIN 1-2 GOT A VACTOR TRUCK AND PUMPED WATER OUT OF THE LIFT STATION | LOOKING INTO THE REASON WHY THERE IS SO MUCH INFILTRATION IN THIS AREA
| EASTERN RICHLAND SEWER CORP. | MONROE | 2012-05-17 | ?-12:00P |  | MH 399 BACK IN THE WOODS ON WEATHER COURT AREA | GROUND | ROOTS GREW INTO THE PIPE AND BLOCKED THE FLOW CAUSING A BACKUP | CAMERA THROUGH THE LINE FOUND ROOTS INTO THE SYSTEM WE CLEANED ALL ROOTS OUT OF THE PIPE SO FLOW COULD RESUME
IN0032964 | CRAWFORDSVILLE WWTP | MONTGOMERY | 2012-03-23 | 9:20A-9:50A |  | CSO-002 | SUGAR CREEK | RAIN 0.5"
IN0032964 | CRAWFORDSVILLE WWTP | MONTGOMERY | 2012-08-17 | 5:45P-7:00P | 25 | MH ON PLANT GROUND | STORM SEWER TO SUGAR CREEK | BYPASS DUE TO PLC MALFUNCTION, PROGRAM ALLOWED INFLUENT VALVE FROM THE EQ BASIN TO FLOW AT A RATE OF 8 MGD | REPROGRAM PLC TO ELIMINATE POTENTIAL OF 8 MGD FLOW FROM THE EQ BASIN TO THE PLANT SYSTEM
IN0022721 | DARLINGTON MUNICIPAL STP | MONTGOMERY | 2012-09-02 | 1:55P-2:20P | 100 | DARLINGTON # 1 LIFT STATION | GROUND | RAIN 1.4 BOTH PUMPS IN THE DARLINGTON # 1 LIFT STATION FAILED DUE TO POWER OUTAGE | SPREAD LIME ON AFFECTED AREAS
IN0022721 | DARLINGTON MUNICIPAL STP | MONTGOMERY | 2012-10-01 | 5:50P-6:05P | 100 | DARLINGTON # 1 L S | GROUND | BOTH PUMPS/VFD'S FAILED | ADDED LIME TO AFFECTED AREAS.
IN0040711 | LITTLE RACCOON RSD | MONTGOMERY | 2012-10-15 | 1:00P-2:00P | 1000 | EFFLUENT MH ALONG ROAD TO CREEK | SOAKED IN GROUND | MECHANICAL FLOAT/VALVE SYSTEM STUCK. EFFLUENT WATER. | STOPPED DISCHARGING RESET FLOW
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-01-13 | 3:58A-4:00AM |  | 147 | GROUND | EQUIPMENT FAILURE WORKING ON PUMPS BYPASSED COUPLE MINS | WORKING ON STARTERS
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-01-17 | 9:15A - 10:30A |  | #76 | WHITE LICK CREEK | RAIN .1"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-01-17 | 10:19A-11:55A |  | # 32 | WHITE LICK CREEK | RAIN .1"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-01-22 | 3:30A-3:59A |  | #76 | WHITE LICK | RAIN .1"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-01-24 | 11:30A - 11:58A |  | #32 | WHITE LICK CREEK | POWER OUTAGE
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-01-26 | 6:30A - 8:30A |  | #76 | WHITE LICK CREEK | RAIN .1" | CLEAN AND LIME
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-01-26 | 8:00A - 12:05A |  | #32 | WHITE LICK CREEK | RAIN .1" | CLEAN AND LIME
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-05-01 | 4:24P-4:55P |  | #147 | WHITE LICK | RAIN 1.5"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-05-01 | 4:24P-4:55P |  | #76 | WHITE LICK | RAIN 1.5"
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-08-06 | 6:00P-7:30P |  | MH # 50 | NEXT TO MH | MAIN PLUGGED UP | USED VAC TRUCK JETTED OUT
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-09-02 | 6:00P-6:30P |  | #76 | WHITE LICK CREEK | RAIN 2.5
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-09-07 | 10:00P-12:00A |  | MH # 76 | WHITE LICK CREEK | RAIN 2.0 | RAKE & PUT LIME DOWN
IN0039772 | BROOKLYN MUNICIPAL STP | MORGAN | 2012-11-06 | 12:00P-2:00P | 400 | SERVICE CLEAN OUT | GROUND | MAIN PLUGGED UP | USED VAC TRUCK TO CLEAN MAIN MH 202 VAC UP WATER OFF GROUND
| CIRCLE K 0013 | MORGAN | 2012-04-25 | 8:00A - 8:30A |  | TROY STANLEY DR AND PARK ST | GROUND | AT&T BORE THROUGH LINE | SPREAD LIME AND REPAIRED LINE
IN0049361 | MAPLETURN UTILITIES, INC. | MORGAN | 2012-01-12 | 6:00A - 7:30A | 6000 | PLANT | GROUND | RAGS CAUGHT BETWEEN AERATION AND CONTACT CHAMBER | CLEANED AREA
IN0020303 | MARTINSVILLE MUNICIPAL STP | MORGAN | 2012-03-27 | 11:50A - 12:30P | 200 | 109 JANAY DR. MH BEFORE LS | STORM SEWER | BLOWN FUSE AND BAD SWITCH IN LS | REPAIRED LS AND CLEANED AREA
IN0036820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2012-01-17 | 6:00A-7:00A |  | M H EAST OF PUMP STATION UNPACK LOT N OF PUMP STATION | GROUND TO STORM TO CREEK PAVEMENT | RAIN 2"
IN0026820 | MORGANTOWN MUNICIPAL STP | MORGAN | 2012-01-25 | 6:00A - 5:00P |  | LS SR 135 AT THE BRIDGE | GROUND TO INDIAN CREEK | RAIN 1.75"
IN0023825 | TOWN OF MOORESVILLE | MORGAN | 2012-03-24 | 10:00A-12:30P |  |  | BASEMENT OF MRS WRIGHTSMAN | GREASE CLOGGING SANITARY SEWER LINE | CLEANED GREASE OUT OF SANITARY SEWER W/RODDER TRUCK & VAC
IN0020664 | AVILLA MUNICIPAL STP | NOBLE | 2012-01-17 | 6:00A-10:00A | 8000 | MANHOLE W OF 4TH ST LIFT STATION | ELEY CREEK | RAIN 1.2 I&I | VERIFIED THAT PUMPS WERE RUNNING, LOCATING I&I
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2012-01-10 |  | 18000 | CSO-009 | GROUND | WATER DEPARTMENT BACK-WASHED PLANT FILTER
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2012-02-17 | 2/19 | 85000 | CSO #2 | STREAM | RAIN
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2012-03-25 |  | 183000 | CSO 002 SMITH ST. | RECEIVING STREAM | PLUG IN LINE | CLEANED LINE
IN0023582 | LIGONIER MUNICIPAL STP | NOBLE | 2012-11-09 | 7:15A-8:30A | 8202 | CSO #9 | ELKHART RIVER | SEWER LINES AT THE INTERSECTION OF CAVIN & RICHMOND ST ARE NOT OF ADEQUATE SIZE. | BACK WASHING IS WILL BE DONE AT LOW FLOW PERIODS TO OPTIMIZE PPL CAPACITY
IN0024431 | RISING SUN MUNICIPAL UTILITIES | OHIO | 2012-06-17 |  | 25 | MH # 0-1 | ROADWAY SHOULDER | POWER FAILURE POWER BLINK KICKED OUT BOTH PUMPS | RESET BOTH PUMPS. BOTH PUMPS CAME ON TO CATCH UP AND OVERWHELMED MH
IN0021601 | ORLEANS MUNICIPAL STP | ORANGE | 2012-12-06 | 2:30P - 4:15P |  | MAIN LIFT STATION MCKINLEY ST | TRANSPORT SEWAGE TO PLANT | PUMP FAILURE | SET UP BYPASS PUMP AND WILL INSTALL SUBMERGIBLE PUMP UNTIL NEW LS
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2012-01-12 | 8:00A-8:00A (1/13) |  | JOSEPH INDUSTRY | FIELD, APP 1000 FT | RAIN 1.27 OF RAIN IN LAST 24 HR | WILL LET SITE DRY UP AND THEN CLEAN UP AND APPLY LIME TO AREA
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2012-01-23 | 10:00A-3:15P |  | JOSEPH INDUSTRY | FIELD,APP. 1000 | RAIN .72" | WILL LET SITE DRY UP THEN WE WILL CLEAN UP SITE, AND APPLY LIME TO AREA ALL PUMPS UP AND RUNNING
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2012-01-26 | 1:30P - 6:00P (1/27) |  | JOSEPH INDUSTRY 004 | LICK CREEK | RAIN .91" | ALL PUMPS RUNNING; WILL CLEAN AND LIME
IN0024023 | PAOLI MUNICIPAL STP | ORANGE | 2012-03-16 | 7:00 A -3:00P |  | JOSEPH INDUSTRY | FIELD,APP 1000 FT | RAIN 1.20" | WILL LET SITE DRY AND THEN CLEAN UP AND APPLY LIME TO AREA
IN0024449 | ROCKVILLE MUNICIPAL STP | PARKE | 2012-09-18 | 9:30A-9:44A | 3000 | FORCE MAIN FOR WASTE LINE TO DIGESTER | GROUND | WASTE LINE IS LEAKING. | VALVE WAS TURNED OFF AS QUICKLY AS POSSIBLE. AREA WAS HOSED DOWN WITH JET TRUCK AS BEST POSSIBLE.
IN0022449 | ROCKVILLE MUNICIPAL STP | PARKE | 2012-10-18 | 2:37P-3:20P | 16000 | SHELL L S SW CORNER OF 36 AND 41 HWY | GROUND TO STORM DRAIN | RELEASE WAS FROM MH NEXT TO LS NO DEBRIS OR SOLIDS EXITING MH WHEN OBSERVED SPILL FROM COLLECTION SYSTEM. | REPAIR WILL BE MADE AS SOON AS POSS. BOTH PUMPS WERE TUNED ON AND PUMPED LEVEL DOWN, THEN RAN ONE PUMP ON HAND CONTROL.
IN0062901 | CANNELTON, CITY OF | PERRY | 2012-07-22 | 11:00A - 11:30A | 300 | FORCE MAIN ON RIVER ROAD | GROUND | BROKEN FORCE MAIN | REPLACED BROKEN AREA
IN0021016 | TELL CITY MUNICIPAL STP | PERRY | 2012-07-19 |  | 1000 | BASEMENT IN THE 900 BLOCK OF 9TH AND 10TH ST | HOUSEHOLD BASEMENT | RAIN 1.3 VERY INTENSE RAIN CAUSED A HYDRAULIC OVERLOAD OF THE SYSTEM WHICH SEEMS TO BE SOMEWHAT RESTRICTED. | FLOWS WERE SHORT LIVED AND THE FLOW WENT BACK DOWN QUICK
INJ060801 | ARCELOR MITTAL/BURNS HARBOR | PORTER | 2012-11-13 | 11:25A - 12:10P | 500 | SANITARY PLANT INFLUENT | SANITARY PLANT EFFLUENT | SANITARY PNEUMATIC LIFT PUMP FAILED IN PRESSURIZED STATE | PUMP ISOLATED AND WILL BE REPLACED
| DAMON RUN CONSERVANCY DIST. | PORTER | 2012-10-31 |  |  | LS (PET HAVEN) WET WELL LOCATED ON U.S. HWY 6 WEST OF MERIDAN | UNKNOWN DITCH | AN OVER-TEMP ALARM SHUT DOWN THE LS PUMP CAUSING THE SURCHARGE. | OVER-TEMP ALARM WAS RESET & THE PUMP HAS OPERATED SINCE THEN.
IN0051446 | LAKE ELIZA CONSERVANCY DIST. | PORTER | 2012-05-09 |  |  | 81 SOUTH 500 WEST MH | GROUND | HIGH VOLUME OF FLOW FROM WASTEWATER LAGOON | EFFLUENT VALVE AT LAGOON CLOSED SOME TO DECREASE FLOW RATE
| PORT OF INDIANA | PORTER | 2012-04-09 | 8:00A-8:30A | 500 | 1190 E LOOP RD / LIFT STATION | STORM SEWER | PROBLEM WAS A STUCK FLOAT SWITCH ON LIFT STATION PUMP | RESPONDED AS SOON AS POSSIBLE TO RESET PUMPS TO REDUCE WATER LEVEL
IN0024368 | PORTAGE MUNICIPAL STP | PORTER | 2012-03-19 | 6:00A-6:30A | 5 | 6702 OLD PORTER ROAD | BASEMENT |  | OPENED BLOCKAGE @ THE MH BY JETTING W/ THE JETT TRUCK
IN0024368 | PORTAGE MUNICIPAL STP | PORTER | 2012-09-20 | 06:30-06:45 | 1000 | OXIDATION DITCH IN PLANT | GROUND | MIXED LIQUOR PUMP STATION FAILED TO START CAUSING OVERFLOW AT OXIDATION DITCH | THE MIXED LIQUOR WERE PLACED IN HAND OPERATION. CALLED TECHNICIAN.
IN0024368 | PORTAGE MUNICIPAL STP | PORTER | 2012-10-12 | 2:46P-3:46P | 600 | 7076 NOTTINGHAM ST M H | GROUND | JETTED LINE TO OPEN LINE, FOUND THAT LINE WAS PLUGGED W/PAPER TOWELS. | WILL FOLLOW UP W/ HOME OWNER'S IN AREA W/OUTREACH MATERIALS.
IN0031119 | SHOREWOOD FOREST UTILITIES | PORTER | 2012-09-27 |  | 500 | 425 UTILITY DRIVE FM | GROUND | FORCE MAIN FROM SHOP LS LEAKING | SHUT FM DOWN; WILL REPAIR LINE
INJO46949 | TOWN OF PORTER | PORTER | 2012-07-19 | 12:20A-1:20A | 20000 | PORTER AVE LIFT STATION | LITTLE CALUMET RIVER | POWER FAILURE, EQUIPMENT FAILURE, RAIN 2.94 | TOWN OF PORTERS VAC TRUCK ON SITE 4 LOADS TO HELP LIFT STATION KEEP UP
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-01-12 | 12:00A - 10:45A | 25 | 1104 KENTUCKY | BASEMENT SHOWER DRAIN | BLOCKAGE IN PRIVATE LINE | PLUMBER REMOVED
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-01-17 | 10:48A-11:00A | 50 | BASEMENT 412 MILTON ST | BASEMENT | OVERFLOW | VCU WRD SEWER DEPT CLEANED THE CITY SANITARY/STORM SEWER COMBO
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-01-18 | 10:38A-11:00A | 100 | FLOOR DRAINS 1101 GLENDALE BLVD | FLOOR | PRIVATE SANITARY OFFICE MGR FOR THE GLENDALE MEDICAL CLINIC STATED | VCU WRD SEWER DEPT CLEANED THE CITY SANITARY SEWER MAIN WITHIN ETC
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-02-13 | 9:59A-10:45A | 5 | 506 LAFAYETTE ST BASEMENT | BASEMENT | PRIVATE SANITARY THE HOMEOWNER STATED IN THE ORIGINAL SEWER CALL TO THE VCU-WRD SEWER DEPT THAT THERE WAS SEWER WATER STANDING AROUND THE BASEMENT FLOOR DRAIN WITHIN THE RESIDENCE LOCATED @ 506 LAF ST | CLEANED THE CITY SANITARY SEWER MAIN WITHIN THE ROAD DIRECTLY NORTH OF THE RESIDENCE LOCATED
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-02-23 | 11:17A-11:45A | 5 | 2101 DUNWOODY BASEMENT | BASEMENT | RAIN .03" THE HOMEOWNER STATED IN THE ORIGINAL TELEPHONE SEWER CALL TO THE VCU-WRD SEWER DEPT THAT A SEWAGE BACKUP IN THE BASEMENT FLOOR DRAIN WAS OCCURRING WHILE SHE WAS USING THE WASH MACHINE ETC | CLEANED THE CITY SANITARY SEWER MAIN WITHIN THE ROAD DIRECTLY IN FRONT OF THE RESIDENCE LOCATED @ 2101 DUNWOODY DR
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-02-25 | 4:00A-5:00A | 5 | 1807 PEACHTREE DR | BASEMENT | PRIVATE SANITARY SEWER | SEWER DEPT CLEANED THE CITY SANITARY SEWER MAIN WITHIN THE ROAD DIRECTLY IN FRONT OF THE RESIDENCE LOCATED @ 1807 PEACHTREE,
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-02-28 | 8:51A-10:00A | 75 | MH LIFT STATION, FORCE MAIN, ETC | BASEMENT FLOOR DRAIN WITH THE RESIDENCE | CITY SANITARY SEWER MAIN BLOCKAGE/OBSTRUCTION | CLEANED THE CITY SANITARY SEWER UNDER THE GRASS/LAWN
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-03-10 | 2:50P-4:00P | 10 | 1506 CHESAPEAKE PARK DR | BASEMENT | NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-03-23 | 8:33P-10:15P | 400 | 809 WOOD ST BASEMENT | BASEMENT FLOOR DRAIN | RAIN 0.21" | CLEANED THE CITY SANITARY/STORM SEWER COMBINATION MAIN LOCATED IN THE GRASS DIRECTLY
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-03-29 | 7:35P-8:20P | 25 | 1006 INSTITUTE ST | INSTITUTE ST | PRIVATE SANITARY | NO BLOCKAGE FOUND. HOMEOWNER WILL CAL PLUMBER,
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-04-04 | 4:10P-5:00P | 100 | PRIVATE SANITARY SEWER SERVICE LINE CLEAN | BONTLEY'S TOWING GRAVEL PARKING LOT LOCATION | PRIVATE SANITARY | REMOVED 400 GALLONS OF WASTEWATER. OWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-04-26 | 7:15P - 8:15P | 100 | 1007 ELM ST. BASEMENT | BASEMENT | NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-05-07 | 7:00A-8:00A | 50 | 832 LINCOLNWAY | BASEMENT | RAIN 1.14" | NO BLOCKAGE FOUND; HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-05-07 | 8:30A-9:30A | 10 | 1012 ELMHURST AVE | BASEMENT | RAIN 1.13" | NO BLOCKAGE FOUND; HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-05-10 | 3:00P-4:30P | 100 | 1702 NAPOLEAN ST | BASEMENT | PRIVATE SANITARY | NO BLOCKAGE FOUND; HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-05-11 | 2:30P-3:30P | 10 | 50 MARKS RD | BATHROOM FLOOR DRAIN | PRIVATE SANITARY SEWER | NO BLOCKAGE FOUND; HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-05-16 | 10:45A - 11:15A | 10 | 203 JEFFERSON ST BASEMENT | BASEMENT | NO OBSTRUCTION FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-05-29 | 11:00A - 11:30A | 30 | 813 WOOD ST BASEMENT | BASEMENT | NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-06-16 | 5:10P - 5:45P | 100 | 1509 WASHINGTON ST | BASEMENT SHOWER DRAIN | RAIN .01" NO BLOCKAGE FOUND | PLUMBER COULD NOT FIND BLOCKAGE IN LATERAL
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-06-18 | 8:48A - 9:15A | 3 | 1706 BEECH ST | BATHTUB DRAIN | NO BLOCKAGE FOUND | WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-06-30 | 9:00A - 9:50A | 4 | 2205 LINDEN DR | BASEMENT | RAIN .15" NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-07-25 | 1:15P - 1:30P | 3 | CITY HALL | BATHROOM | BLOCKAGE WITHIN INTERNAL BUILDING LINES | CALLED PLUMBER
IN0024600 | VALPARAISO MUNICIPAL STP | PORTER | 2012-07-29 | 7:00P - 8:30P | 10 | 2001 ARROW LEAF DR. | BATHROOM FLOOR | NO BLOCKAGE FOUND | HOMEOWNER WILL CLEAN HOME'S SANITARY SEWER LINE
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-08-04 | 6:00P - 7:30P | 30 | BATHTUB DRAIN | BATHTUB | NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER TO CLEAN SANITARY LINE
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-08-13 |  |  | FLOOR DRAIN WITHIN THE LAUNDRY ROOM @ the residence | FLOOR DRAIN | PRIVATE SANITARY | THE VCU WRD SEWER DEPT CLEANED THE CITY SANITARY/STORM
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-09-17 | 8:20A - 10:00A | 5 | KITCHEN SINK 1903 CHICAGO ST. | SINK | NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-09-29 | 8:30P - 9:30P | 10 | BASEMENT FLOOR DRAIN 401 ERIE ST. | BASEMENT | DID NOT FIND BLOCKAGE | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-01 |  | 5 | BASEMENT UTILITY SINK 3 LOGAN ST. | SINK | DID NOT FIND BLOCKAGE | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-02 | 12:30P - 12:50P | 25 | ACCESS MH FOR TRIPLE BASIN SEPARATOR | GROUND | MH IS ACCESS POINT INTO FIRE DEPARTMENT'S OIL AND GREASE SEPARATOR | CLEANED MH; DEPT WILL SCHEDULE CLEANING
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-02 | ? - 2:05P |  | 1708 WHITTIER PARK | RESIDENCE | ROOTS IN HOME'S LATERAL | REMOVED BY HOMEOWNER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-02 | 9:00P - 9:40P | 50 | BATHTUB DRAIN 203 FAIR ST. | BATHTUB | DID NOT FIND BLOCKAGE | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-08 |  | 5 | 1002 CHICAGO ST. | APARTMENT | NO BLOCKAGE FOUND | LANDLORD WILL CALL PLUBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-10 | 10:15P-11:00P | 5 | THE BASEMENT FL DRAIN 1803 ROCK CASTLE PARK | BASEMENT | NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-11 | 1:30A-2:25A | 1 | THE BASEMENT FL DRAIN 206 MORGAN BLVD | BASEMENT | NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-17 | 3:45P - 4:45P | 5 | 405 COURTNEY ST | BASEMENT | CITY CLEANED SEWER; NO BLOCKAGE FOUND | HOMEOWNER WILL CLEAN HOME'S SANITARY LINE
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-19 | 11:00A - 12:00P | 5 | 3 HARRISON BLVD | BASEMENT FLOOR DRAIN | NO BLOCKAGE IN CITY SEWER | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-10-27 | 12:15P - 1:10P | 7 | BASEMENT FLOOR DRAIN | BASEMENT FLOOR | CLEANED SEWER MAIN. NO BLOCKAGE FOUND. | WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-02 | 9:30A - 10:45A | 2 | GARAGE FLOOR DRAIN | GARAGE FLOOR | TELEVISED SEWER MAIN AND DID NOT FIND BLOCKAGE | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-11 | 12:00P - 8:30P | 5 | 205 CAMPBELL BASEMENT | FLOOR DRAIN | NO BLOCKAGE IN MAIN | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-12 | 6:30A - 7:30A | 5 | 1114 FRANKLIN ST BASEMENT | FLOOR DRAIN | NO BLOCKAGE IN MAIN | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-15 | 11:00A - 12:00P | 1 | 551 BOUNDARY ST BASEMENT | FLOOR DRAIN | NO BLOCKAGE IN MAIN | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-18 | 7:10P - 7:50P | 75 | FLOOR DRAINS 1084 LINWOOD | FLOOR | FAILED LIFT STATION | PUMPED DOWN WET WELL AND REPLACED FAULTY COMPRESSOR
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-23 |  | 10 | BASEMENT FLOOR DRAIN 401 MILTON | BASEMENT | RAIN .5" CLEANED SEWER MAIN AND DID NOT FIND OBSTRUCTION | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-26 | 11:50A - 1:30P | 5 | BASEMENT FLOOR DRAIN 507 MONROE ST. | BASEMENT | CLEANED SEWER MAIN AND DID NOT FIND OBSTRUCTION | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-27 | 4:45P - 6:00P | 2 | SANITARY CLEANOUT OUTSIDE 8 LOCUST ST. | GROUND | NO CAP ON OUTSIDE CLEANOUT; NO BLOCKAGE FOUND | HOMEOWNER WILL CALL PLUMBER AND REPLACE CAP
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-11-27 | 7:10A - 7:30A | 1 | BASEMENT FLOOR DRAIN 4201 HEMLOCK | BASEMENT | CLEANED SEWER MAIN AND DID NOT FIND OBSTRUCTION | HOMEOWNER WILL WATCH DRAIN
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-12-05 | 11:34A - 12:05P |  | 1202 CARRSBROOKE DR. | FLOOR DRAIN | NO BLOCKAGE IN CITY MAIN; BLOCKAGE IN PRIVATE SANITARY | BLOCKAGE REMOVED
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-12-11 | 11:00A - 2:00P | 15000 | PRIVATE SANITARY LINE MH BEHIND PORTER COUNTY JAIL | GROUND | DEBRIS IN 8" LINE | JET RODDED LINE
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-12-12 | 8:00A - 1:00P | 1000 | PRIVATE SANITARY SERVICE LINE CLEANOUT MH BEHIND PORTER COUNTY JAIL | GROUND | DEBRIS AND STUCK JET RODDER HOSE FROM PREVIOUS DAY | REMOVED DEBRIS, FLUSHED AREA
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-12-24 | 11:00A - 1:00P | 10 | 1068 JOLIET | BASEMENT | CLEANED SEWER MAIN AND DID NOT FIND OBSTRUCTION | HOMEOWNER WILL CALL PLUMBER
IN0024660 | VALPARAISO MUNICIPAL STP | PORTER | 2012-12-27 | 9:52A - 10:10A | 10 | 1107 NAPOLEON | BASEMENT | CLEANED SEWER MAIN AND DID NOT FIND OBSTRUCTION | HOMEOWNER WILL CALL PLUMBER
IN0052191 | A.B. BROWN STATION | POSEY | 2012-06-24 | 3:30A - 11:30A (6/24) |  | #1 COOLING TOWER OVERFLOW | GROUND | AIR LEAK CAUSED VALVE TO FAIL TO OPEN RESULTING IN SUMP OVERFLOW | THROTTLED REGULATOR TO REDUCE FLOW AND COMPLETED REPAIRS
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2012-06-03 | 11:15A-6:20A | 293760 | MT VERNON WWTP | OHIO RIVER | POSSIBLE POWER SURGE | PROJECT UNDERWAY FOR TELEMETRY SYSTEM
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2012-09-17 | 4:15P-8:15P | 4476 | E & S HOUSING L. S. | MCFADDIN CREEK | RAIN 2.3" | STUDYING I&I
IN0035696 | MOUNT VERNON MUNICIPAL STP | POSEY | 2012-09-18 | 7:00A - 8:00A | 83300 | MT VERNON WWTP | GROUND | RAIN 2.3" PLANT HYDRAULICALLY OVERLOADED; FLOW TO AERATION TRAIN #2 | KEIFER BROTHERS CHANGED SPLITTER BOX TO DIRECT FLOW BACK TO AERATION TRAIN #1
IN0052191 | SIGECO, A. B. BROWN STATION | POSEY | 2012-08-02 | 10:36P - 11:53P |  | COAL PILE/SOUTH SIDE RUN OFF POND | UNNAMED TRIBUTARY | RAIN 2.31"
IN0045527 | CLEAR CREEK CONSERVANCY DISTRICT | PUTNAM | 2012-10-14 | 1:00P-3:00P | 1000 | V-Z L S | GROUND | HI WATER ALARM FLOAT DID NOT WORK PROPERLY | CHANGE FLOAT SWITCH
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-01-17 | 10:48A-12:50P | 12000 | M H W-65 | RABBIT RUN CREEK | ROOTS, RAIN 1.2" 8" CLAY TILE MAIN HAD BLOCKAGE | WILL JET LINE EVERY THREE MONTHS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-01-17 |  |  | MH D-2 | DOE CREEK | RAIN 1.2 JASON PALIN STOPPED BY THE WWTP TODAY WITH A COMPLIANT FROM A CITIZEN THAT ON OR AROUND 1/17/12 | TOWN RECEIVED $600,000 GRANT IN DEC 2010 TO REPLACE THIS LIFT STATION
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-01-18 | 4:00P-4:32P | 500 | MH A-18 STARDUST HILLS | GROUND | CONSTRUCTION RELATED ROOTS 8" SEWER LINE HAD BLOCKAGE IN LINE DUE TO ROOTS. JETTED FROM MH A-48 TO MH A-49 | PUT ON SCHEDULE TO BE JETTED EVERY THREE MONTHS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-01-26 | 9:15A - 1:00P | 4500 | MH D-2 LS 4 | DOE CREEK | RAIN 1.1" | REPLACING LS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-02-03 | 3:15P-3:45P | 25 | MH W-77 | GROUND/ BLKTOP | 8" SEWER LINE HAD BLOCKAGE FROM MH W-77 TO MH W-76 | SCHEDULE REGULAR CLEANING FOR LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-02-22 | 3:00P-3:10P | 300 | MH D-65 | GROUND | TREE ROOTS IN MAIN | JETTING LINE
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-04-04 | 10:41A-3:18P | 150000 | LIFT STATION # 4 MH D-2 | DOE CREEK | EQUIPMENT FAILURE, RAIN 0.5 LIFT STATION # 4 PUMP # 2 SHORTED OUT & MELTED ALL THE WIRES.
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-05-14 |  | 825 | OUTFALL 001 | RABBIT RUN | WORKER TURNED WRONG VALVE WHILE CLEANING | INSPECTED CREEK
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-06-05 | 11:46A-12:20P |  | LIFT STATION #4 D-2 MH | DOE CREEK | EQUIPMENT FAILURE INTAKES BLOCKED WITH DEBRIS | NONE APPARENT
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-08-22 | 7:40A-7:50A | 600 | LIFT STATION # 4 MH D-2 | DOE CREEK | DEBRIS | FLUSHED PUMPS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-08-23 | 7:45A-8:00A | 500 | LIFT STATION #4 MH D-2 | DOE CREEK | PUMPS AIR LOCKED | ADJUSTED FLOATS
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-09-10 | 2:58P-11:30A | 5 | DOE CREEK LIFT STATION | GROUND IN PAVEMENT | 6" FORCE MAIN HAD A VERY SMALL CRACK IN LINE THAT WAS SEEPING PUT REPAIR CLAMP ON IT
IN0022616 | CLOVERDALE MUNICIPAL STP | PUTNAM | 2012-10-10 | 4:00P-9:00A | 96000 | L S #4 MH D-2 | DOE CREEK | WATER LEVEL WENT BELOW INTAKES & AIRLOCKED THE PUMPS | WILL CHECK WET WELL LEVEL BEFORE CHECKING PUMPS
IN0022132 | GREENCASTLE MUNICIPAL STP | PUTNAM | 2012-01-23 | 04:55A - 06:10A | 10000 | CORNSTALK LIFT STATION | STREAM BESIDE L.S. | POWER FAILURE | CLEANED UP DEBRIS & APPLIED A BLEACH SOLUTION TO AFFECTED AREA
| HERITAGE LAKE POA | PUTNAM | 2012-09-11 | 8:30A-9:15A | 100 | LIFT STATION | GROUND | LIFT STATION PUMPED OUT. FLOAT SWITCH FIXED | LIFT STATION PUMPED OUT WITHIN 40 MIN OF LEAK.
IN0039624 | VAN BIBBER LAKE CD | PUTNAM | 2012-06-11 | 6:00P-8:00P |  | CLEAN OUT LOT 3012 | STREET | CONSTRUCTION RELATED 8" SEWER PLUGGED UP. HAD TO HIRE JET TRUCK TO CLEAN SEWER LINE | SPRAY SPILL WITH BLEACH
IN0041173 | FAIRVIEW ACRES MHP | RANDOLPH | 2012-05-12 |  |  | CLEANOUT PIPE | GROUND | COLLECTION SYSTEM LINE WAS OBSTRUCTED CAUSING SYSTEM TO BACK UP INTO FINGERS OF SYSTEM AND OUT OF A CLEANOUT | JETTED LINE AND CLEANED AREA
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2012-01-17 | 6:00A - 11:00A (1/18) | 75000 | OUTFALL #002 | ARBOGAST DITCH | RAIN .87" | ADJUST PUMPS FOR MAXIMUM FLOW
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2012-01-18 | 6:00A- |  | OUTFALL #002 | ACBOGAST DITCH | RAIN AFTER 2" SNOW MELT | ADJUST PUMPS FOR MAXIMUM FLOW
IN0020729 | PARKER CITY MUNICIPAL STP | RANDOLPH | 2012-01-23 | A- 4:00P (1/24) | 50000 | OUTFALL 002 | ARBOGAST DITCH | RAIN .35" | ADJUST PUMPS FOR MAXIMUM FLOW
IN0020982 | UNION CITY MUNICIPAL STP | RANDOLPH | 2012-09-07 | 10:55P-9:40A | 540000 | JACKSON PIKE LIFT STATION | LITTLE MISSISSINEWA RIVER | RAIN 3.1 DIVERTED NORTH INLET FLOW TO POND # 1 PUMP @ JACKSON LIFT KEPT SHUTTING DOWN
IN0023779 | MILAN MUNICIPAL STP | RIPLEY | 2012-01-17 | 9:00A-11:00A | 6000 | MANHOLE#16A#17,#118 LIFT STATION GRADE SCHOOL | STREAM | RAIN 2.5" | I WAS PUMPING INTO OUR HOLDING TANKS W/2-3 TRASH PUMPS TO ACCOMMODATE MORE FLOW @ PLANT STROM MODE
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2012-01-17 | 9:45A-3:30P | 50000 | HEADWORKS | DOWN HILL TO TRIBUTARY OF PLUM CK | RAIN 3.2" | MAXIMIZE FLOW
IN0021695 | OSGOOD MUNICIPAL STP | RIPLEY | 2012-01-26 | 9:15P - 11:30P | 20000 | HEADWORKS | DOWN HILL TO TRIB OF PLUM CREEK | RAIN 2" | PUSHED AS MUCH FLOW THROUGH PLANT AS POSSIBLE
IN0024937 | CARTHAGE MUNICIPAL STP | RUSH | 2012-08-08 | 11:30A - 12:30P |  | MH 704 N MAIN ST | GROUND | OVERFLOW LINE FOUR FEET DOWN FROM TOP OF MH | JETTED LINE; LIMED AREA; CAP OVERFLOW LINE
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2012-01-17 | 7:00A-3:30P | 4000 | 191,457,97,97A,105 | GROUND | RAIN 0.9 HEAVY RAINFALL
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2012-04-17 | 7:00A-? | 300 | MH | GROUND | MANHOLE STOPPED UP WITH GREASE | PURCHASED SEWER JETTER CLEANED OUT LINE
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2012-05-06 | 7:00A-4:00P | 3000 | MH 191,457,97,97A,105 | GROUND | RAIN 2.3" | WORKING ON GETTING MONEY TO REPAIR COLLECTION SYSTEM
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2012-10-16 | 4:30P-5:30P | 300 | 352 MH | GROUND & STICK DITCH | PEPSI HAD A BROKEN VALVE & RELEASED 4500 GAL OF SYRUP INTO SEWER. AND OUR L S WOULD NOT HANDLE IT. | WORKING ON GETTING MONEY TO REDO COLLECTION SYSTEM.
IN0025135 | AUSTIN MUNICIPAL STP | SCOTT | 2012-12-09 | 7:00-7:00 | 300 | 97A 112 105 | GROUND, & STICK DITCH | RAIN 1.3 TOO MUCH RAIN L S WON'T HANDLE | WORKING ON GRANT TOO PUT IN ANOTHER FORCE MAIN ON MAIN L S
IN0021911 | MORGAN FOODS, INC. | SCOTT | 2012-01-11 |  | 300000 | WASTEWATER LAGOON | PERMITTED OUTFALL 001 | RAIN .3" | BLENDED WITH FINAL EFFLUENT AND SAMPLED
IN0021911 | MORGAN FOODS, INC. | SCOTT | 2012-01-17 |  | 600000 | MORGAN FOODS WASTEWATER LAGOON | PERMITTED OUTFALL 001 | RAIN 1.0 | NO DAMAGE OR ADVERSE EFFECTS HAVE BEEN OBSERVED. ACCORDANCE W/OUR NPDES PERMIT
IN0021911 | MORGAN FOODS, INC. | SCOTT | 2012-01-23 |  | 300000 | MORGAN FOODS' WASTEWATER LAGOON | PERMITTED OUTFALL 001 | RAIN 1.0" | NO DAMAGE OR ADVERSE EFFECTS HAVE BEEN OBSERVED. SAMPLES WERE COLLECTED @ OUTFALL
IN0032867 | SHELBYVILLE MUNICIPAL STP | SHELBY | 2012-08-26 | 6:00P-8:15AM | 1500 | FAIRLAND ROAD LIFT STATION | GROUND | EQUIPMENT FAILURE GUARD DOG MONITOR SHOWED PUMP RUN SUNDAY BUT LOW. PLANT FOREMAN FOUND POWER OFF TO CONTROLLER. TURNED PUMP ON HAND | USED VACTOR SEWER TRUCK TO CLEAN UP SPILLAGE AND WASH DOWN DITCH. INSPECTED HANKINS DITCH NEARBY WITH NO SIGNS OF WASTE REACHING IT
IN0061662 | ROCKPORT NORTH | SPENCER | 2012-03-01 | 7:00A-11:20A | 500 | LIFT STATION BASE ROAD | GROUND | EQUIPMENT FAILURE NOT SURE WHEN OVERFLOW STARTED BUT THE FLOW AT THE PLANT WAS ACTUALLY MORE THAN THE PREVIOUS DAY OVERFLOW FROM STATION DISCOVERED | CLEANED UP OVERFLOW AND WILL HAVE THE ELECTRICIAN DIAGNOSE THE PROBLEM WHEN HE ARRIVES BACK TO TOWN IN THE MEANTIME WE WILL CONTINUE TO MONITOR THE STATION
IN0061662 | ROCKPORT NORTH POTW | SPENCER | 2012-03-20 | 8:30A-9:00A | 500 | LIFT STATION ON BASE ROAD | GROUND | HAD A PROBLEM W/THIS LIFT STATION ON 3/1/12 & REPORTED ON OVERFLOW. FOUND THE LAG FLOAT WAS BAD & CALLING IN BOTH PUMPS. | CONTINUED MONITORING OF FLOAT SYSTEMS
IN0061662 | ROCKPORT NORTH POTW | SPENCER | 2012-11-02 | ?-7:30A | 500 | L S ON BASE ROAD | GROUND | FLOAT TANGLE | PUMPED STATION DOWN, FREED FLOAT, CLEANED CONCRETE LID WHERE OVERFLOW OCCURRED.
IN0061662 | ROCKPORT NORTH POTW | SPENCER | 2012-12-19 |  | 4000 | FORCE MAIN 231 AND 500 NORTH | GROUND | FARMERS REPLACING FIELD TILES HIT FM | WILL REPAIR
IN0021067 | ROCKPORT SOUTH | SPENCER | 2012-06-05 |  | 30000 | DIGESTER AT SOUTH TREATMENT PLANT | GROUND | SENDING CHLORINE CONTACT TANK WASTE BACK TO DIGESTER VALVE WAS LEFT OPEN FLOODED DIGESTER | VALVE CLOSED. GROUND CLEANED UP.
IN0021067 | ROCKPORT SOUTH | SPENCER | 2012-08-02 | 2:30A - 10:30A | 60000 | CSO PIPE | OHIO RIVER | RAIN 3.1" LOST POWER | REPLACED TRANSFORMER
IN0021067 | ROCKPORT SOUTH | SPENCER | 2012-11-20 | 12:00P-? | 20000 | 4TH ST FORCE MAIN | GROUND AND STORM DRAIN DITCH | BREAK IN FORCE MAIN. CREWS STARTED DIGGING TO REPAIR AS SOON AS THEY ARRIVED THIS MORNING & WERE INFO BY STREET DEPT. | LINE WILL BE REPAIRED. SAND BAGS WERE USED TO STOP FLOW FROM GOING INTO STORM DRAIN.
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2012-03-08 | 10:00A - 3:30P | 5000 | MH #15 LS #8 | GROUND | RAIN .95" | MONITORING SITUATION; REPAIRS SLATED FOR 2012
IN0020605 | SANTA CLAUS MUNICIPAL STP | SPENCER | 2012-05-01 | 2:00P-2:30P |  | #4 LIFT STATION | GROUND | RAIN .6" ENERGY PROVIDER HAD BLOWN FUSE AT TRANSFORMER CONTACTED VECTREN AND THEY REPLACE FUSE ONCE THAT WAS DONE THE STATION PUMPED DOWN. EVERYTHING IN WORKING ORDER | MAKING SURE LIFT STATIONS ARE RUNNING AND PUMPING KEEPING CLOSE EYE ON THEM
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-03-06 | 8:21A-? |  | 429 DITTMAN ST | BASEMENT BACKUP | ROOTS | REMOVED BLOCKAGE
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-04-05 |  |  | BASEMENT | BASEMENT | LATERAL SEWER BORED THROUGH BY ELECTRIC DEPARTMENT | FIXED LINE. ELECTRIC COMPANY RESPONSIBLE FOR COST
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-07-26 |  |  | 515 W 12TH ST | BASEMENT | RAIN 1.93"
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-07-27 | 5:08P-6:50P | 2000 | MIDDLEBORO LIFT STATION | ST JOSEPH RIVER | RAIN >2" WET WELL AT LIFT STATION OVERLOADED WITH SAND AND GRIT DUE TO COLLAPSED INCOMING SEWER LINE | WET WELL TO BE MANUALLY CLEANED OUT OF DEBRIS AND TO BE PUT BACK IN SERVICE AS QUICKLY AS POSSIBLE
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-07-31 |  |  | 718 W 7TH ST. | BASEMENT | RAIN | INSPECTING AFFECTED SEWER MAINS
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-08-04 |  |  | BASEMENT DRAIN | BASEMENT | RAIN
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-08-04 |  |  | MH 19 | GROUND | RAIN 2.76" | THE SEWER DEPT CLEANED & DISINFECTED THE AREA
IN0025640 | MISHAWAKA MUNICIPAL STP | ST JOSEPH | 2012-12-13 | 1:07P - 2:00P |  | 1305 CHARLOTTE | BASEMENT | GREASE | VACUUMED MAIN
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-01-04 | ? - 12:30P (1/6) |  | MAIN LINE | 3821 BRENTWOOD BASEMENT | MAIN LINE CAVED IN | REPAIRING LINE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-02-09 |  |  | CHLORINATION AND DECHLORINATION |  | PRE-APPROVED ANTICIPATED BYPASS FOR FACILITY IMPROVEMENTS
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-02-24 | 12:45P-5:10P |  | MAIN LINE | BASEMENT | NO DAMAGE REPORTED | JETRODDER NUMBER 488 OPENED THE BLOCKAGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-02-28 | 2:00P-3:15P |  | MANHOLE | STREET AT 116 BARTLET ST | NO HOME OR BUSINESS BACK UP | JETRODDER 469 OPENED THE BLOCKAGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-03-12 | 9:40A-10:55A |  | MAIN LINE ON | BASEMENT |  | JET RODDER NUMBER 488 OPENED OUR MAIN LINE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-04-15 | 11:45A-1:00P |  | MH ON SOUTHBROOK | STREET | CLOG IN LINE | JET RODDER NUMBER 488 OPENED OUR MAIN LINE AND CLEANED UP ALL SEWAGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-04-18 | 1:30A-4:30A | 90000 | LIFT STATION | ST JOSEPH RIVER | POWER FAILURE A CAR STRUCK NEARBY POWER POLE AND TOOK THE POLE AND POWER OUT | GENERATOR OPERATED PUMPS UNTIL POWER WAS RESTORED
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-05-12 | 7:10P-9:00P |  | MH IN THE 100 BK OF WEST PENDLE ST | STREET | BLOCKAGE IN LINE | JETRODDER # 488 OPENED THE BLOCKAGE AND CLEANED UP ALL SEWAGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-05-20 | 5:30P-3:30P |  | MAIN SEWER LINE | BASEMENT @ 1006 VASSAR AVE | BLOCKED MH WHICH HAD BEEN ASPHALTED OVER | MANHOLE & SEWER LINE LOCATED. MANHOLE WILL BE RAISED TO STREET LEVEL MH & SEWER LINE WILL BE PUT ON OUR GIS & PRINTED MAPS
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-14 | 10:00P-? |  | MAINLINE | BASEMENT 806 SHERIDAN | HEAVY RAIN 2"-5"
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-14 | 9:00P-? |  | MAINLINE | BASEMENT 3022 SUNNYMEDE | HEAVY RAIN 2"-5"
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-14 | 7:00P-? |  | MAINLINE | 728 SHERIDAN BASEMENT | HEAVY RAIN 2" TO 5"
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-15 | 7:15P-? |  | MAINLINE | BASEMENT | HEAVY RAIN 2"-5"
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-19 | 4:00A-5:00A | 12000 | CSO 39/27TH ST LIFT STATION | ST JOSEPH RIVER | RAIN 1.9 | LIFT STATION DISCHARGE MH CASTING WAS DAMAGE DURING CONSTRUCTION. PUMP DISCHARGE AND SEWER GRAVITY FLOWS CAUSED SURCHARGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-19 | 7:15AM-9:50A | 8000 | INTERSECTION OF MICHIGAN & RIVERSIDE | ST JOSEPH RIVER | RAIN 1.6 LIFT STATION WAS SURCHARGED OVER CAPACITY
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-23 | 4:01P-4:23P |  | MAIN LINE | STREET |  | JETRODDER 488 OPENED THE BLOCKAGE
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-26 | 9:53P-? |  | MAIN LINE | BASEMENT 1941 E DONALD ST | HEAVY RAIN
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-26 |  |  | MAIN LINE | BASEMENT 3022 SUNNYMEDE AVE | HEAVY RAIN
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-26 | 10:20P-? |  | MAIN LINE | BASEMENT | HEAVY RAIN
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-26 | 9:20P-? |  | MAIN LINE | BASEMENT 1343 CORRY ST | HEAVY RAIN
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-26 | 10:20P-? |  | MAIN LINE | BASEMENT 1945 E DONALD ST | HEAVY RAIN
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-07-27 |  |  | MAIN LINE | BASEMENT | HEAVY RAIN
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-08-04 | 5:00P-5:30P | 6000 | CSO 039/27TH ST LIFT STATION | ST JOSEPH RIVER | RAIN 0.69" | BROKEN MH CASTING THAT ALLOWED DISCHARGE WAS REPLACED THE AFTERNOON OF 8/6/12
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-10-21 | 7:45P-9:00P | 15 | MH | GROUND AT 3032 BOYNTON AVE | BLOCKAGE IN MH | JET RODDER NUMBER 488 OPENED THE BLOCKAGE.
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-12-19 | 12:04P-12:58P |  | MAIN LINE | FL @ 1909 SWYGART AVE | ROOTS | JET RODDER NUMBER 466 OPENED OUR MAIN LINE.
IN0024520 | SOUTH BEND MUNICIPAL STP | ST JOSEPH | 2012-12-21 | 4:40P-6:55P |  | MAIN LINE | BASEMENT AT 18487 CYPRESS CR | OBSTRUCTION | JETRODDER NUMBER 466 OPENED OUR MAIN LINE
IN0063606 | KOONTZ LAKE REGIONAL SEWER DIST | STARKE | 2012-10-04 | 6:00A-10:00A | 5 | LATERAL LINE BEFORE GRINDER STATION 7849 N TOPINABEE ST | BATH TUB & FL OF BATHROOM | CONSTRUCTION RELATED | BATHROOM CLEANED, LATERAL LINE CHECKED TO BE CERTAIN IT IS OPEN CHECKED GRINDER STATION THOROUGHLY CYCLED PUMPS & CHECKED ALARMS
IN0063606 | KOONTZ LAKE REGIONAL SEWER DISTRICT | STARKE | 2012-03-22 | 7:15P-8:00P | 500 | AIR RELEASE VALVE MH @8501 TIPPECANOE ST | GROUND | MH WAS PUMPED OUT BY PUMPER TRUCK AND HAND VALVE WAS DISCOVERED TO BE PARTIALLY OPEN CAUSING THE RELEASE, VALVE WAS CLOSED IMMEDIATELY & ALL VALVES IN MH | MANHOLE WAS PUMPED OUT IMMEDIATELY AND DISPOSED OF BY SEPTIC HAULER. LIQUID THAT WAS RELEASED RAN TO A SODDED AREA AND WAS NOT VISIBLE.
IN0063606 | KOONTZ LAKE REGIONAL SEWER DISTRICT | STARKE | 2012-03-27 | 12:00P-4:30P | 1000 | LEAK IN THE LINE @ 7720 TECUMSEH ST | LIQUID RAN TO SODDED AREA | CONSTRUCTION RELATED NEW LINE/APPARENTLY A BAD CONNECTING JOINT IN LINE | WHEN NOTIFIED & ASSESSED WHAT NEEDED TO BE DONE CALLED CONTRACTOR TO IMMEDIATELY EXCAVATE & REPAIR LEAK
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2012-03-15 | 17:15-19:05 | 112485 | CSO # 4 | UNNAMED DITCH TO PINE CREEK | RAIN 1.54" PLANT AND CSC FACILITY WERE IN OPERATION @ FULL SPEED | RESEARCHING REMOVAL OF STORM DRAINS FROM SANITARY ON FRANKLIN ST
IN0020877 | NORTH JUDSON MUNICIPAL STP | STARKE | 2012-06-16 | 21:30-2150 | 2831.939 | CSO # 004 | UNNAMED DITCH TO PINE CREEK | RAIN 1.25" | PLANT AND CSO FACILITY WERE IN OPERATION AT FULL SPEED
| ANGOLA GARDENS | STEUBEN | 2012-04-27 | 4/30 | 55000 | LS 425 S SHOUP ST. | GROUND | EQUIPMENT FAILURE; TRIPPED BREAKER | RESET AND REPLACED BREAKER
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2012-08-27 | 2:00P - 4:00P | 50 | FORCE MAIN | FM SERVING TRI-STATE LS | BROKEN CLEAN OUT CAP GOT STUCK IN FM AND CRACKED FM | REMOVED OBSTRUCTION AND WILL REPLACE FM
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2012-11-19 | 7:30A - 10:45A | 2500 | MULTIPLE SITES ON HIRES LS SEWER SHED | GROUND | POSSIBLE TRANSDUCER MALFUNCTION. | PUT BOTH PUMPS ON HAND POSITION AND INSTALLED BACK UP HIGH LEVEL FLOAT
IN0021296 | ANGOLA MUNICIPAL STP | STEUBEN | 2012-11-20 | 9:00A - 9:15A | 2000 | AIR RELIEF MH @ 1901 NORTH WAYNE ST. | GROUND | CORRODED PIPE NIPPLE BETWEEN THE ISOLATION VALVE AND AIR RELIEF VALVE | CLEANED ALL LIQUID AND DEBRIS. REPLACING PIPING WITH STAINLESS STEEL
IN0050822 | HAMILTON LAKE C.D. | STEUBEN | 2012-06-24 | 4:30P - 5:30P | 400 | 280 LN 207A DISCHARGE LINE | GROUND | CONTRACTOR HIT PRESSURE DISCHARGE LINE WITH EXCAVATOR | PUMPED SEWAGE AND REPAIRED LINE
IN0050822 | HAMILTON LAKE C.D. | STEUBEN | 2012-07-16 | ? - 9:30A | 500 | 22-8 LOT 49 AT HAMILTON SHORES MHP | GROUND | HIGH WATER ALARM BUZZER TURNED OFF | REPAIRED STATION AND LIMED AREA
IN0060097 | REGION B | STEUBEN | 2012-08-03 | 12:15-3:00 | 1500 | MH | WOODED AREA | POWER FAILURE THE THREE PHASE POWER WENT OUT | PULLED OUT EMERGENCY GENERATOR
IN0061557 | STEUBEN LAKES RWD | STEUBEN | 2012-01-18 | 3:50P-7:45P |  | SOUTH OF 1420 N 900 W | GROUND | CONSTRUCTION - HIT 8" FORCE MAIN | COLLECTION SYSTEM CREW HAD VAC TRUCK& PUMPER TRUCK ON SITE
IN0021148 | FARMERSBURG MUNICIPAL STP | SULLIVAN | 2012-01-26 | 8:00A 12:00P | 10000 | CONTACT TANK | GROUND | RAIN 1.5" | SNAKED EFFLUENT LINE
IN0050296 | HOOSIER ENERGY REC, INC. | SULLIVAN | 2012-07-30 | 10:00A - 1:00P | 14600 | PLANT | GROUND | UPSET CAUSED CARRY OVER OF SOLIDS TO FILTERS AND OVERFLOWED LOWEST MH | CLEANED AREA AND BACKWASHED FILTERS
IN0020389 | SHELBURN MUNICIPAL STP | SULLIVAN | 2012-01-17 | 8:00A-1:00P | 10000 | MANHOLE | GROUND | RAIN 1.3 HI FLOW DUE TO PRECIPITATION | NONE AFTER RAIN STOPPED MANHOLE RECEDED
IN0020389 | SHELBURN MUNICIPAL STP | SULLIVAN | 2012-02-05 | 3:45P-4:15P | 1500 | LIFT STATION #1 | GROUND/DITCH | RAIN .5" THROTTLE LINKAGE HAD TO BE REPAIRED-LIFT STATION #1 IS CURRENTLY UNDER CONSTRUCTION | ONCE CONSTRUCTION IS COMPLETED THE LIFT STATION WILL BE ABLE TO HANDLE XTRA FLOW & ALL NEW COMPONENTS
IN0020389 | SHELBURN MUNICIPAL STP | SULLIVAN | 2012-02-18 | : |  | LIFT STATION | GROUND | HAD TO RESET PUMPS @ MAIN LIFT STATION | CHECK EVERYDAY/ GOING TO MAKE A PREVENTATIVE MAINT PROG
IN0020389 | SHELBURN MUNICIPAL STP | SULLIVAN | 2012-02-29 | 14:30-15:00 | 2000 | THOMAS ST LIFT STATION | STREAM NO NAME | EQUIPMENT FAILURE HAD TO RESET PUMPS | CLEANED UP AROUND LIFT STATION
IN0024554 | SULLIVAN MUNICIPAL STP | SULLIVAN | 2012-05-29 | 1500-8:30A | 2500 | MH | UNNAMED DITCH | LINE WAS PLUGGED IN WOODED AREA. JETTED LINE AND OPENED IT | CLEANED UP DEBRIS AROUND AREA DITCH IS DRIED OUT
IN0020036 | BATTLE GROUND WWTP | TIPPECANOE | 2012-05-06 | 8:00P-6:36P | 87120 | HAWKS NEST LIFT STATION | GROUND AROUND LIFT STATION | LIGHTING STRUCK LIFT STATION, KNOCKING OUT FUSE WHICH DID NOT ALLOW CONTROLS TO ENGAGE PUMPS | BATTLE GROUND TOWN EMPLOYEES GOING TO CLEAN AREA AND LIME
IN0020036 | BATTLEGROUND MUNICIPAL STP | TIPPECANOE | 2012-05-11 | 3:50A-7:21A | 20000 | WOODS EDGE LS FORCE MAIN | BURNETTS CREEK, NORTH FORK | FORCE MAIN PIPE SPLIT | REPAIRED PIPE, AREA CLEANED AND LIMED
IN0032468 | CITY OF LAFAYETTE WPCD | TIPPECANOE | 2012-08-05 |  |  | 1700-1900 BLOCK OF NORTH 27TH ST | CATCH BASINS | RAIN 3+ CITY WAS NOT NOTIFIED UNTIL 8/6/12 @ 7:48A. UNABLE TO DETERMINE THE AMOUNT OF SEWAGE ON THE GROUND. CITY SEWER WAS OPERATING @ NORMAL FLOWS WHEN OUR EMPLOYEES ARRIVED ON SITE. | CLEANED ENTIRE AREA
IN0032468 | CITY OF LAFAYETTE WPCD | TIPPECANOE | 2012-08-18 | 11:45A-1:45P | 90 | 4501 SUGAR MAPLE | BASEMENT | TREE ROOTS PLUGGED SEWER # 4501 SUGAR MAPLE CAUSING BACK UP IN BASEMENT | CREWS RESPONDED TO JET CITY SEWER & REMOVED TREE ROOTS
IN0032468 | CITY OF LAFAYETTE WPCD | TIPPECANOE | 2012-09-01 | 12:30P-1:30P | 5000 | CITY SEWER ONTO N 27TH ST | BASEMENT | RAIN 1.5 IN 45 MINUTES | CITY CREWS CLEANED THE CURBSAND ROAD ON N 27TH ST
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-01-06 | 12:40P - 1:15P | 20 | MH @ 716 N. 14TH ST. | STREET | GREASE | REMOVED DEBRIS, FLUSHED AREA
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-01-17 | 4:34A-8:15A | 2000 | 40 & 8 LIFT STATION | UNNAMED DITCH TO WILDCAT CREEK | RAIN 1.51" LIFT STATION WAS RUNNING @ FULL CAPACITY | CONTINUE PREVENTATIVE MAINTENANCE TO KEEP THE LIFT STATION
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-01-18 | 9:49A-10:35A | 15 | 832 S WAGONWHEEL CT | BASEMENT | CITY SEWER WAS PLUGGED | JETTED CITY SEWER APPROX 251 FT. LINE IS OPEN NOW
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-01-25 | 2:00P - 2:40P |  | MH 1201 TEAL RD | GROUND | GREASE | JETTED SEWER
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-02-29 | ? - 8:50A (3/2) | 100 | RAINEY BROOK LS VALVE PIT | GRASS AROUND STATION | 2" CHECK VALVE IN VALVE PIT BROKE; WOULD DRAIN BACK INTO VALVE PIT | CHECK VALVE IS ISOLATED AND WILL BE REPLACED
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-03-21 | ?-10:05AM | 60 | RAINEY BROOK LIFT STATION VALVE PIT | GRASS AROUND STATION | A 2 INCH CHECK VALVE IN THE VALVE PIT BROKE. THE PUMPS WOULD PUMP THE STATION DOWN AND WHEN THE PUMPS HUT OFF THE FORCE MAIN WOULD DRAIN BACK INTO THE VALVE PIT & OVER FLOW A SMALL AMOUNT | THE CHECK VALVE WILL BE REPLACE. IT IS CURRENTLY ISOLATED
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-04-09 | 11:53A-3:15P | 100 | MH BEHIND BRIDGE WATER COURT | GROUND | SEWER IS PLUGGED WITH GREASE. | CLEANED UP AREA AND UNPLUGGED SEWER
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-05-07 | 8:40A-9:10A | 500 | 40 & 8 LIFT STATION | UNNAMED DITCH TO WILDCAT CREEK | RAIN .89" IT APPEARS TO HAVE BEEN HIT BY LIGHTNING | PHASE MONITOR & OMNI SITE ALARM SYSTEM WILL BE REPLACED
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-06-25 | 10:44A - 2:45P | 100 | 1915 EVERETT ST. | BASEMENT | CITY SEWER PLUGGED WITH MINERAL DEPOSITS | JETTED SEWER; WILL REMOVE DEPOSITS
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-06-30 | 10:44A - 1:00P | 25 | CITY SEWER | BASEMENT 26 SUNDOWN CT | PLUGGED SEWER | JETTED SEWER TO PEN AND CLEANED AREA
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-11-02 | 2:08P-2:50P | 100 | 50 S KENSINGTON COURT SANITARY MH | STORM SEWER | CALL CAME IN FOR A PLUGGED SEWER. CREWS RESPONDED IMMEDIATELY & UNPLUGGED THE SEWER. | RELEASE TO STORM SEWER WAS CONTAINED & VAC'D OUT OF STORM SEWER. WILL TELEVISE SEWER FOR FURTHER REVIEW.
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-12-07 | 12:50P-1:31P | 25 | CITY SEWER | 1805 SHOSHONE DR | RAIN .10" ROOTS | ROOT CUT LINE
IN0032468 | LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-12-20 | 11:15A - 12:30P | 10 | CITY SEWER | BASEMENT | RAIN .98" SEWER LINE PLUGGED | UNPLUGGED SEWER
IN0023990 | OTTERBEIN MUNICIPAL STP | TIPPECANOE | 2012-06-26 |  |  | AERATION TANK | GROUND | SAMPLE CONTAINER WEDGED IN PIPE | REMOVED CONTAINER FROM PIPE AND HOSED DOWN SLUDGE
| PURDUE UNIV GROUND BDLG | TIPPECANOE | 2012-02-13 | 12:00P-12:30P | 5 | RUSSEL ST EXTENSION LATERAL | GROUND | LEAK OCCURRED IN A PLUGGED LATERAL BY THE NEW GROUNDS BLDG ON AHLERS DRIVE | RESTROOMS AND SINKS CEASED BEING USED, 5 GAL SPILL TREATED WITH LIME/ UNPLUG LINE
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-04-03 | 12:54P-1:35P | 500 | ABANDONED FORCE MAIN @ NW & WINDSOR | CONTRACTOR'S EXCAVATION | CONSTRUCTION RELATED VACTOR CREW WAS DISPATCHED TO ASSIST CONTRACTOR WITH CLEAN UP | SPILL WAS CONTAINED WITHIN THE CONTRACTOR'S EXCAVATION
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-04-09 | 3:15P-4:00P | 75 | NORTHWESTERN AVE & YEAGER RD | CONTRACTOR'S EXCAVATION | VACTOR CREW WAS DISPATCHED TO ASSIST CONTRACTOR WITH CLEAN UP. | SPILL WAS CONTAINED WITHIN CONTRACTOR'S EXCAVATION
IN0024821 | WEST LAFAYETTE MUNICIPAL STP | TIPPECANOE | 2012-10-20 | 3:00P - 5:10P | 300 | MH NEAR 1836 LOCUST LANE | GROUND, STREET/COMBINED SEWER VIA INLET | GREASE | VACTOR WAS DISPATCHED TO OPEN UP THE SEWER MAIN & RESTORE FLOW.
| SHARPSVILLE UTILITIES | TIPTON | 2012-05-07 | 14:30-16:32 | 5440 | STATION A PUMP PIT SHARPSVILLE | MUD CREEK | REPLACED LEAKING PIPING AND PUMP ADAPTERS IN PUMP PIT
| SHARPSVILLE UTILITIES | TIPTON | 2012-09-07 | 9:00P-7:45A | 14197 | STATION A PUMP PIT | MUD CREEK | RAIN 3.4
| SHARPSVILLE UTILITIES | TIPTON | 2012-10-23 | 1414-2300 | 12175 | STATION A, PUMP PIT, SHARPSVILLE | MUD CREEK | RAIN 1.3
IN0021474 | TIPTON MUNICIPAL STP | TIPTON | 2012-01-23 | 8:00A-6:00P | 16289 | DIV A STATION A PUMP PIT | MUD CREEK | RAIN .6 SNOW MELT 3 INCHES
IN0021474 | TIPTON MUNICIPAL STP | TIPTON | 2012-01-26 | 11:54P - 6:00A (1/27) | 24276 | DIV A STATION A PUMP PIT | MUD CREEK | RAIN 1.4"
| BROOKVILLE LAKE RSD | UNION | 2012-01-23 | 9:00A - 11:30A | 10000 | MOUNDS LS | GROUND | MALFUNCTION IN PLC | REPLACED PLC
| BROOKVILLE LAKE RSD | UNION | 2012-09-10 | 9:00A | 10000 | FOX RUN LIFT | GROUND | CONTROL BREAKER TRIPPED | RESET BREAKER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-01-14 | 11:40P-2:30A | 60 | 2805 EASTBROOKE DR | GROUND @ MANHOLE | EQUIP FAILURE COLLECTION SYSTEM STAFF EST 60 GAL OF WASTEWATER | WE HAVE DETERMINED THAT THE UTILITY OWNED TURNK SEWER WAS HOLDING DUE TO ROOTS
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-01-20 | 4:00P - 5:30P | 3 | WASHINGTON AVE MH | GROUND | RAGS IN PRIVATE LATERAL | FLUSHED LATERAL
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-01-23 | 4:50P - 5:10P | 5 | 2006 MONROE AVE CLEANOUT | GROUND | OBSTRUCTION IN LATERAL | FLUSHED LATERAL
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-01-24 | 1:45P - 2:15P | 10 | 6705 BAYARD PARK DR MH | GROUND | ROOTS | RAN ROOT SAW IN MAIN
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-02-06 | 8:15A - 11:25A | 1000 | 1500 WATERWORKS RD | GROUND TRIBUTARY TO BEE SLOUGH | WET WELL WASTE LINE RUPTURED | FIXED LINE AND LIMED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-02-07 | 6:30P - 9:30P | 2 | 3207 LAKE DR. TOILET | BATHROOM FLOOR | OCCURRED DURING ROOT MAINTENANCE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-02-07 | 2:40P - 6:00P | 100 | 5412 FIELDING MANOR DR PRIVATE CLEANOUT | GROUND | ROOTS IN ADJACENT PROPERTY'S LATERAL | FLUSHED LINE
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-02-16 | 3:50P - 6:00P | 10 | 437 TYLER AVE CLEANOUT | GROUND | ROOTS | REMOVED DEBRIS, FLUSHED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-03-05 | 9:25A-10:30A | 25 | 1909 GREENCASTLE DRIVE | GROUND | OBSTRUCTION | DEBRIS CLEANED from AFFECTED AREA AND LIME APPLIED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-03-08 | 2:00P - 3:30P | 20 | 2609 RAVENSWOOD DR GARAGE FLOOR DRAIN | GROUND | SEWER COLLAPSED | VACUUMED MH
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-03-14 | 5:45P - 5:50P | 2 | 2900 S ENGLEWOOD CLEANOUT | GROUND | RESIDENTIAL GREASE | CLEANED SEWER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-03-29 | ?-12:10P |  | PRIVATE MANHOLE | GROUND/STORM DITCH | PRIVATE SSO EST FLOW RELEASED 200 GAL. THIS IS BEING REPORTED AS A PRIVATE SANITARY SEWER OVERFLOW ON BEHALF OF. | DEBRIS CLEANED FROM AFFECTED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-04-09 | 10:30A-10:50A | 2 | CLEANOUT | GROUND | ROOTS | DEBRIS CLEANED FROM AFFECTED AREA AND LIME APPLIED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-05-27 | 4:00P-4:45P | 20 | 720 BONNIEVIEW DR MH | GROUND | EQUIPMENT FAILURE | AFFECTED AREA CLEANED AND LIME APPLIED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-06-19 | 2:30P-4:15P | 5 | PRIVATE PROPERTY CLEANOUT | GROUND | ROOTS AND RAGS | AFFECTED AREA CLEANED BY HOMEOWNER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-07-27 | 1:45P-2:30P | 25 | PRIVATE PROPERTY CLEANOUT | GROUND | ROOTS | AFFECTED AREA CLEANED AND LIME APPLIED CLEANED SEWER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-07-30 | 3:15P-6:15P | 100 | CLEANOUT | GROUND | CLOGGED LINE | RAN ROOT SAW
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-07-30 | 1:00P-2:00P | 25 | MH GRATING | GROUND | ROOTS | AFFECTED AREA WAS VACUUMED AND LIME WAS APPLIED TO NEUTRALIZE IT RAN ROOT SAW
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-02 | 11:30P - 12:00A (8/3) | 15 | 1413 ADAMS AVE TOILET | BATHROOM FLOOR | RAIN 2.31" | CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-02 | 11:25P - 1:45A (8/3) | 50 | 1220 SOUTH SPRING ST BASEMENT DRAIN | BASEMENT | RAIN 2.31" | CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-02 | 10:10P - 12:45A (8/3) | 100 | 613 N. NORMAN AVE MH | GROUND | RAIN 2.31" | CLEANED AREA AND APPLIED LIME
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-02 | 10:10P - 12:30A (8/3) | 10 | 213 N ROTHERWOOD BATHROOM TOILET | BATHROOM FLOOR | RAIN 2.31" | CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-02 | 11:00P - 1:45A (8/3) | 350 | 804 E MULBERRY ST BASEMENT DRAIN | BASEMENT | RAIN 2.31" | CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-02 | 11:30P - 1:45A (8/3) | 25 | 436 WEINBACK AVE BASEMENT DRAIN | BASEMENT | RAIN 2.31" | CLEARED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-15 | ?-11:00A | 2000 | PRIVATE MH | GROUND/STORM DITCH | PRIVATE SSO ESITMATED FLOW RELEASED:2000 GAL THIS IS BEING REPORTED AS A PRIVATE SANITARY SEWER OVERFLOW ON BEHALF. OF MR TOM WAHOSKI MANAGER OF NORMANDY ARMS APTS ETC | PROPERTY OWNER RESPONSIBLE FOR CLEAN UP
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-24 | 3:25P-4:45P | 10 | FOUNDATION DRAIN | BASEMENT | EQUIPMENT FAILURE OBSTRUCTION | AFFECTED AREA CLEANED BY HOMEOWNER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-08-26 | 5:00P-7:00P | 5 | MH | GROUND | EQUIPMENT FAILURE SSO ESTIMATE FLOW RELEASED 5 GAL UTILITY RECEIVED REPORT OF MH RELEASING WASTEWATER. | AFFECTED AREA CLEANED & LIME APPLIED.
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-09-10 | 4:00P-4:45P | 100 | 5300 POLLACK MH | GROUND | GREASE | AFFECTED AREA CLEANED & LIME APPLIED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-09-10 | 10:30A-10:35A | 15 | 515 S. CONGRESS MH | GROUND | ROOTS | AFFECTED AREA CLEANED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-09-17 | 8:45P-9:35P | 25 | BATHROOM TOILET | BATHROOM FLOOR | ROOTS | CREW CLEANED MAIN SEWER; AFFECTED AREA CLEANED BY HOMEOWNER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-09-24 | 8:20A - 8:50A | 5 | 7611 BELLMEADE AVE PROPERTY LINE CLEANOUT | GROUND | ROOTS IN LATERAL | CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-10-02 | 2:30P-8:00P | 150 | 4209 KATHLEEN AVENUE | GROUND/CRAWLSPACE | ROOTS | CLEANED MAIN SEWER; AFFECTED AREA CLEANED BY PROPERTY OWNER.
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-10-18 | 9:00A - 11:30A | 150 | 2816 MARYBETH AVE SHOWER DRAIN | BASEMENT | OBSTRUCTION IN MAIN SEWER | CLEANED MAIN SEWER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-10-23 | 11:45A-12:30P | 30 | 711 SAINT MARY'S DRIVE | GROUND | OBSTRUCTION | CLEANED SEWER; AFFECTED AREA CLEANED.
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-10-30 | 10:10A-10:25A | 2 | 3021 WAYSIDE DRIVE | GROUND | OBSTRUCTION IN PROPERTY LINE CLEANOUT | AFFECTED AREA CLEANED
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-11-08 | 12:15P - 7:15P | 30 | 6717 LINCOLN AVE PROPERTY LINE CLEANOUT | GROUND | ROOTS IN LATERAL | CLEANED LATERAL AND AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-11-18 | 9:35A-12:30P | 80 | 2755 WAYSIDE DR | GROUND | UPON INVESTIGATION IT WAS DETERMINED THAT THE MAIN SEWER WAS OBSTRUCTED. CREW CLEANED MAIN SEWER TO REMOVE OBSTRUCTION, RELEASE ELIMINATED. | AFFECTED AREA CLEANED. CREW CLEANED MAIN SEWER TO REMOVE OBSTRUCTION, RELEASE ELIMINATED.
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-11-21 | 3:45P - 9:30P | 15 | 801 RAVENSWOOD DR. FLOOR DRAIN | BASEMENT | MAIN SEWER OBSTRUCTED | CLEANED SEWER AND REMOVED OBSTRUCTION
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-11-29 | 10:05A - 2:30P | 75 | 732 & 804 SOUTHFIELD RD MH | GROUND | SEWER OBSTRUCTED | REMOVED OBSTRUCTION AND CLEANED AREA
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-12-06 | 3:55P-4:45P | 10 | 6601 E CHERRY ST | GROUND | ROOTS | AFFECTED AREA CLEANED. CLEANED SEWER MAIN
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-12-21 | 10:40A - 11:00A | 5 | 1816 GREENFIELD RD MH | GROUND | OBSTRUCTION | CLEANED SEWER
IN0033073 | EVANSVILLE STP-EASTSIDE | VANDERBURGH | 2012-12-27 | 12:15P - 12:35P | 5 | 3025 E. CHANDLER CLEANOUT | GROUND | OBSTRUCTION IN LATERAL | CLEANED LATERAL CONNECTION AND REMOVED OBSTRUCTION
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-01-23 | 3:00P - 3:45P | 200 | 9422 HEDGEWOOD CT | GROUND | GREASE | FLUSHED MAIN
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-01-23 | 10:45A - 11:30P | 300 | 711 WEST MILL RD | GROUND | OBSTRUCTION | FLUSHED MAIN
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-01-25 | 8:30A - 10:30A | 200 | 3020 IGLEHEART AVE MH | GROUND | ROOTS | FLUSHED MAIN
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-02-02 | 9:00A-11:00A | 5 | 2824 PENNSYLVANIA AVE | GROUND | EQUIPMENT FAILURE | AFFECTED AREA CLEANED & LIME APPLIED. AREA WILL BE PLACE ON UTILITY'S PREVIOUS MAINT SCHEDULE. AREA WILL BE VISUALLY MONITORED FOR 72 HRS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-02-14 | 6:40P - 7:30P | 10 | 3204 KRATZVILLE CLEANOUT | GROUND | DEBRIS | REMOVED DEBRIS
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-02-16 | 2:00P - 11:00A (2/17) | 60 | MILLERSBURG RD LS | GROUND | DAMAGED AIR RELEASE VALVE | REPLACE VALVE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-02-17 | 1:30P-2:00P | 5 | 816 TULIP AVE | GROUND | SSO EST FLOW RELEASED 5 GAL & ROOTS | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-02-18 | 12:50P-2:05P | 10 | 1613 WESTERN HILLS AVE | GROUND | SSO EST FLOW GAL CREW RESPONDED TO REQ FOR SERV. UPON ARRIVAL THERE WAS EVIDENCE THAT MH HAD PRIOR RELEASE BUT WAS NOT RELEASE WHEN CREW ARRIVED | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-02-24 | 7:30A-9:00A | 10 | 217 LOGWOOD DRIVE | GROUND | SSO EST FLOW RELEASED 10 GAL CREW RESPONDED TO REQUEST TO SERVICE UPON ARRIVAL THERE WAS EVIDENCE THAT CLEANOUT HAD PRIOR RELEASE, BUT WAS NOT RELEASING WHEN CREW ARRIVED | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-02-25 | 3:30P-10:15P | 4000 | PPG LIFT STATION FORCE MAIN | GROUND | SSO EST FLOW RELEASED 4000 GAL UTILITY RECEIVED REPORT OF MANHOLE RELEASING WASTEWATER, | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-08 | 8:30A - 11:00A | 41250 | 2550 N BAKER AVE FIRST AVE SIPHON CHAMBER | TRIBUTARY TO PIGEON CREEK | RAIN 1.2" COLLECTION SYSTEM MAXIMIZED | SANDBAGS PLACED ON SIPHON CHAMBER TO SECURE COVER
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-08 | 5:15P - 7:15P | 5 | 3648 STRATFORD RD. | GROUND | OBSTRUCTION | CLEANED AND LIMED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-08 | 8:30A - 1:00P | 27000 | 711 W. MILL RD MH | GROUND | RAIN 1.2" | CLEANED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-10 | 4:05P-5:40P | 30 | 2418 JOAN PLACE | GROUND | ROOTS | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-14 | 4:15P - 4:50P | 700 | 4500 W LLOYD EXPRESSWAY MH | GROUND | GREASE IN LINE | CLEANED LINE AND GROUND
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-26 | 2:06P-5:36P | 100 | 726 GEORGETTE ST | GROUND | CSSR ESTIMATED FLOW RELEASED: CREW RESPONDED TO REPORT OF WASTEWATER PONDING BEHIND RESIDENCE UPON ARRIVAL IT WAS DETERMINED THAT CAVE-IN AROUND MH WAS THE SOURCE OF THE RELEASE. CREW FLUSHED MAIN TO ELIMINATE RELEASE | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-29 | 2:00P-4:15P | 20 | 4920 N 4TH AVE | GROUND | ROOTS | THE RESIDUAL MATERIAL WAS CLEANED UP AND LIME WAS APPLIED TO THE AFFECTED AREA THE CLEANOUT
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-03-30 | 4:50P-5:10P | 10 | BASEMENT FLOOR | BASEMENT |  | PROPERTY OWNER RESPONSIBLE FOR CLEAN UP OF PRIVATE PROPERTY
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-04-10 | 9:00A-9:05A | 2 | PRIVATE PROPERTY TOILET | BATHROOM FLOOR | SSO EST FLOW RELEASED:2 GAL UTILITY RECEIVED CALL FROM HOMEOWNER THAT WATER HAD RELEASED FROM COMMODE ONTO BATHROOM FLOOR | HOMEOWNER CLEANED AFFECTED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-04-23 | 9:20A-10:30A | 5 | PROPERTY LINE CLEANOUT | GROUND | OBSTRUCTION IN LINE | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-05-05 |  | 66000 | 2550 N BAKER AVE | TRIBUTARY TO PIGEON CREEK | RAIN 1.92 | SANDBAGS REPLACED ON SIPHON CHAMBER AND AREA SECURED WITH CONSTRUCTION FENCING
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-05-05 |  | 24000 | 711 W MILL RD MH | GROUND/STORM SEWER | RAIN 1.92 | AFFECTED AREA CLEANED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-05-29 | 9:15A-10:15A | 2 | 209 SHERIDAN RD CLEANOUT | GROUND | OBSTRUCTION | DEBRIS CLEANED FROM AFFECTED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-06-02 | 2:20P-3:45P | 5 | PROPERTY LINE CLEANOUT | GROUND | OBSTRUCTION IN CLEANOUT | DEBRIS CLEANED FROM AFFECTED AREA AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-07-04 | 3:20P - 5:05P | 5 | 1365 MESKER PARK DRIVE FLOOR DRAIN | BASEMENT | ROOTS AND RAGS IN MAIN SEWER | CLEANED SEWER
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-07-09 | 10:45P-12:00A | 75 | 10700 EAGLE CROSSING DR., COMMODE, PROPERTY LINE CLEANOUT | BATHROOM FLOOR, GROUND | GREASE | AFFECTED AREA CLEANED AND LIME APPLIED. PROPERTY BACKUP AREA CLEANED BY HOMEOWNER
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-07-12 | 9:30A-11:30A | 20 | PRIVATE SEWER FORCE MAIN | GROUND | PRIVATE LS; FORCE MAIN DAMAGED DURING CONSTRUCTION | DEBRIS CLEANED FROM AFFECTED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-07-25 | 10:05A-10:10A | 1500 | MILLERSBURG ROAD LIFT STATION | GROUND | LIFT STATION CREW WAS INSTALLING A BYPASS PUMP @ THE MILLERSBURG LIFT STATION FOR WET WELL CLEANING. | CREW EXERCISED GATE VALVE TO SEAT TO STOP RELEASE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-08-02 | 11:10P 12:30A (8/3) | 50 | 8 TULIP AVE MH | BACKYARD | RAIN 2.31" | CLEANED AREA AND APPLIED LIME
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-08-02 | 11:45P - 12:30P (8/3) | 10 | 3609 TREMONT AVE | BATHROOM FLOOR | RAIN 2.31" | CLEANED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-08-02 | 11:00P - 12:00A (8/3) | 25 | 2837 FLOYD ST | BACK UP IN HOUSE | RAIN 2.31" | CLEANED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-08-08 | 7:15A - 8:00A | 25 | 123 FERNWOOD MH | GROUND | OBSTRUCTION IN MAIN SEWER | REMOVE OBSTRUCTION AND CLEANED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-08-13 | 12:10P - 12:45P | 5 | 1105 HARMONY WAY CLEANOUT | GROUND | OBSTRUCTION IN LATERAL | CLEANED AND LIMED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-08-14 | 10:20A-1:00P | 75 | FLOOR DRAIN/PRIVATE LATERAL | BASEMENT/GROUND | SSO ESTIMATED FLOW RELEASE 75 GAL CREW RESPONDED TO REPORT OF WASTEWATER ENTERING BASEMENT | AFFECTED AREA CLEANED & LIME APPLIED. BASEMENT AREA CLEANED BY HOMEOWNER
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-08-27 | 4:45P-7:15P | 150 | PRIVATE PROPERTY CLEANOUT | GROUND | RAIN .90 ROOTS | AFFECTED AREA CLEANED AND LIME APPLIED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-10-18 | 3:10P - 3:30P | 20 | 2745 MARION AVE UTILITY CLEANOUT | GROUND | EVIDENCE OF PRIOR RELEASE BUT SEWER RUNNING FREE AND CLEAR | CLEANED AND LIMED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-10-18 | 9:00A - 9:45A | 20 | 4206 KENSINGTON CLEANOUT | GROUND | OBSTRUCTION IN LATERAL | CLEANED AND LIMED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-10-25 | 5:15P - 6:00 | 5 | 4206 KENSINGTON | GROUND | ROOTS IN LATERAL | REMOVED ROOTS AND CLEANED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-10-25 | 8:00P - 10:00P | 5 | 1319 STINSON AVE FLOOR DRAIN | BASEMENT | SEWER OBSTRUCTED | CLEANED SEWER
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-10-30 | 1:15P-2:00P | 25 | 2511 N FIRST AVENUE | GROUND/STORM SEWER | GREASE | AFFECTED AREA CLEANED.
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-11-11 | 2:20P-5:45P | 20 | 717 STANLEY AVENUE | BASEMENT | MAIN SEWER WAS OBSTRUCTED. | CREW CLEANED MAIN SEWER TO REMOVE OBSTRUCTION, RELEASE ELIMINATED. AFFECTED AREA CLEANED BY HOMEOWNER.
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-11-20 | 1:13P-1:26P | 375 | 8600 UNIVERSITY BLVD | GROUND/STORM DITCH | UPON INVESTIGATION IT WAS DETERMINED THAT A GREASE BLOCKAGE ON THE PUMP FLOATS WAS PREVENTING STATION OPERATION. | CREW TURNED PUMPS ON MANUAL & CLEANED GREASE WASTE FROM FLOATS, RELEASE ELIMINATED. CREW RETURNED STATION TO NORMAL OPERATION.
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-11-23 | 10:30A-9:45A | 200 | 313 DRIER BLVD UTILITY CLEANOUT | GROUND | SEWER OBSTRUCTED | AFFECTED AREA CLEANED
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-11-26 | 12:25P - 4:15P | 700 | 3022 IGLEHART AVE MH | GROUND | CONSTRUCTION DEBRIS | REMOVED DEBRIS, FLUSHED AREA
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-12-03 | 11:45A - 12:30P | 2 | 801 S. BOSSE AVE MH | GROUND | ROOTS | CLEANED MAIN
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-12-03 | 9:20A - 2:20P | 600 | 301 LADONNA BLVD PRIVATE LINE | GROUND | ROOTS IN PRIVATE SANITARY SEWER | CLEANED SEWER
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-12-10 | 9:20P-10:00P | 200 | 4519 STRATFORD ROAD | GROUND/STORM SEWER | OBSTRUCTION | AFFECTED AREA CLEANED & LIME APPLIED.
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-12-11 | 9:00A-A0:15A | 2 | 4512 LONGFIELD DRIVE | GROUND | OBSTRUCTION | AFFECTED AREA CLEANED & LIME APPLIED.
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-12-21 | 9:00A - 10:15A | 3750 | 4080 MILLERSBURG RD | GROUND/CREEK | UPS FAILURE AT LS | UPS REMOVED AND STATION PUT BACK IN SERVICE
IN0032956 | EVANSVILLE STP--WESTSIDE | VANDERBURGH | 2012-12-26 | 7:00A -7:30A | 3 | 363 CRAIG AVE. | GROUND | OBSTRUCTION IN LATERAL | CLEANED LATERAL CONNECTION AND REMOVED OBSTRUCTION
IN0060682 | CLINTON MUNICIPAL STP | VERMILLION | 2012-05-01 | 2:00P-3:00P | 25000 | HEADWORKS AND GRIT CHAMBER | GROUND/INTERCEPTOR TO HEADWORKS | BOTH OF THE VFD PUMPS WERE DETERMINED TO HAVE FAN FAILURES IN TURN CAUSING THE VFD PUMPS TO OPERATOR | THE VFD PUMPS WERE DIAGNOSED AND REPLACEMENT FAN ARE ON ORDER TO REPAIR THE VFD PUMPS
IN0020362 | NORTH MANCHESTER MUN. STP | WABASH | 2012-09-16 | ?-10:00A | 100000 | SEWER MAIN FROM L.S. SOUTH OF 9TH ST. | GROUND, SOYBEAN FIELD | SEWER MAIN COLLAPSED IN FARMER'S FIELD | TOWN PERSONAL SHUT L.S. DOWN TO CONTAIN THE SEWAGE. SET UP BYPASS PUMPING @ THE BREAK & RESUME L.S. PUMPING
IN0024741 | WABASH WWTP | WABASH | 2012-06-18 | 5:44A - 8:15A | 562500 | LS #1 (OUTFALL 004) MIDDLE ST | WABASH RIVER | POWER FAILURE | RESTORED POWER WHICH STOPPED DISCHARGE
IN0022420 | BOONVILLE MUNICIPAL STP | WARRICK | 2012-06-06 | 7:30A-8:00A | 100 | EAST LAKE STR LIFT STATION | GROUND | GREASE & DEBRIS | CLEANED AND DISINFECTED AREA
IN0022420 | BOONVILLE MUNICIPAL STP | WARRICK | 2012-10-21 | 10:30A-10:30A (10/23) | 2500 | STONEHAVEN L S | GROUND/DITCH | BELIEVE A FLUCTUATION OF INCOMING POWER OCCURRED SOMETIME OVER THE WKND OF 10/20-10/22 CAUSING PUMPS NOT TO ACTIVATE WHEN CALLED FOR | ADJUSTED VOLTAGE REGULATOR
IN0022420 | BOONVILLE MUNICIPAL STP | WARRICK | 2012-10-30 | 10:00A - 10:20A | 20 | STONEHAVEN LS | GROUND | VOLTAGE FLUCTUATION CAUSED PUMPS TO NOT ACTIVATE PROPERLY | ADJUSTED VOLTAGE REGULATOR
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2012-01-30 | 1200-1330 | 20 | MANHOLE #51 | STREET | HOME OWNER HAS BACK UP BLOCKAGE DISCOVERED BY PLUMBER ROOTS IN GRAVITY LINE | CAMERA & HIGH PRESSURE WASHER
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2012-03-10 | 14:00-16:00 | 1400 | HENRY'S MOBILE HOME 700 E LINCOLN AVE | YARD & SURROUNDING AREA | CONSTRUCTION RELATED PROPERTY OWNER DIGGING UP SEWER LATERAL FOR REPAIRS, DUG UP & CUT SEWER FORCE MAIN INSTEAD | REPAIRED & CLEANED UP
IN0020435 | CHANDLER MUNICIPAL STP | WARRICK | 2012-08-02 | 10:55P - 7:19A |  | MH #7-198 | DITCH | LS #7 PUMP FAILURE
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-02-05 | 1:30P-2:35P | 2200 | BREAK IN HAISTON LIFT STATION FORCE MAIN @ 8700 LOCUST LANE | DITCH | THE HALSTON LIFT STATION 6 IN FORCE MAIN BROKE, RELEASING UNTREATED SEWAGE INTO A DITCH @ 8700 LOCUST LANE | THE LIFT STATION WAS IMMEDIATELY SHUT DOWN & A VACUUM TANK TRUCK WAS USED TO KEEP THE LIFT STATION WET WELL'S SEWAGE LEVEL SUCKED DOWN.
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-02-10 | 11:00A-2:00P | 68500 | LIFT STATION NO 2 FORCE MAIN BREAK @ 6511 VANADA RD | GROUND & THEN TO CYPRESS CREEK | WE RECEIVED A REPORT @ 11A THAT SEWAGE WAS LEAKING FROM THE LIFT STATION NO 2 24 IN RELIEF FORCE MAIN ON THE JIM VANADA PROPERTY | TO ISOLATE THE BACKFLOW FROM ENTERING THE PIPE @ THE PIPE @ THE HEAD WORKS WE HAD TO TEMPORARILY SHUT DOWN MASTER LIFT STATION
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-06-26 | 4:30P - 5:15P | 100 | HALSTON LS; FORCE MAIN BREAK | GROUND | 6" FORCE MAIN BROKE | USED VACUUM TRUCK TO KEEP LEVEL DOWN; REPAIRED LINE
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-07-25 | 9:30A - ? |  | LS #2 HIGH FLOW FORCE MAIN | GROUND | BROKEN FORCE MAIN | PUMPED AREA AND REPAIRED FORCE MAIN
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-07-25 | 9:30A-? |  | LIFT STATION NO 2 HIGH FLOW FORCE MAIN | GROUND | LIFT STATION NO 2 HAS THE CAPABILITY TO PUMP INTO 2 DIFFERENT FORCE MAINS ETC | THE FORCE MAIN WAS IMMEDIATELY ISOLATED. ON JULY 25, 2012 A PORTABLE PUMP WAS SETUP ALONG WITH 500 FT OF PUMP HOSE.
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-08-15 | 3:00P-7:45A |  | OLD HICKORY LIFT STATION | STORM DITCH TO 2 LAKES | HUMAN ERROR ON 8/15/12 NEWBURGH PERSONNEL WERE REPLACING A MOTOR STARTER AND HAD TURNED THE POWER OFF TO THE STATION | VACUUMED ALL POOLED WATER FROM DITCH AND GROUND. E COLI SIGNS HAVE BEEN PLACED AROUND BOTH LAKES AND SAMPLES
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-08-20 | 8:50A-9:20A | 10 | LS NO.1 AIR RELEASE VALVE | GROUND | AN AIR RELEASE VALVE ON THE LIFT STATION NO 1 FORCE MAIN DEVELOPED A LEAK & AND A SMALL AMOUNT OF SEWAGE WAS RELEASED | THE AIR RELEASE MH WAS VACUUMED OUT WITH A VACUUM TANK TRUCK, AND THE AIR RELEASE VALVE WAS IMMEDIATELY REPAIRED
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-08-27 | 1:10P-2:05P | 1000 | MH NO 06-62 | GROUND | SANITARY SEWER MAIN CLOG THE 8 INCH SANITARY SEWER MAIN @ THE REFERENCED LOCATION CLOGGED W/GRIT & CREATING THE OVERFLOW | THE SEWER MAIN WAS IMMEDIATELY JET CLEANED TO REMOVE THE CLOG. ETC
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-09-10 | 9:30A-9:30A |  | GRAVITY MAIN @ 5422 JEFFRIES LN | DITCH | CRACKED PIPE IN BOTTOM OF DITCH FOUND | WE ARE MAKING A TEMPORARY REPAIR AND WILL TURN IT OVER TO THE ENGINEERS FOR A RECOMMENDATION FOR PERMANENT REPAIR
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-10-24 | 2:16P-2:30P | 10 | CLEAN OUT SERVICING 6222 PFAFFLIN LAKE BLVD UPSTREAM OF M H 13-78 | GROUND | ROOTS | PULLED ROOTS OUT OF THE LATERAL TAP @ IN THE MH. DEBRIS WAS REMOVED IN THE AREA OF THE CLEAN-OUT
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-11-01 | 8:00A-9:45A | 2000 | MH NO 13-131 @ 6677 HILLSGATE COURT | GROUND & DRAINAGE DITCH | THE DOWNSTREAM SIDE OF MH NO 13-131 CLOGGED W/ROOTS & CREATED THE OVERFLOW. | THE ROOTS WERE IMMEDIATELY REMOVED TO CLEAR THE CLOG. ALL POOLED SEWAGE FROM THE OVERFLOW WAS VACUUMED UP.
IN0023892 | NEWBURGH MUNICIPAL STP | WARRICK | 2012-12-23 | 10:20A-11:45A | 5000 | MH 14-181 | DITCH W/CONCRETE SPILLWAY | POSSIBLE ROOTS IN LINE. CLEANED LINE W/JET TRUCK | VACUUMED ALL STANDING WASTEWATER. LINE WILL BE CCTV NEXT WEEK.
IN0021059 | NEW PEKIN MUNICIPAL STP | WASHINGTON | 2012-03-02 | 6:30P-9:30P |  | CHARLES ST LIFT STATION | BLUE RIVER | POWER FAILURE
IN0021644 | SALEM MUNICIPAL STP | WASHINGTON | 2012-03-26 | 7:43A-8:10A |  | AERATION BASIN | GROUND-W FORK BLUE RIVER | POWER FAILURE POWER OUTAGE INFLUENT WAS PUMPED TO LAGOONS OVERFLOW WAS FROM CLARIFIERS DRAINING BACK TO AERATION | OUTAGE WAS ON AERATION BASIN PUMPS. AUTOMATIC ALARM FAILED CAUSE UNKNOWN CLEANING & DISINFECTION AREA
IN0020010 | HAGERSTOWN MUNICIPAL STP | WAYNE | 2012-02-02 | 1:00P-8:30P |  | 651 E MAIN ST BEHIND FACTORY | GROUND TO A CREEK WLD LEAD TO WHITE WATER RIVER | MANHOLE OVERFLOWED DO TO ROOT BLOCKAGE IN THE LINE. NOTICE DURING A WALK THROUGH TO LOOK AREA OVER | HAD TO CALL IN CLUYS TO GET THIS LINE. AFT TRYING OUR TRUCK COULDN'T GET THROUGH LOTS OF ROOTS IN LINE
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2012-01-26 | 7:08A-5:30A | 200 | 143-068 | WHITE WATER RIVER | RAIN .5, EQUIPMENT FAILURE DO TO POSSIBLE BLOCKAGE
IN0025615 | RICHMOND MUNICIPAL STP | WAYNE | 2012-02-24 | 8:00A-9:00A | 10000 | 619 COMMERCE DR | GROUND | WE FOUND MEDICAL TUBING IN BOTH PUMPS SHUTTING THE STATION DOWN BY TRIPPING BREAKERS CLEANED PUMPS AND RESET OVERFLOW WAS STOPPED | WILL SPEAK WITH LINCARE FACILITY BY LIFT STATION USED VAC TRUCK TO CLAN UP AREA OF OVERFLOW
IN0022535 | TOWN OF CENTERVILLE | WAYNE | 2012-10-01 | 11:45A-12:00P | 40 | SERVICE LINE @ 703 NATIONAL EAST | DRY CREEK BED | GREASE | CALLED PRIVATE CONTRACTOR TO CLEAN UP SPILL IN DRY CREEK BED & FIX LINE
IN0022411 | BLUFFTON MUNICIPAL STP | WELLS | 2012-01-17 | 7:00A-8:30A | 10000 | MH @ 1820 WESTERN AVE | GROUND, MIXED STORM WATER,DRAINED | RAIN 1.43 | TURNED ON ADDITIONAL BYPASS CSO PUMP @ TRMNT PLANT
IN0022411 | BLUFFTON MUNICIPAL STP | WELLS | 2012-01-17 | 7:45A-10:30A | 2000 | M H BEFORE LIFT STATION 2695 E. 301 ST | GROUND | RAIN 1.43 CONTROL PROCESSOR FAILURE | TURNED LIFT STATION PUMPS ON MANUAL SWITCH TO BACK-UP FLONT
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-03-14 | 9:23A-9:30A | 10 | 7351 N 1190 W DISCHARGE LINE | GROUND | FOUND BROKEN DISCHARGE LINE, 9:30A SHUT PUMP OFF, 9:33A CALLED CONTRACTOR TO FIX, | SHUT PUMP OFF & CALLED CONTRACTOR TO FIX
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-04-03 | 1:40P-3:25P | 5 |  |  | EQUIPMENT FAILURE | BACK FLOW @ CURB STOP BEING CHANGED BY CONTRACTOR
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-05-09 | 2:08P - 2:25P | 200 | 12340 N UPPER LAKE SHORE | GROUND | BROKEN GRINDER UNIT PUMP | CHANGED PUMPS
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-06-22 | 6:01P - 6:06P | 20 | GRINDER UNIT | GROUND | BAD PUMPS IN GRINDER UNIT | CHANGED PUMPS WITH NEW RUBBER GROMMETS
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-08-25 | 9:30A - 10:05A | 30 | 10128N - 1200W MONTICELLO GRINDER UNIT | GROUND | BROKEN GROMMET ON PUMP | CHANGED GROMMET AND LIMED AREA
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-10-13 | 8:56A - 9:05A | 8 | 11901 ORCHARD DR. | GROUND | BROKEN PUMP IN GRINDER UNIT | INSTALLED NEW PUMP; SPREAD LIME
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-11-09 | 2:35P - 3:10P | 20 | 11724 W 1250 N GRINDER PUMP | GROUND | FAILED PUMP | CHANGED PUMP AND LIMED AREA
IN0062367 | RATTLESNAKE CREEK WWTP | WHITE | 2012-12-29 | 2:20P - 2:24P | 100 | 11929 W. LOOKOUT DR. | GROUND | BROKEN CURBSTOP AND GROMMET | CHANGED CURBSTOP AND GROMMET
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-01-16 | 2:40P-2:43P | 5 | 2425 N PLEASANT VALLEY | GROUND | EQUIP FAILURE 2:40 @ SITE 2:43 TURNED PUMP OFF TO STOP FLUSHING 2:45 SPOKE W/CUST 2:51 REMOVE EXIST, 2:55 REPLACE W/A NEW PUMP | REPLACE PUMP IN GRINDER UNIT W/WORKING PUMP
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-02-18 | 1:57P-2:45P | 300 | 4359 E PENROD MONTICELLO | GROUND | BROKEN DISCHARGE LINE FROM GRINDER TO MAINLINE | SHUT GRINDER OFF & SHUT DOWN CURB STOP/FIX BROKEN DISCHARGE LINE BY CONTRACTOR
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-04-09 | 8:01?-8:18? | 2 | CURB STOP | GROUND | BAD O-RING ON CURB STOP, LEAKING OUT & FILLING TUBE AND OVERFLOWING | SHUT PUMP OFF CALLED CONTRACTOR TO FIX 8:30 ARRIVED 9:30 AND FIXED BY 11:30
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-05-05 | 7:34P-7:35P | 40 | 3065 STABLE RD CURB STOP | GROUND | BROKEN CURB STOP | REPLACED CURB STOP BACK FLOW AT ROAD
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-05-10 | 2:58P - 3:15P | 50 | 3834 FORREST LODGE LOOP | GROUND | BROKEN DISCHARGE LINE | FIXED BROKEN COUPLER FROM GRINDER UNIT
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-05-28 | 2:55P-3:10P | 25 | GRINDER UNIT | GROUND | BROKEN DISCHARGE LINE | SHUT PUMP OFF UNTIL CONTRACTOR ARRIVED
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-07-16 | 1:00P-1:25P | 20 | CURB STOP | GROUND | EQUIPMENT FAILURE BAD O-RING | SHUT PUMP & CURB STOP OFF REPLACED O-RING
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-08-07 | 6:30P 9:00P | 600 | 1 1/4" LINE TO MAIN | GROUND | CONTRACTOR BORED THROUGH LINE | SHUT OFF PUMP AND FIXED LINE
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-08-20 | 8:32A-8:37A | 20 | 198 W. NORWAY RD | GROUND | LEAKING AROUND GRINDER | LIMED YARD, PUT IN NEW PUMP
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-10-04 | 7:30P - 7:40P | 20 | 4866 N BOXMAN PLACE DISCONNECT BOX | GROUND | DISCONNECT BOX RIGHT LEG WAS BURNT | PUT ON NEW DISCONNECT BOX AND BREAKER; LIMED YARD
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-10-22 |  | 5 | 5746 NW SHAFER DR | GROUND | BROKEN DISCHARGE LINE | FIXED LINE
IN0060887 | TWIN LAKES REG SEWER DISTRICT | WHITE | 2012-11-29 | 4:52P - 5:09P | 30 | 3574 E. BAILEY RD. CURB STOP | GROUND | BROKEN CURB STOP | FIXED CURB STOP AND LIMED AREA