## SSO & Bypass Incidents
TEMPO AI ID # | TEMPO Incident # | NPDES Permit # | Reporting Source (Responsible Party) | County Name | Discharge Begin Date | Discharge End Date | Report Received Date | Estimated Quantity | Units | Discharge Location Description | Incident Description | Resolution | Media Impacted | Waterbody(s) Impacted
1632 | 35252 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-01-13 02:00 | 2013-01-13 05:00 | 2013-01-14 10:13 | 300 | gallons | Manhole at Franklin Street and Lehman Street Berne IN | Precipitation event and snow melt contributed to an Untreated Release from a manhole to the catch basin at the same location that enters sewage system. | The Long Term Control Plan for the City of Berne has been approved. | SSO Reached Public Land
1632 | 35253 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-01-13 02:00 | 2013-01-13 06:00 | 2013-01-14 10:12 | 700 | gallons | Manhole at Franklin Street and Hendricks Berne IN | Precipitation event and snow melt caused an Untreated Release from a manhole to the catch basin at the same location that enters sewer system. | The Long Term Control Plan for the City of Berne has been approved. | SSO Reached Public Land
1632 | 35249 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-01-13 03:00 | 2013-01-13 06:00 | 2013-01-14 10:13 | 200 | gallons | Manhole at Gay Drive Berne In | Precipitation event and snow melt coupled to cause an untreated release from a manhole. | The Long Term Control Plan for the City of Berne has been approved. | SSO Reached Public Land
1632 | 35254 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-01-13 03:00 | 2013-01-13 05:00 | 2013-01-14 10:12 | 5000 | gallons | Lift Station on Parr Road and 000 CR. Berne IN | Precipitation event and snow melt caused an Untreated Release from a Lift Station to the ground around the Lift Station | The Long Term Control Plan for the City of Berne has been approved. | SSO Reached Public Land
1632 | 35250 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-01-13 03:00 | 2013-01-13 05:00 | 2013-01-14 10:13 | 500 | gallons | Manhole at Indiana Street and Van Buren Street Berne IN | Precipitation event triggered an Untreated Release from manhole. | The Long Term Control Plan for the City of Berne has been approved. | SSO Reached Public Land
1632 | 35251 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-01-13 03:00 | 2013-01-13 06:00 | 2013-01-14 10:13 | 1000 | gallons | Manhole at Linn Grove Avenue and Van Buren Street Berne IN | Precipitation event and snow melt resulted in Untreated Release from manhole to Catch Basin that enters into sewer system. | the Long Term Control Plan for the City of Berne has been approved. | SSO Reached Public Land
1632 | 35660 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-01-18 20:00 | 2013-01-18 23:45 | 2013-01-21 09:08 | 22000 | gallons | Main Street Lift Station force main | Blowout(rupture) of force main from lift station resulted in untreated release from lift station to receiving waters. | Release occurred while station was shut down to repair rupture. | SSO Reached Receiving Water | Sprunger Ditch
1632 | 36345 | IN0021369 | BERNE CITY WASTE WATER TREATMENT PLANT SITE 1 | Adams | 2013-04-15 20:30 | 2013-04-20 12:00 | 2013-04-22 08:34 | 23310000 | gallons | City of Berne WWTP | Precipitation event caused a partially treated release from treatment plant to receiving waters. | Pumped partially treated effluent from Pond 2 to Habegger Ditch | SSO Reached Receiving Water | Habegger Ditch
1632 | 39490 | IN0021369 | Berne City Waste Water Treatment Plant Site 1 | Adams | 2013-07-03 02:00 | 2013-07-03 03:00 | 2013-07-03 08:22 | 0 |  | Lift Station on Parr Rd and Cr 000 | Rain 1.19 inches Power Failure Equipment Failure. Lighting hit the station. Our electrician had to put new parts in. | Repair pump Station | SSO Affected Private Property
1632 | 42887 | IN0021369 | Berne City Waste Water Treatment Plant Site 1 | Adams | 2013-12-22 02:00 | 2013-12-22 06:00 | 2013-12-23 08:38 | 3000 | gallons | Triple Zero Lift Station | Rain 2.23 inches With 2.23 inches of rain a pump went down. One pump could not keep up. | Repaired Pump station See Report | SSO Affected Private Property
7716 | 34819 | IN0039314 | DECATUR WASTE WATER TREATMENT PLANT | Adams | 2013-02-14 11:45 | 2013-02-14 12:00 | 2013-03-04 13:30 | 7000 | gallons | CSO 005 pump station | Equipment (sump pumps) triggered an Untreated Release from CSO005 on 02/14/2013. | Pump(s) failed triggering overflow. Pump is being repaired and investigating the replacement mechanical seals for packing. | SSO Reached Receiving Water | Saint Marys River
7716 | 35577 | IN0039314 | DECATUR WASTE WATER TREATMENT PLANT | Adams | 2013-04-11 09:30 | 2013-04-11 11:30 | 2013-04-18 11:38 | 0 |  | Manhole 600 Block E Monroe St Farm Field | Untreated Release Rain 2.79 |  | SSO Affected Private Property
1608 | 35193 | IN0039357 | GENEVA MUNICIPAL WASTE WATER TREATMENT PLANT | Adams | 2013-01-30 09:00 |  | 2013-01-30 10:48 | 0 |  | Manhole on Ford Street Geneva IN | Untreated release from manhole as a result of a rain event. | Overflow to the ground. Maximizing flow to WWTP without upsetting treatment. | SSO Reached Public Land
1608 | 34763 | IN0039357 | GENEVA MUNICIPAL WASTE WATER TREATMENT PLANT | Adams | 2013-02-27 09:30 |  | 2013-02-27 09:31 | 0 |  | Hirschy field manhole | A .51 inch precipitation event triggered an undescribed release to a farm field on 2-27-2013 | No action taken | SSO Affected Private Property
1608 | 34513 | IN0039357 | GENEVA MUNICIPAL WASTE WATER TREATMENT PLANT | Adams | 2013-03-11 14:30 |  | 2013-03-11 15:18 | 0 |  | Hirscher Field Ground | Continue on precipitation then a down pour at 13:00 checked at 14:00 and no spill at 14:30 overflow had started. | Continue to look for illegal connection & infiltration | SSO Affected Private Property
1608 | 35607 | IN0039357 | GENEVA MUNICIPAL WASTE WATER TREATMENT PLANT | Adams | 2013-04-11 08:00 |  | 2013-04-11 07:57 | 0 |  | Hirschyfield Manhole Ground | Untreated Release 2.75 inch rain |  | SSO Affected Private Property
15296 | 35854 | IN0040380 - Terminated | Monroe Public Water Supply | Adams | 2013-01-13 | 2013-01-14 | 2013-01-16 08:26 | 20000 | gallons | Lift Station | Precipitation event and snow melt resulted in unpermitted discharge from WWTP to retention pond | Keep pumps running that pump sewage to Berne Treatment Plant. Continuing to dye test system to find sources of influent. In the past year 80 to 10000 dollars spent on Lift Station update and force main air relief valves to try to increase flow. Continuing update plan. | SSO Reached Receiving Water
15295 | 39667 | 35378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-04 10:21 | 2013-08-05 07:47 | 0 |  | C29 - 40 Gold Course | Rain 4.75 inches Light rain 8/2/13 during the day had .24 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hr period was 4.75 inches. |  | SSO Reached Receiving Water | Beal Taylor Ditch
1856 | 35366 |  | ALLEN COUNTY REGIONAL SEWER DISTRICT | Allen | 2013-03-04 10:30 | 2013-03-04 13:30 | 2013-03-05 08:00 | 4000 | gallons | Hadley Rd near Acola Indiana | Force Main cut by City of Fort Wayne Construction Related City of Fort Wayne Digging hit Force Main running along Hadley Rd near Arcola Indiana | Construction crew repaired line and put back in service . Lift stations and pumps were turned off to stop overflow. | SSO Affected Private Property
6851 | 37623 |  | GRABILL TOWN | Allen | 2013-06-01 | 2013-06-01 17:30 | 2013-06-01 17:20 | 10000 | gallons | Town of Grabill Manhole 2-4 and Page Road Lift Station | Precipitation event flow exceeded system capacity resulting in untreated release from manhole and lift station to ground and receiving water. |  | SSO Reached Public Land; SSO Reached Receiving Water | Witham Ditch
15295 | 39261 | 0035378 (Main Aboite Plant) | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 14:20 | 2013-06-01 04:00 | 2013-06-01 15:20 | 0 |  | D 30-55 Field off Covington Rd | Rain 5 inches very heavy rain starting 10:00 5/31/13
15295 | 40413 | 78 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 21:45 | 2013-08-03 01:15 | 1913-09-26 11:30 | 0 |  | D31/120 Coves West Lakes | Light rain 8-2-13 during day had .25 inches by 4:00pm. Very heavy rain starting about 7PM 8/2/13 till early morning 8-3-13 4.5 inches. Total in 24 hr period was 4.75 inches. |  | SSO Reached Receiving Water
4110 | 36310 | IN0023116 - Terminated | HUNTERTOWN WATER WORKS | Allen | 2013-04-19 04:00 | 2013-04-19 12:00 | 2013-04-22 17:07 | 10000 | gallons | Serene Shores gravity manhole at 12526 Wandering Way | Precipitation event and I & I contribution resulted in an untreated release from manhole to storm sewer detention basin and receiving waters. | The town is implementing the recommendations of an I & I study for the old section of town and planning a flow equalization basin to reduce the operating pressure on the force main. Ths is the first observed overflow with the new wet monitoring program.The town will investigate the sewer network for observed location of Inflow and correct. Any future occurrences will be reported in 24 hours. An action plan will be prepared to address appropriate response for containment and cleanup. | SSO Reached Public Land; SSO Reached Receiving Water; Storm Sewer | Geller Ditch
4110 | 36312 | IN0023116 - Terminated | HUNTERTOWN WATER WORKS | Allen | 2013-04-19 04:00 | 2013-04-19 12:00 | 2013-04-22 17:08 | 20000 | gallons | 16339 Lima Road - Lima road Gravity sewer manhole.1601 West Gump Road - Gravity sewer manhole. | Precipitation event and I & I contribution resulted in untreated release from multiple manholes to surrounding ground ditches storm sewer and receiving waters. | this was the first observed occurrence ofoverflow with the new wet weather monitoring program. The town is currently implementing the recommendations of an I & I study completed for the old part of town in 2012. This includes structure lining and structure repair. The town will investigate the sewer network for observed locations of infiltration and correct. Any future occurrences will be reported in 24 Hours. A procedure will be established for monitoring other areas as well. | SSO Reached Receiving Water; Storm Sewer | Willow Creek
4110 | 38699 | IN0023116 - Terminated | HUNTERTOWN WATER WORKS | Allen | 2013-06-12 10:30 | 2013-06-13 01:30 | 2013-06-13 13:30 | 5000 | gallons | Manhole in front of 2007 Canaveral Ct Open Ditch to Willow Creek | Rain 3 inches. This infiltration exceeded the capacity of the sewer system and resulted in overflow through the casting in the sewer manhole in front of h & H Sales on Lima Rd. | The Utility Board has awarded a contract to line pipe and to perform manhole rehabilitation on this collection system. The town will continue to investigate the sewer network for observed locations of infiltration and correct any future occurrences will be reported in 24 hours. | SSO Reached Receiving Water | Willow Creek
4110 | 38718 | IN0023116 - Terminated | HUNTERTOWN WATER WORKS | Allen | 2013-06-12 22:30 | 2013-06-13 01:30 | 2013-07-25 11:25 | 5000 | gallons | 16339 Lima Road - Manhole | Untreated Release. 3 Inches precip in 3 hours. This infiltrtation exceeded the capacity of the sewer system and resulted in an overflow through the casting in the sewer manhole in front of the H & H Sales on Lima Road. | The Utility Board has awarded a contact to line pipe and to perform manhole rehabilitation on this collection system. the town will continue to investigate the sewer network for observed locations of infiltration and correct any future occurences will be reported in 24 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Willow Creek
4110 | 39665 | IN0023116 - Terminated | HUNTERTOWN WATER WORKS | Allen | 2013-08-02 19:00 | 2013-08-02 21:00 | 2013-08-05 20:58 | 0 |  | Manhole Lima Road Gravity Sewer Manhole 16339 Lima Road. | Rain 3.6 inches Exceeded max Capacity Due to heavy rainfall large quantities of inflow and infiltration entered the sanitary sewer network. This infiltration exceeded the capacity of the sewer system & resulted in overflow through the casting in the sewer manhole in front of H&H Sales on Lima Road. This overflow entered the west roadside ditch flowed into the storm sewer and into Willow Creek. | See Report | SSO Reached Receiving Water | Willow Creek
4110 | 42888 | IN0023116 - Terminated | HUNTERTOWN WATER WORKS | Allen | 2013-12-21 20:00 | 2013-12-22 08:00 | 2013-12-23 15:59 | 0 |  | H & H Sales Building 16339 Lima Rd. | Unknown and under investigation. Occurrence was during a period of heavy snow melt and rainfall. | See Report | SSO Basement Backup
15335 | 35616 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-03 13:00 | 2013-01-03 15:30 | 2013-01-07 13:26 | 52200 | gallons | Griswold Pump Station 1700 to 1799 Griswold | A contractor was de-chlorinating a 48 inch new water line at the filtration plant and was discharging in the combination line that goes into a 15 inch siphon. The discharge was too fast for the siphon to handle the flow. The line backed into the pump station and caused the pumps to discharge water into the river. Partially Treated Release to Receiving Waters. | Process has been discontinued and an alternative means of discharging dechlorinated water is being pursued. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Saint Marys River
15335 | 35571 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-04 | 2013-01-04 23:59 | 2013-01-07 13:25 | 0 |  | CSO Outfall O23 080. 1200 to 1599 East Hollis Lane | A water main break resulted in city water entering the combined sewer system and caused an overflow from CSO Outfall to receiving waters. | The city continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Saint Marys River
15335 | 35575 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-04 10:00 | 2013-01-07 09:30 | 2013-01-07 13:25 | 100 | gallons | 8402 Wheelock Road Z50 022 | Equipment failure. Small break in 8 force main just outside of pump station resulted in an untreated release that did not reach or affect any regulated water body. | Contracted with contractor working on a separate job to do the repair on the force main. The city continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system.
15335 | 35576 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-04 10:00 | 2013-01-04 16:00 | 2013-01-07 13:25 | 3000 | gallons | 9002 Wheelock Road | Another utility doing construction drove a guide wire support through the city s 8 sewer force main. The resulting flow went into a ditch to a storm drain to receiving water. | City crews repaired the damaged force main. The city continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows int the sewer collection system. | SSO Reached Receiving Water
15335 | 43781 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-04 13:23 | 2013-01-04 14:20 | 2014-01-04 13:35 | 114 | gallons | 4222 Tamarack S30 023 Tamarack Dr | An overflow occurred from the above listed separate sanitary sewer line. The line was practically blocked with roots. The City flushed the line and removed the blockage. The City will televise to ensure there are no further blockages in the line. | See Report | SSO Reached Public Land
15335 | 35574 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-04 14:00 | 2013-01-04 14:34 | 2013-01-07 13:25 | 10 | gallons | 5006 Guaine. T26 063 | A partial blockage resulted in an untreated release from a manhole to the ground around it. | The City flushed and was able to open the line. The overflow did not reach or adversely affect a regulated waterbody. The City flushed the line and the overflow was cleaned up. The city continues to implement its approve CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system.
15335 | 35556 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-10 10:45 | 2013-01-10 16:30 | 2013-01-15 11:29 | 130000 | gallons | 9661 Coverdale Road | Equipment failure broken clamp on 14 force main just outside Lift Station. Resulted in untreated flow to the fill valve pit and overflow to receiving waters. | City pumped and hauled the flow until repairs could be made. The city continues to implement it approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Robinson Ditch
15335 | 35473 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-13 15:15 | 2013-01-14 14:15 | 2013-01-15 11:30 | 50000 | gallons | 4127 Petit Avenue S15-011 | Precipitation event combined with partial blockage triggered an untreated release from SSO manhole to receiving waters Trier Ditch. | Cleared grease sticks and sanitary debris from sewer resolving the overflow. Affected area was cleaned up. The city continues to implement it approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water
15335 | 35798 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-13 19:30 | 2013-01-16 06:30 | 2013-01-17 15:56 | 100000 | gallons | L19 033 K19 023 | Precipitation event coupled with snow melt saturated ground and rising rivers resulted in untreated release from SSO to receiving waters. | The city used remote pumps in an impacted area to avoid or mitigate severe property damage and street flooding. | SSO Reached Receiving Water | Saint Marys River
15335 | 35670 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-15 12:00 | 2013-01-15 16:00 | 2013-01-16 09:44 | 500 | gallons | 1505 Feighner Road | Private contractor cut into a force main instead of the correct gravity main and caused an untreated release to receiving waters. | Pump station shut down to stop flow so that repairs could be made.The city continues to implement its approved SMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Pleasant Run Ditch
15335 | 35143 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-01-21 17:45 | 2013-01-21 19:45 | 2013-01-22 09:19 | 200 | gallons | W14 041 Regina Drive 7612 Regina Drive Fort Wayne IN | Separate Sanitary Sewer Overflow due to partial blockage by sanitary debris. | The city flushed and opene the line which cleared the overflow. Overflow area was cleaned up. The city will televise the line to verify there are no other blockages in the line. The city continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Public Land
15335 | 35316 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-02-11 16:30 | 2013-02-11 19:30 | 2013-04-01 21:11 | 20 | gallons | Cleanout 4920 Old Maysville Rd Ground | Untreated Release An overflow occurred from the above mentioned location (cleanout) to the ground only. The City s separate sanitary line was partially plugged. The City flushed and opened the line. However it cannot be determined at this time if the homeowner s private lateral contributed to the incident. The overflow was cleaned up. The overflow did not reach or adversely affect a regulated water body. | The City flushed the line and the overflow was cleaned up. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 34923 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-02-11 16:30 | 2013-02-11 19:30 | 2013-02-12 14:30 | 36 | gallons | Release occurred at the sewer cleanout at residential address of 4920 Old Maysville Road Fort Wayne in Allen county | An overflow from the cleanout occurred due to a city separate sanitary line being partially obstructed. Not determined if homeowner s private lateral contributed to the incident. | Overflow did not reach or adversely affect a regulated water body. Overflow was cleaned up. The city flushed the line and the overflow was cleaned up. The city continues to implement it approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 35317 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-02-13 17:00 | 2013-02-13 18:45 | 2013-04-01 10:30 | 0 |  | 4903 Buell Dr Basement | Untreated Release A basement backup was reported at the above mentioned address which is located in the combined sanitary sewer system. The City flushed the line and removed a partial blockage. However it can not be determined if the homeowner s private lateral contributed to the incident. The City s line is down and flowing. The back up event did not result in a discharge or adversely affect a regulated water body. | The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City flushed the line. The city continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 34954 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-02-13 18:00 | 2013-02-13 18:45 | 2013-02-14 10:30 | 0 |  | 4903 Buell Drive Fort Wayne IN | Basement backup at 4903 Buell Dr. Unknown amountof untreated waste in basement. | City flushed the line and removed a partial blockage. Can t be determined if the homeowner s private lateral contributed to the incident. The city continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 35319 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-02-27 08:19 | 2013-02-27 22:30 | 2013-04-01 14:00 | 0 |  | 4902 Galway Dr 2913 uhrick 4913 Desoto Dr Basement | Untreated Release Rain 1.210 inches A basement backup was reported at the above mentioned addresses located in the separate sanitary sewer line. The City flushes the line and removed a partial blockage. However it can not be determined if the homeowner s private laterals contributed to the incident. The City line is down and flowing. The back up event did not result in a discharge or adversely affect a regulated water body. | The city flushed the line. The City continues to implement it s approved CMOM and CSSOP program which include many preventative maintenance activities designed to prevent an/or minimize overflows in the sewer collection system. The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent an/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 34790 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-02-27 08:19 | 2013-02-27 22:30 | 2013-02-27 14:00 | 0 |  | Sewer backups at 4902 Galway Drive 2913 Uhrick and 4913 Desoto Drive in Fort Wayne IN. | Basement backups reported at 3 addresses | Basement backups were reported at 49o2 Galway Dr. 2913 Uhrick and 4913 Desoto Drive located in the separate sanitary sewer line. The city flused the line and removed a partial blockage. However it cannot be determined if the homeowner s private laterals contributed to the incident. The City line is down and flowing. The back up did not result in a discharge or adversely affect a regulated waterbody. The City flushed the line. The City continues to implement it approved SMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 34789 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-02-27 13:14 | 2013-02-27 14:30 | 2013-02-27 14:00 | 0 |  | 1219 Burgess Street Fort Wayne IN | A basement backup was reported at 1219 Burgess Street | A basementbackup was reported at 1219 Burgess in the combined sewer line. The city flushed the line and removed a partial blockage. However it cannot be determined if the homeowner s private laterals contributed to the incident. The back up event did not result in a discharge or adversely affect a regulated waterbody. The city flushed the line. The city continues to implement it approved CMOM and CSSOP programs which include many preventitive maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 34570 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-01 08:00 | 2013-03-04 09:30 | 2013-03-05 12:46 | 2836000 | gallons | M18 256 Spy Run Creek | Untreated Release Equipment Failure The regulator at M18 256 was plugged with grease and other sanitary debris. The city flushed the line and removed the blockage. The section on pipe will be add to the City regularly scheduled degreasing program.WWTP Flow During Release (MGD)3/1 67.193/2 67.253/3 64.99 | The City flushed the line. The City continues to implement it s approved CMOM and CSSOP program which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Spy Run Creek
15335 | 34570 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-01 08:00 | 2013-03-04 09:30 | 2013-05-05 12:46 | 2836000 | gallons | M18 256 Spy Run Creek | Untreated Release Equipment Failure The regulator at M18 256 was plugged with grease and other sanitary debris. The city flushed the line and removed the blockage. The section on pipe will be add to the City regularly scheduled degreasing program.WWTP Flow During Release (MGD)3/1 67.193/2 67.253/3 64.99 | The City flushed the line. The City continues to implement it s approved CMOM and CSSOP program which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Spy Run Creek
15335 | 34572 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-04 09:28 | 2012-03-04 12:00 | 2013-03-05 12:46 | 0 |  | 1627 Fairhill Rd. Basement | Untreated release. A basement backup was reported at the above listed address which is located in the combined sanitary sewer system. The City flushed the line to remove any potential partial blockages. However it cannot be determined if the homeowner s private lateral contributed to the incident. The back up event did not result in a discharge or adversely effect a regulated water body. | The city flushed the line The city continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance actives designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 35320 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-04 09:28 | 2013-03-04 12:00 | 2013-04-01 13:45 | 0 |  | 0627 Fairhill Rd Basement | Untreated Release A basement backup was reported at the above listed address which is located in the combined sanitary sewer system. The City flushed the line to remove any potential partial blockages. However it can not be determined if the homeowner s private lateral contributed to the incident. The back up event did not result in a discharge or a adversely effect a regulated water body. | The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent an/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 37399 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-05 | 2013-03-05 23:59 | 2013-04-05 14:50 | 0 |  | S15 011 & S15 005 Clive Ave and Philley Ave Ground | Untreated release. While doing routine manhole investigations on 4.5/13 it appears an overflow occurred at the above listed locations to the ground only the line is down and flowing normal. Cause and volume of the overflow is unknown. Upon speaking with a nearby homeowner the City was informed on 4.5/13 the overflowed likely occurred at some point between March5 2013 and March 11 2013. The WWTP flow on March 5th was 62.853 MG and 70.513 MG on March 11th. The overflow was to the ground only and did not reach or adversely affect a regulated water body. | The areas around the manholes was cleaned up. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City will monitor this area. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 34597 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-06 10:00 |  | 2013-03-06 10:26 | 0 |  | Near 7440 St Joe Rd Ground near Krunckenburg Ditch | During regular outfall inspections on 3/5/13 City crew noticed an pool of septic water on the ground adjacent to the Krunckenburg Ditch. The City s follow up inspection determined this pipe has been abandoned and is no active. It is believed the septic pool is a result of water lift in the abandoned sewer pipe that has gone septic. This pipe is not currently flowing. The City discussed this with IDEM on 3/6/13 and is therefore reporting this for informational purposes. | The City will remove any remaining septic water in this pipe to prevent recurrence. The City continues to implement it s approved CMOM and CSSOP which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City will remove any remaining septic water in this pipe to prevent recurrence. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Public Land
15335 | 35370 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-11 01:10 | 2013-03-11 05:00 | 2013-03-15 15:24 | 100000 | gallons | T34 027 T34 028 and T26 081 Krunkenburg Ditch | Untreated Release 10 Snow and 0.46 Rain Extraordinary weather created conditions which caused the below-described discharges from the City s separate sanitary sewer system notwithstanding the City s compliance with it s COM and NPDES Permit. These overflows would not have occurred without the snowmelt conditions that occurred from March 6th through March 11th. The continuous snowmelt of 10 of snow over a 5-6 day period resulted in a constant state of high soil saturation. This creates the potential for any amount of rainfall to trigger high RDII which we say on 3/10 and 3/11. And in this area the resulting RDII was enough to trigger an overflow even though the rainfall events themselves were not significant. From a hydrologic point of view it s reasonable to define the event as starting on March 5th with the record snowfall continuing for 6 days with continuous snowmelt and ending with two small rainfalls on the 10th and 11th. As the snowfall data shows a controlling component of the overflow event (the snowfall that generated the snowmelt/saturation period) had a return period of 18years. T34-028 (approximately 75000 gallons) T34-027 (approximately 21 000 gallons via emergency pumping don to protect homes form eminent property damage) T26-81 | The City utilized it s best efforts leading up to and throughout the extreme event and as explained above the City mitigated property with emergency pumping. It is also designing a pilot lining project to further improve area inflow elimination. Lining of sewer lines from T34-012 to T34-055 were lined in 2012. In addition to the actions stated above the City continues to implement its approved CMOM program and is planning further hydraulic assessment of the T34 and T26 area. | SSO Reached Receiving Water
15335 | 34745 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-11 17:02 | 2013-03-11 12:00 | 2013-03-15 15:13 | 4200 | gallons | X14 060 1503 Carlow Ct 1500 to 1716 Carlow Ct. Ground | Untreated Release Rain 0.460 inches An overflow occurred at the above listed manhole in the separate sanitary sewer system. The line was plugged with grease and other sanitary debris. Additionally there was an extraordinary wet weather event (0.46 inches of rain on 3/11 coupled with sharp temperature increases following record snowfall including more than 10 inches of snow melt) on an already saturated ground. The City flushed the line to remove the blockage. The incident was not a capacity issue but rather a blockage. The overflow was to the ground only and did not reach or adversely affect a regulated water body. | The City flushed the line and the overflow was cleaned up. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer system. The City flushed the line and the overflow was cleaned up. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 34768 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-11 17:02 | 2013-03-11 12:00 | 2013-03-15 15:17 | 4200 | gallons | X14 060 1503 Carlow Ct 1500 to 1716 Carlow Ct Ground | Untreated Release Rain 0.460 inches An overflow occurred at the above listed manhole in the separate sanitary sewer system. The line was plugged with grease and other sanitary debris. Additionally there was an extraordinary wet weather event (0.46 inches of ran on 3-11 a coupled with share temperature increases following record snowfall including more than 10 inches of snow melt) on and already saturated ground. The City flushed the line to remove the blockage. The incident was not a capacity issue but rather a blockage. The overflow was to the ground only and did not reach or adversely affect a regulated water body. | The City flushed the lone and the overflow was cleaned up. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City flushed the line and the overflow was cleaned up. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 34746 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-14 20:39 | 2013-03-15 | 2013-03-15 15:13 | 603 | gallons | F18 029 2532 Grand Canyon Corridor 2532 Grand Canyon Corridor | Untreated release. An overflow was reported at the above listed location as a result of the contractor error. This address above is located in new housing development. The City found 2 mandrel nylon rope reels and several large bundles of rope blocking the pipe that was left from the contractor. This was not the result of capacity concerns. The City flushed the line and removed the debris. The overflow was cleaned up. The City will go back to the site and do more work to make sure there is no other blockages in the line. This overflow was to the ground only and did not reach or adversely affect a regulated water body. | The City flushed the line to remove the blockage. The City continues to implement its approved CMOM and CSSP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City will go back to the site and do more work to make sure there is no other blockages in the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 34765 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-03-14 20:39 | 2013-03-15 | 2013-03-15 15:17 | 603 | gallons | F18 029 2532 Grand Canyon Corridor 2532 Grand Canyon Corridor Ground | Untreated Release An overflow was reported at the above listed location as a result of the contractor error. This address above is located in new housing development. The City found 2 mandrel nylon rope reels and several large bundles of rope blocking the pipe that was left from the contractor. This was not the result of capacity concerns the City flushed the line and removed the debris. The overflow was cleaned up the City will go back to the site and do more work to make sure there is no other blockages in the line. This overflow was to the ground only and did not reach or adversely affect a regulated water body. | The City flushed the line to remove the blockage. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City will go back to the site and do more work to make sure there is no other blockages in the line. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 35558 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-05 | 2013-04-05 23:59 | 2013-04-08 09:02 | 0 |  | S 15 011 & S15 005 Clive Ave and Philley Ave Ground | Untreated Release While doing routine manhole investigations on 4/5/13 it appears an overflow occurred at the above listed locations to the ground only. The line is down and flowing normal. Cause and volume for the overflow is unknown. Upon speaking with a nearby homeowner the City informed on 4/5/13 the overflowed likely occurred at some point between March 5th 2013 and March 11th 2013. The WWTP flow on March 5th was 62.853 MG and 70.513 MG on March 11th. The overflow was to the ground only and did not reach or adversely affect a regulated waterbody. | the areas around the manholes was leaned up. the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and /or minimize overflows in the sewer collection system. The City will monitor this area. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system.
15335 | 35799 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-11 08:19 | 2013-04-11 10:30 | 2013-04-15 08:36 | 0 |  | 302 McKinnie Ave Basement | Untreated release Rain 1.670 inches. A basement backup was reported at the above listed address located in the combined sanitary sewer system. The City flushed the line to remove any potential partial blockages. however it cannot be determined if the homeowner s private lateral contributed to the incident. The backup was not a result of a capacity issue. The backup event did not result in a discharge or adversely effect and regulated water body. | The City flushed the line. the City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 37400 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-11 08:19 | 2013-04-11 10:30 | 2013-04-11 14:00 | 0 |  | 302 McKinnie Ave Basement | Untreated Release Rain 1.670 inches. A basement backup was reported at eh above listed address located in the combined sanitary sewer system. The City flushed the line to remove any potential partial blockages. However it cannot be determined if the homeowner s private lateral contributed to the incident. The backup was not a result of a capacity issue. The backup event did not result in a discharge or adversely effect a regulated water body. | The City flushed the line. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 35801 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-12 11:10 | 2013-04-12 13:10 | 2013-04-15 08:36 | 0 |  | Calvary Baptist Church Hazelette Rd Hazelette Rd and St Joe Center Rd Basement | Untreated Release Rain 1.750 inches. A basement backup was reported at the above listed address which is located in the separated sanitary sewer system. The City flushed the line to remove a potential partial blockage. However it cannot be determined if the homeowner s private lateral contributed to the incident. The backup was not a result of the capacity issue. The backup event did not result in a discharge or adversely effect a regulated waterbody. | The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 37401 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-12 11:10 | 2013-04-12 13:10 | 2013-04-12 14:30 | 0 |  | Calvary Baptist Church Hazelett Rd Hazelett Rd and St Joe Center Rd Basement. | Untreated Release Rain 1.750 inches. A basement backup was reported at the above listed address which is located in the separated sanitary sewer system. The City flushed the line to remove a potential partial blockage. However it cannot be determined if the homeowner s private lateral contributed to the incident. The backup was not a result of a capacity issue. The backup event did not result in a discharge or adversely effect a regulated water body. | The City flushed the line. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 36049 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-16 23:50 | 2013-04-17 09:00 | 2013-04-18 13:04 | 0 |  | 4038 Maplecrest Road | A basement backup occurred as a result of the line being hit during a water line repair. | The city repaired and flushed the line to remove any potential partial blockages. Could not be determined if homeowner s private lateral contributed to the incident. The backup was not a result a capacity issue.The city continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 37404 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-16 23:50 | 2013-04-17 09:00 | 2013-04-17 14:00 | 0 |  | 4038 Maplecrest Rd Basement. | Untreated Release Rain 0.510 inches. A basement backup was reported at the above listed address located in the separate sanitary sewer system. The line was hit during a water repair. The City repaired and flushed the line to remove any potential partial blockages. However it cannot be determined if the homeowner s private lateral contributed to the incident. Backup was not a result of a capacity issue. The backup event did not result in discharge or adversely effect a regulated water body. | The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement its approved CMOM and SCCOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 36371 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-18 | 2013-04-19 23:59 | 2013-04-24 14:39 | 0 |  | Basements Affected: 1720 Paveys Glen Run 1818 Paveys601 Lyell Ct5920 Southcreat2802 Dellview2009 Chochtimar Trail1722 Cinnamon Rd3200 Irvington Dr5010 Southwood Ave4834 Montrose Ave2204 Vance Ave3112 Beaver Ave. | Untreated Release Rain 3.03 inches Extreme wet weather created conditions resulting in discharges from the City s separate sanitary sewer system described on the attached notwithstanding the City s compliance with it s CMOM and NPDES Permit. Specifically fort Wayne received a total of 2.99 inches of rain in an 18 hour period during April 18-19. That 2.99 inches was immediately preceded by 8 consecutive days of rain totaling 2.29 inches. Such preceding conditions saturated area soil and elevated river levels so as to significantly exasperate the impact of the additional rainfall on April 18-19. Ultimately the conditions on April 18-19 had a effect of being greater than a 10 year storm event. This coupled with rising rivers also resulted in the city using remote pumps throughout the impacted area to avoid or mitigate severe property damage and street flooding. The City listed the original call to IDEM above but kept in touch with IDEM several time throughout the wet weather event process. | The City utilized it s best efforts leading up to and throughout the extreme event and as explained above the City mitigated damages to property with emergency pumping. Furthermore the City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. IN addition to the actions above the City continues to utilize it s best efforts to comply with it s NPDES Permit and implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 37414 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-18 | 2013-04-19 23:59 | 2013-04-19 14:00 | 0 |  | Manhole# L23 013 St Mary s River | Untreated Release Rain 3.03 inches. Extreme wet weather created conditions resulting in discharges from the City s separate sanitary sewer system described on the attached notwithstanding the City s compliance with its CMOM and NPDES Permit. Specifically Fort Wayne received a total of 2.99 inches of rain in an 18 hour period during April 18-19. That 2.99 inches was immediately preceded by 8 consecutive days of rain totaling 2.29 inches. Such preceding conditions saturated area soils and elevated river levels so as to significantly exasperate the impact of the additional rainfall on April 18-19. Ultimately the conditions on April 118-29 had an effect of being greater than a 10 year storm event. This coupled with rising rivers also resulted in the City using remote pumps throughout the impacted area to avoid or mitigate severe property damage and street flooding. The City listed the original call to IDEM above but kept in touch with IDEM several time throughout the wet weather event process. | The City utilized its best efforts leading up to and throughout the extreme event and as explains above the City mitigated damages to property with emergency pumping. Furthermore the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. In addition to the actions above the City continues to utilize its best efforts to comply with its NPDES Permit and implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property | Saint Joseph River
15335 | 36658 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-19 | 2013-04-24 | 2013-04-26 09:27 | 0 |  | Fort Wayne | Precipitation event(s) resulted in untreated release into multiple residential locations from multiple sanitary sewer manholes to surrounding ground and receiving waters. | City using remote pumps to avoid or mitigate severe property damage and flooding. City continues to implement its approved CMOM and CSSOP programs which include many preventative manintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup; SSO Reached Public Land; SSO Affected Private Property | Maumee River; Saint Marys River; Spy Run Creek
15335 | 37012 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-19 11:20 | 2013-04-19 02:00 | 2013-05-17 14:29 | 75 | gallons | N15 0079 & N15 080 r4600 to 4700 S Monroe Street Ground | Untreated Release Rain 4.36 inches Upon records review the City determined the above listed manholes located in the combined sewer system were inadvertently omitted from the original incident report timely submitted to IDEM on 4/26/13. Extreme wet weather created conditions resulting in discharges from the City combined sanitary sewer system described above notwithstanding the City s compliance with it s CMOM and NPDES Permit. Specifically Fort Wayne received a total of 2.99 inches of rain in an 18 hour period during April 18-19. That 2.99 inches was immediately preceded by 8 consecutive days of rain totaling 2.29 inches. Such preceding conditions saturated area soils and elevated the river levels so as to significantly continuation of the wet weather event. This coupled with rising rivers also resulted in the City using remote pumps throughout the impacted area to avoid or mitigate severe property damage and street flooding. The City originally verbally notified IDEM on 4/19/13 | The City utilized it s best efforts leading up to and throughout the extreme event as explained above the City mitigated damages to property with emergency pumping. Furthermore the City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. IN addition to the actions above the City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 38818 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-19 11:20 | 2013-04-19 02:00 | 2013-05-17 03:00 | 75 | gallons | N15 079 & N15 080 4600 to 4700 S Monroe Street Ground | Upon records review the City determined the above listed manholes located in the combined sewer system were inadvertently omitted from the original incident report timely submitted to IDEM on 4/26/13. Extreme wet weather created conditions resulting in discharges from the City combined sanitary sewer system described above nothwithstanding the City s compliance with it s CMOM and NPDES Permit. Specifically Fort Wayne received a total of 2.99 inches of rain in and 18 hour period during April 18-19. That 2.99 inches was immediately proceeded by 8 consecutive days of rain totaling 2.29 inches. Such proceeding conditions saturated area soils and elevated the river levels so as to significantly exasperate the impact of the additional rainfall on April 18-19. Ultimately conditions on April 23-24 resulting in continuation of the wet weather event. This coupled with rising rivers also resulted in the City using remote pumps throughout the impacted area to avoid or mitigate severe property damage and street flooding. The City originally verbally notified IDEM on 4/19/13. | The City utilized its best efforts leading up to and throughout the extreme event as explain above the City mitigated damages to property with emergency pumping. Furtherrmore the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. In addition to the actions above the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and /or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 37398 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-19 15:18 | 2013-04-22 01:30 | 2013-06-06 10:09 | 33375000 | gallons | Outfall #001 Static Aerator/dechlorination partial bypass Maumee River. | Bypass of Treatment Process Rain 3.01 inches. The City of Fort Wayne received a total of 3.01 of rainfall of rainfall of which 2.99 was received in 18 hours. As a result of high river elevations (moderate flood stage) caused by the rainfall the Maumee River caused a hydraulic restriction of the treatment plant. This restriction then caused the plant to began backing-up. As a result the plant slowed pumping to as low as 45 MGD flow rate. | In order to increase plant flow relieve the collection system and lesson CSO discharges throughout the system 3-12 (approx. 6MGD each) pumps were brought in to pump final treated plant effluent of pond 3. This effluent was pumped over the pond bank into the Maumee River in the same location as the normal plant effluent. This action did cause a bypass of the static aerators and dechlorination processes. Effluent from the pumps was tested each day for D.O. and TRC. The D.O. average values were 8.58 on (4/19) 8.74 (4/20) and 9.19 (4/21). Effluent TRC s were 0.267 on (4/19) <0.003 (4/20) and (4.21). Effluent TRC s were 0.267 on (4/19) <0.003 (4/20) and <0.003 (4/21). TRC and D.O. was tested 200 yards downstream at Coliseum Blvd. TRC was found to be below detection limits each day and the D.O. was 8/80 or better for each day. The City of Fort Wayne is currently designing and effluent pump station with a build completion date of 2015. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Maumee River
15335 | 36075 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-19 15:18 | 2013-04-22 01:30 | 2013-04-23 14:22 | 33375000 | gallons | Outfall #001 Static aerator/Dechlorination partial bypass Maumee River | Bypass of a Treatment Process Rain 3.01 inches The City of Fort Wayne received a total of 3.01 of rainfall of which 2.99 was received in 18 hours. As a result of high river elevations (moderate flood stage) caused by the rainfall the Maumee River caused a hydraulic restriction of the treatment plant. This restriction then caused the plant to begin backing-up. As a result the plant slowed pumping to as low as 45 MGD flow rate. | In order to increase plant flow relieve the collection system and lesson CSO discharges throughout the system 3-12 (approx 6 MGD each) pumps were brought in to pump final treated plant effluent of pond 3. This effluent was pumped over the pond bank into the Maumee River in the same location as the normal plant effluent. This action did cause a bypass of the static aerators and dechlorination processes. Effluent from the pumps was tested each day for D.O. and TRC. The D.C. average values were 8.58 on (4/19) 8.74 (4/20) and 9.19 (4/21). Effluent TRC s were 0.267 on (4/19) <0.003 (4/20) and <0.003 (4/21). TRC and D.O. was tested 200 yards downstream at Coliseum Blvd. TRC was found to be below detection limits each day and the D.O. was 8.80 or better for each day. The City of Fort Wayne is currently designing and effluent pump station with a build completion date of 2015. | SSO Reached Receiving Water | Maumee River
15335 | 37237 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-01 | 2013-05-05 23:59 | 2013-05-28 14:48 | 891750 | gallons | Griswold Pump Station St Mary s River | Untreated Release Construction Related Upon routine review of CSO data the Griswold Pump Station appears to have pumped between may 1 to May 5 2013. The City s SCADA system shows the dewatering pumps in the wet well pumped during the following times: 5/1/13 - (1.3 hours); 5/2/13 - (59) minutes; 5.3.13 - (44 minutes); 5/4/13 - (17 minutes); 5/5/13 - (4 minutes). During this time it is possible ground water was rising in the wet well thus causing dewatering pumps to turn on. Upon further investigation into the matter and error was discovered in the way the Griswold Pump Station was programmed during recent construction (new pumps and pump controls were recently installed by a third party contractor). As a result the City has reconfigured the way the station operates. The WWTP flow during the described event is as follows 5/1/13 70.395 MGD; 5/2/13 - 70.485 MGD; 5/3/13 - 68-647 MGD 5/4/13 - 64.203 MGD 5/5/13 - 62.418 MGD | The City reconfigured the operation of pumps at the station. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activates designed to prevent and/or minimize overflows in the sewer collection system. The its reconfigured the operation of pumps at the station. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Saint Marys River
15335 | 38793 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-01 07:45 | 2013-05-05 07:45 | 2013-05-24 08:00 | 891750 | gallons | Griswold Pump Station St. Mary River | Untreated release Construction Related. Upon routine review of CSO data the Griswold Pump Station appears to have pumped between May 1st to May 5th 2013. The City s SCADA system shows the dewatering pumps in the wet well pump during the following times. 5/1/13 (1.3 hours); 5/2/13 (59 minutes) 5/3/13 (44 minutes) 5/4/13 (17 minutes); 5/5/13 (4 minutes). During this time it is possible ground water was rising in the wet well thus causing the dewatering pumps to turn on. Upon further investigation into the matter an error was discovered in the way the Griswold Pump Station was programmed during recent construction (new pumps and pump controls were recently installed by a third party contractor). As a result the City has reconfigured the way the station operates. The WWTP flow during the described event is as follows 5/1/13 - 70.395 MGD 5/2/13 70.485 MGD; 5/3/13 70.485 MGD 5/3/13 68.647 MGD; 5/4/13 64203 MGD; %/5/13 62.418 MGD. | The City reconfigured the operation of pumps at the station. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City reconfigured the operation of pumps at the station. The City continues to implement it approved CMIOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimizeoverflows in the sewer collection system. | SSO Affected Private Property | Saint Marys River
15335 | 36782 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-01 10:42 | 2013-05-01 14:30 | 2013-05-02 09:01 | 500 | gallons | S66 013 4411 Park Place Drive | The 8 inch separate sanitary line was plugged down stream in the manhole at the drop connection. Result was Sanitary sewer overflow of untreated release to surrounding ground. | Heavy rags and grease are thought to be the cause of the plug. The City was able to remove a section of the pipe in the manhole which allowed the line to flow properly.The City wil encourage the nursing home directly up stream of the plug not to flush their disposable towels and wips in the sanitary sewer.The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Public Land
15335 | 38821 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-01 10:42 | 2013-05-01 14:30 | 2013-05-01 14:00 | 0 |  | S66 013 4411 Park Place Dr Ground | Untreated Release The 8 inch sperate sanitary line was plugged down stream in the manhole at the drop connection. Heavy rags and grease are thought to be the cause of the plug. The City was able to remove a section of the pipe in the manhole which allowed the line to flow properly. The discharge was to the ground only it did not reach a waterbody. | The City will encourage the nursing home directly up stream of the plug not to flush there towels and wipes in the sanitary sewer. The City will continue to implement its CMOM and CSSOP programs. | SSO Affected Private Property
15335 | 38794 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-03 01:18 | 2013-07-29 03:00 | 2013-05-03 09:00 | 0 |  | 808 Countrywood Basement. | Untreated Release A basement backup was reported at the above listed address located in the sperate sanitary sewer system. The City flushed the line to remove any potential partial blockages. However it cannot be determined if the homeowner s private lateral contributed to the incident. The backup as not a result of a capacity issue. The backup event did not result in a discharge or adversely effect a regulated water body. | The City flushed the line. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 36752 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-03 01:18 | 2013-05-03 03:00 | 2013-05-03 08:26 | 0 |  | 808 Country Wood Place | An unknown cause resulted in an untreated release to residential basement. Can t be determined if homeowners private lateral contributed to the backup. | The City flushed the line to remove any potential partial blockages.The city continues to implement it approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 38738 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-03 01:18 | 2013-05-03 03:00 | 2013-05-03 09:00 | 0 |  | 808 Country Wood Pl Basement | Untreated Release A basement backup was reported at the above listed address located in the separate sanitary sewer system. The City flushed the line to remove any potential partial blockages. However it cannot be determined if the homeowner s private lateral contributed to the incident. The backup was not a result of a capacity issue. The backup event did not result of a capacity issue. The backup event did not result in a discharge or adversely effect a regulated water body. | The City flushed the line. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and /or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 36863 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-13 12:32 | 2013-05-13 14:00 | 2013-05-14 13:36 | 0 |  | 1716 & 1730 Cinnamon Road 1730 Cinnamon Rd Basement | Untreated Release A basement backup was reported at the above listed addresses located in the separate sanitary sewer system. The City flushed and root sawed the line to remove roots and any potential blockages. However it cannot be determined if the homeowner s private lateral contributed to the incident. The backup was not a result of a capacity issue. The backup event did not result in a discharge or adversely effect a regulated water body. | The City flushed the line. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Basement Backup
15335 | 36862 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-13 12:32 | 2013-05-13 14:00 | 2013-05-14 13:32 | 0 |  | 1716 & 1730 Cinnamon Rd 1730 Cinnamon Rd Basement | Untreated Release A basement backup was reported at the above listed addresses located in the separate sanitary sewer system. The City flushed and root sawed the line to remove roots and any potential blockages. However it can not be determined if the homeowner s private lateral contributed to the incident. The backup was not a result of a capacity issue. The backup event did not result in a discharge or adversely effect and regulated water body. | The City flushed the line. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement it s approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 37571 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-30 13:00 | 2013-05-30 13:30 | 2013-06-03 14:02 | 200 | gallons | P10 041 | A break in a 24 inch pipe resulted in a cave in blockage and overflow to receiving water. | The City began excavating the site to make the repair. The City then contracted with a private contractor to continue making the repair. The City removed debris from pipe and bypass pumped to an adjacent manhole to avoid further overflows. The overflow was cleaned up. The private contractor completed the repair on 5/31/13. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City will line this section of pipe to avoid other issues. | SSO Reached Receiving Water | Maumee River
15335 | 37997 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-31 | 2013-06-01 | 2013-06-19 09:00 | 0 |  | (Ground) 5360 Glendale 4542 Maplescrest 6625 Monle Ave EII 018 | Extreme wet weather created conditions resulting in discharged form the City s sewer system listed on Attachments B&C notwithstanding the City s compliance with it s CMOM CSSOP and NPDES Permit. The City of Fort Wayne received approximately 4.59 inches in a 3 hour time frame. Such conditions exceeded th 100 year storm and caused the Maumee River to increase roughly 14 feet in less than a few hours. This storm event and rising river levels necessitated the City to use remote pumps in certain areas to avoid or mitigate severe property damage and street flooding. In addition to the discharges to water bodies reflected on Attachment B&C Attachment B includes discharges that not reach a regulated water body. Reports were sent to IDEM in an abundance for informational purpose. Some or all of those backups may have been caused by problems due to structures not owned or contrtolled by the City. | The City mitigated damages to properties with emergency pumping (see Attachment C). Furthermore the City continues to implement its approved CMOM and CSSOP program which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 37649 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-31 | 2013-06-01 | 2013-06-07 14:57 | 0 |  | (GROUND) 5630 Glendale 4542 maplecrest 6625 Monte Ave Ell 018 | Rain 4.59 inches. Extreme wet weather created conditions resulting in discharges from the City s sewer system listed on Attachments B & C notwithstanding the City s compliance with its CMOM CSSOP and NPDES Permit. Specifically Fort Wayne Received approximately 4.59 inches of rain in less than a 18 hour period including more than 3.69 inches in a 3-hour time frame. Such conditions well exceeded those of a 100 year storm event and caused the Maumee River to increase roughly 14 feet in less than a few hours. This 100 year plus storm event and rising river levels necessitated the City s use of remote pumps in certain areas to avoid or mitigate severe property damage and street flooding. In addition to the discharges to water bodies reflected on Attachments B & C Attachment B includes discharges that did not reach a regulated water body. Similarly Attachment B reflects possible basement backup events reported to the City. Some or all of those backups may have been caused by problems due to structures not owned or controlled by the City. | As mentioned above the City mitigated damages to properties with emergency pumping (see Attachment C). Furthermore the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 37979 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-31 | 2013-06-01 | 2013-06-19 08:39 | 0 |  | (Basement Affected) 1922 Forest Valley Dr1720 &1818 Pavehs Glen Run 6216 Monarch Dr 6720 Kirkdale Dr7705 Harcourt Dr8099 Mystic Dr 6201 Manchester Dr3216 Portage Blvd 2009 Chochtimar Trl 2125 Curdes Ave1018 Pemberton Dr1049 Tennessee Ave 2203 Kenwood Ave2218 Lynn Ave4262 Reed424 E Wildwood Ave & 922 W Wildwood Ave4636 Weisser Park 2118 Edgehill Ave 17131802 1805 1809 18121813 1817 1909 Emerson Ave | Rain 4.59 inches Extreme wet weather created conditions resulting in discharges from the City s sewer system listed on Attachments B&C notwithstanding the City s CMOM CSSOP and NPDES permit. Fort Wayne received approximately 4.59 inches in a 3 hour time frame this exceeded the 100 year storm event and caused the Maumee River to increase roughly 14 feet in a few hours. The City s used remote pumps in certain areas to avoid or mitigate severe property damage and street flooding. In addition to discharges to water bodies reflected on Attachments B&C Attachment B includes discharges that did not reach a regulated water body. Attachment B reflects possible basement backup events reported to the City. Some or all of those backups may have been caused by problems due to structures not owned or controlled by the City. Reports submitted to IDEM in an abundance of caution for informational purposes. | See Attachment A | SSO Basement Backup
15335 | 37774 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-06-10 16:30 | 2013-06-10 18:45 | 2013-06-11 13:00 | 135 | gallons | 2920 Reed Rd T18 015 | Unknown An overflow occurred to the ground only at the above listed location in the separate sanitary sewer system. The City flushed the line to remove the blockage. The event was not a result of a capacity issue. The overflow was to the ground only and did not reach or adversely affect a regulated waterbody. | The City flushed line and the overflow was cleaned up. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City flushed line and the overflow was cleaned up. The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property
15335 | 39084 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-06-24 21:55 | 2013-06-24 23:15 | 2013-06-27 03:29 | 0 |  | 9661 Coverdale Rd D43 006 | The City of fort Wayne had extremely high winds (excess of 60mph) on 6/24/13 This caused a tree to fall on the power line that supplies power to the pump station. The City uses a portable generator to supply power until the main line power could be restored. | See Report | SSO Reached Receiving Water
15335 | 39562 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-07-16 19:15 | 2013-07-16 19:30 | 2013-07-17 14:02 | 0 |  | 9661 Coverdale Rd D43 006 | Power Failure the station lost power for a brief time. Immediately after losing power the City took a portable generator out to restore the power. Before the City could connect the generator the main power feed was back online. It is not known why the station had a break in power. | See Report | SSO Reached Receiving Water | Robinson Brindle Creek
15335 | 39565 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-07-16 19:15 | 2013-07-16 19:30 | 2013-07-17 03:37 | 0 |  | 9661 Coverdale Rd D43 006 | Power Failure The station lost power for a brief time. Immediately after losing power the City took a portable generator out to restore the power. Before the City could connect the generator the main power feed was back online. It is not know why the station had a break in power. | See Report | SSO Reached Receiving Water | Robinson Brindle Creek
15335 | 39563 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-07-16 20:00 | 2013-07-16 09:15 | 2013-07-17 14:12 | 0 |  | W18 030 2228 Cimarron Pass | An overflow occurred at the above listed location in the separate sanitary system. The City flushed the line to remove the blockage. The event was not result of a capacity issue. | See Report | SSO Reached Receiving Water | Bullerman Ditch
15335 | 39599 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-07-24 14:21 | 2013-07-24 18:00 | 2013-07-24 23:20 | 0 |  | 3320 West Ferguson Rd | An overflowed occurred at the above listed location in the separate sanitary system. The city root sawed the line to remove the blockage. The event was not a result of a capacity issue. The overflow was to the ground only and did not reach or adversely impact a regulated waterbody. | Removed Blockage See Report | SSO Affected Private Property
15335 | 39330 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-08-02 14:02 | 2013-08-03 14:03 | 2013-08-03 09:00 | 0 |  | Bluffton Road Baer Road | Rain 3.59 inches Extreme wet weather created conditions resulting in discharges from the City s sewer system described in the attached notwithstanding the City s compliance with its CMOM CSSOP and NPDES Permit. Specifically Fort Wayne received 3.59 inches of rain in a short duration far exceeding a 10-year wet weather event. See attached for specific locations. This is 3 of 3 reports concerning this wet weather event. | Normal 0 false false false EN-US X-NONE X-NONE MicrosoftInternetExplorer4 The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The City continues to implement its approved CMOM and CSSOP programs which included preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system | SSO Reached Receiving Water | Fairfield Ditch; Saint Marys River
15335 | 39333 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-08-02 14:51 | 2013-08-03 14:51 | 2013-08-03 09:00 | 0 |  | BASEMENTS: 807 Florence Ave 727 Florence Ave 5021 Buell Dr 4407 Karen Ave 1716 Richardson Ave 1049 Tennesee Ave 4010 Arkington Ave 6816 Arlington Ave 5021 Fairfield Ave 2407 Sandpoint 5920 Southcrest Dr 926 E. Hawthorne St 402 W. Paulding Rd 2402 Oakridge Rd 6816 Winnebago | Rain 3.59 inches Extreme wet weather created conditions resulting in discharges from the City s sewer system described in the attached notwithstanding the City s compliance with itsCMOM CSSOP and NPDES Permit. Specifically Fort Wayne received 3.59 inches of rain in a short duration far exceeding a 10-year wet weather event. See attached for specific locations. This is 2 of 3 reports concerning this wet weather event. | The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. The backup event did not result in a discharge or adversely affect a regulated waterbody. | SSO Basement Backup
15335 | 39336 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-08-02 15:07 | 2013-08-03 15:07 | 2013-08-03 09:00 | 0 |  | M18 231 Spy Run Creek 600 Blk Poplar Ground 131092 Ground 131094 Ground L18 129 St. Mary s River L18 088 St. Mary s River X18 003 Ground | Extreme wet weather created conditions resulting in discharges from the City s sewer system described in the attached notwithstanding the City s compliance with its CMOM CSSOP and NPDES Permit. Specifically Fort Wayne received 3.59 inches of rain in a short duration far exceeding a 10-year wet weather event. See attached for specific locations. This is 1 of 3 reports concerning this wet weather event. | The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. Overflows to the ground only did not reach or adversely affect a regulated waterbody.The City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system | SSO Affected Private Property; SSO Reached Receiving Water | Saint Marys River; Spy Run Creek
15335 | 39372 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-08-05 11:00 | 2013-08-05 11:20 | 2013-08-05 11:30 | 0 |  | Abandoned storm outfall near 73440 St Joe Rd at Rothman Rd. | Unknown Upon further investigation and televising results it was determined that City s 8 inch sanitary line was leaking into an abandon 18 inch storm outfall pipe. the City made the repair on the 8 inch line and plugged the abandoned storm line to prevent recurrence. The overflow that reached the creek was cleaned up by a private contractor. | See Report | SSO Reached Receiving Water
15335 | 39374 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-08-11 14:49 | 2013-08-11 14:49 | 2013-08-12 09:00 | 0 |  | 3104 Canterbury Blvd Q30 025 | An overflow occurred in the above listed separate sanitary sewer line. The City flushed and removed a partial blockage. The overflow was to the ground only and did not reach or adversely affect a regulated waterbody. | See Report | SSO Reached Public Land
15335 | 40012 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-08-28 09:45 | 2013-08-28 10:00 | 2013-09-04 15:00 | 0 |  | M10 306 | The (Lamplight Inn Assisted Living Building) was testing the fire sprinkler system located in the building s basement. The facility pumped water from the fire system out to the street ultimately entering storm inlets in the combined sewer system. The event was originally reported as a water main break. The City discovered this caused a discharge at the above listed NPDES permitted CSO outfall as part of routine weekly data downloads. This event was not due to a capacity issue. | See Report | SSO Reached Receiving Water
15335 | 40019 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-09-05 10:00 | 2013-09-05 11:30 | 2013-09-05 15:00 | 0 |  | Between N30 142 & N30 159 725 Camden Dr. | Unknown While smoke testing the separate sanitary sewer line a City crew discovered that the separate sanitary line was cracked. The City bypassed pump from N30 142 to N30 152 until the line was repaired. | Repaired Pipe See Report
15335 | 40678 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-10-01 11:30 | 2013-10-01 08:50 | 2013-10-01 14:30 | 0 |  | 400 East of Ardmore & Engle Rd Ardmore Ave and Engle Rd | Force Main The City was notified at 11:30 on 10/01/2013 that a break in the forcemain occurred. The total volume cannot be determined. The overflow resulting from the break was to the ground only and did not reach or adversely affect a regulated waterbody. The overflow was cleaned up and the pipe was repaired. | Repaired Pipe See Report | SSO Reached Public Land
15335 | 41860 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-10-10 10:39 | 2013-10-10 10:40 | 2013-11-14 14:00 | 0 |  | Griswold Pump Station 1130 Spy Rrun Ave | Construction Related While making repairs to a pump at the Griswold Pump Station a contractor tested the pump causing a brief dry weather overflow of less than one minute duration. The City learned of this malfunction from reviewing the SCADA data and the report issued from the contractor. Based on SCADA data and contractor report review the City is submitting this dry weather overflow incident report. | Repaired Pump Station See Report | SSO Reached Receiving Water | Saint Marys River
15335 | 43095 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-12-22 | 2013-12-22 | 2013-12-22 13:00 | 0 |  | M18 231 | See Attachment A | See Attachment A | SSO Reached Receiving Water | Spy Run Creek
15335 | 43094 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-12-22 | 2013-12-22 | 2013-12-22 13:00 | 100000 | gallons | See Attachment B | See Attachment A | See Arrachment A | SSO Reached Receiving Water | Fairfield Ditch; Saint Marys River; Krunkenburg Ditch
15335 | 43763 | IN0032191 | Fort Wayne Water Pollution Control Plant | Allen | 2013-12-30 08:41 | 2013-12-30 10:25 | 2013-12-30 12:12 | 600 | gallons | V62 162 6915 Baswin CV | An overflow occured from the above listed separate sanitary sewer line. The line was blocked by concrete and sand. The City flushed to open the line. The overflow was cleaned up. | Removed Blockage See Report | SSO Reached Receiving Water | Saint Joseph River
15335 | 37949 | IN0032191 (Affected Waterbody) Not Listed: Krunkenberg Drain Robinson Brindle Creek | Fort Wayne Water Pollution Control Plant | Allen | 2013-06-12 23:30 | 2013-06-13 06:30 | 2013-06-14 12:09 | 0 |  | Wildwood/Wildmere K07 029 Baer Rd H27 044 Hartman Rd K15 167 Chaucer & Lynnhurst T34 009 Monarch Dr V14 020 Coverdale Lift Station | Unknown Rain 2.63 inches. Extreme wet weather created conditions resulting in discharges from the City s sewer system in compliance with its CMOM CSSOP and NPDES Permit. The City of Fort Wayne received approximately 2.63 inches of rain. The City used remote pumps in certain areas to avoid or mitigate sever property damage and street flooding. These events are listed in Attachment B. This list is reported to IDEM for informational purpose. | The City of Fort Wayne preformed emergency pumping and continues to implement it s approved CMOM and CSSOP programs. Continue to use preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Maumee River; Saint Marys River
15335 | 37476 | IN0032191 (Krunkenburg Ditch water body was effected also it isn t listed in the drop down option yet.) | Fort Wayne Water Pollution Control Plant | Allen | 2013-04-19 14:00 |  | 2013-04-19 14:00 | 0 |  | (Bullerman Ditch Manhole:)X18 192 X18 193 X18 001 X18 002 X18 003 (Krunkenburg Ditch Manholes:) T34 024 T34 028 T46 089 T46 004 T34 027 T38 008 and Vesey Park. (Spy Run Creek Manholes:) M18 231 L18 129 L18 088 T38 008 and Well Street Siphon | Untreated Release Rain 4.36 inches. Extreme wet weather created conditions resulting in discharges from the City s separate sanitary sewer system described on the attached notwithstanding the City s compliance with its CMOM and NPDES Permit. Specifically Fort Wayne received a total of 2.99 inches of rain in an 18 hour period during April 18-19. That 2.99 inches was immediately preceded by 8 consecutive days of rain totally 2.29 inches. Such preceding conditions saturated area soils and elevated river levels so as to significantly exasperate the impact of the additional rainfall on April 18-19. Ultimately the conditions on April 18-19 had a effect of being greater than a 10 year storm event. This coupled with rising rivers also resulted in the City using remote pumps throughout the impacted area to avoid or mitigate severe property damage and street flooding. The City listed the original call IDEM above but kept in touch with IDEM several time throughout the wet weather event process. | The City utilized its best efforts leading up to and throughout the extreme event and as explained above the City mitigated damages to property with emergency pumping. Furthermore the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. In addition to the actions above the City continues to utilize its best efforts to comply with its NPDES Permit and implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Spy Run Creek; Bullerman Ditch
15335 | 37676 | IN0032191 Krunkenburg Ditch isn t an option in Affected Waterbody List yet. | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-31 | 2013-06-01 | 2013-06-07 14:57 | 0 |  | Bullerman Ditch Manhole: X18 001 X18 002 Flaugh Ditch Manhole: E03 019 Krunkenburg Ditch Manhole M18 231 T34 024 T34 028 Spy Run Creek Manhole: Spy Run Creek Manhole L18 129 Maumee River Manhole: V06 001 | Rain 4.59 inches. Extreme wet weather created conditions resulting in discharges from the City s sewer system listed on Attachments B&C notwithstanding the City s compliance with its CMOM CSSOP and NPDES Permit. Specifically Fort Wayne received approximately 4.59 inches in a 3-hour time frame. Such conditions well exceeded those of a 100 year storm event and cause the Maumee River to increase roughly 14 feet in less than a few hours. This 100-year plus storm event and rising river levels necessitated the City s use of remote pumps in certain areas to avoid or mitigate severe property damage and street flooding. In addition to the discharges that did not reach a regulated water body. Such re reported to IDEM in an abundance of caution for informational purposes. Similarly Attachment B reflects possible basement backup problems due to structures not owned or controlled by the City. | As mentioned above the City mitigated damages to properties with emergency pumping (see Attachment C). Furthermore the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property | Flaugh Ditch; Maumee River; Saint Marys River
15335 | 40990 | IN0032191 Outfall 010 251 | Fort Wayne Water Pollution Control Plant | Allen | 2013-10-09 14:28 | 2013-10-11 09:30 | 2013-10-11 13:49 | 0 |  | 010251 1614 Edgewater Ave | The grinder pumps in the combined sewer pump station became clogged thus resulting in the wetwell to fill and overflow the weir into the storm wetwell. As a result pumps in the filled wetwell activated and intermittently pumped to the receiving water during dry weather. | See Report | SSO Reached Receiving Water | Maumee River
15335 | 38002 | IN0032191 Water Body Affected: Krunkenburg Ditch | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-31 | 2013-06-01 | 2013-06-19 09:00 | 0 |  | (Manhole) 062 080 X18 001 X18 002 E03 019 M18 231 T34 024 T34 028 L18 129 V06 001 | Rain 4.59 inches. Extreme wet weather created conditions resulting in discharges from the City s sewer system listed on Attachments B&C the City s compliance with its CMOM CSSOP and NPDES Permit. The City of Fort Wayne received approximately 4.59 inches of rain in less than a 18 hour period. Such condition well exceeded those of a 100 year storm event and caused the Maumee River to increase roughly 14 feet in less than a few hours. The City used remote pumps in certain areas to avoid or mitigate severe property damage and street flooding. In addition to the discharges to water bodies reflected on Attachment B&C Attachment B includes discharges that did not reach a regulated water body. Such reports went to IDEM in an abundance for informational purposes. | AS mentioned above the City mitigated damages to properties with emergency pumping (see Attachment C). Furthermore the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Reached Receiving Water | Flaugh Ditch; Maumee River; Saint Marys River
15335 | 37674 | IN0032191 Waterbody Affected: Krunkenburg Ditch it wasn t a listed option. | Fort Wayne Water Pollution Control Plant | Allen | 2013-05-31 | 2013-06-01 | 2013-06-07 14:57 | 0 |  | Bulleman Ditch Manhole: X18 001 X18 002 Flaugh Ditch Manhole: E03 019 Krunkenburg Ditch Manholes: M18 231 T34 024 T34 028 Spy Run Creek: Spy Run Creek: L18 129 Maumee River Manhole: V06 001 | Rain 4.59 inches. Extreme wet weather created conditions resulting in discharges from the City s sewer system listed on Attachments B&C notwithstanding the City s compliance with its CMOM CSSOP and NPDES Permit. Specifically Fort Wayne received approximately 4.59 inches of rain in less than an 18 hours period including more than 3.69 inches in a 3 hour time frame. Such conditions well exceeded those of a 100 year storm event and caused the Maumee River to increase roughly 14-feet in less than a few hours. This 100 year plus storm event and rising river levels necessitated the City s use of remote pumps in certain areas to avoid or mitigate severe property damage and street flooding. In addition to the discharges that did not reach a regulated water body. Such are reported to IDEM in an abundance of caution for informational purposes. Similarly Attachment B reflects possible basement backup problems due to structures not owned or controlled by the City. | As mentioned above the City mitigated damages to properties with emergency pumping (see Attachment C). Furthermore the City continues to implement its approved CMOM and CSSOP programs which include many preventative maintenance activities designed to prevent and/or minimize overflows in the sewer collection system. | SSO Affected Private Property | Flaugh Ditch; Maumee River; Saint Marys River
15335 | 41645 | IN0032191 T10 042 | Fort Wayne Water Pollution Control Plant | Allen | 2013-11-03 12:44 | 2013-11-03 16:30 | 2013-11-04 10:30 | 0 |  | T 10 043 5232 Nassau Dr | An overflow occurred from the above listed seperate sanitary sewer line. The line was paretically blocked with roots. The City flushed and root sawed to open the line. The overflow was cleaned up. | Removed Blockage See Report | SSO Reached Receiving Water | Maumee River
15295 | 34708 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-01-12 07:30 | 2013-01-14 01:00 | 2013-01-14 08:44 | 1250000 | gallons | M/H C30-19A Beside Lift Station | Due to excessive rain snow melt and saturated ground conditions an approximate total of 1250000 gallons were diverted to Discharge 101 on 1/12/2013 and 1/13/2013. A minimum of 6.0 MGD was maintained to aeration at all times. | Flow from rain and snow melt abated on 1/14/2013. A new larger F/M is under design and a new pump station upstream will be installed when F/M is constructed. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 35533 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-01-13 12:05 | 2013-01-14 01:30 | 2013-01-14 09:09 | 6000 | gallons | M/N C30-19A Beside Lift Station | Precipitation event and snow melt combined to cause an untreated release from Lift station manhole to surrounding ground and receiving water. | A new larger F/M under design and a new pump station upstream will be installed when F/M is constructed. | SSO Reached Public Land; SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 35288 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-01-13 12:05 | 2013-01-14 01:30 | 2013-03-26 15:04 | 6000 | gallons | M/H C30-19A Beside Lift Station Ground & Beal Taylor Ditch | Untreated Release Rain 3 snow melt and 1.75 inches rain. Rained heavy 1-13-13 1.5 inches Light Rain 1-14-13 .25 inches 3 inch snow melt. | Anew larger F/M under design and a new pump station upstream will be installed when F/M is constructed. | SSO Affected Private Property
15295 | 37213 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-01-13 12:05 | 2013-01-14 01:30 | 2013-05-29 11:05 | 6000 | gallons | M/HC30-19a Beside Lift Station Ground Beal Taylor Ditch | Untreated Release Rain 3 inches Snow 1.75 inches | A new Larger F/M under design and a new pump station upstream will be installed when F/M is constructed. | SSO Affected Private Property; SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 34516 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-03-10 18:24 | 2013-03-12 05:00 | 2013-03-12 20:10 | 30000 | gallons | Sycamore L/S M/H c3019 A by L/S Sycamore L/S M/H C30-19A by L/S | Untreated Release Rain .5 inches 10.4 Snow melt. 10.4 inch snow melt for 3-6-13 also light rain 3-10 & 11-13 Sycamore at 5:35AM 3-11-13 stopped overflowing but started back at 8:23AM 3-11-13 | A new larger F/M under design and also a new pump station will be installed when F/M is constructed. | SSO Affected Private Property
15295 | 36129 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 09:45 | 2013-04-19 09:45 | 2013-04-19 12:08 | 30000 | gallons | C 35-12 Dell Lock WayC 35-9 Dell Lock Way R | Precipitation event(s) caused untreated release from manholes to receiving waters |  | SSO Reached Receiving Water | Taylor Ditch
15295 | 36536 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 20:15 | 2013-04-20 09:05 | 2013-04-20 08:51 | 128000 | gallons | C30-19A by Lift StationC29-40 Sycamore Golf Course | Precipitation event(s) flow exceeded capacity of Sanitary Sewer Collection System resulting in untreated release from manholes to surrounding ground and receiving waters. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 36202 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 20:15 |  | 2013-04-19 09:01 | 0 |  | L 30-19A L 29-40 | Precipitation event triggered untreated release from manholes to surrounding ground and receiving waters. |  | SSO Reached Public Land; SSO Reached Receiving Water | Taylor Ditch
15295 | 37215 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 20:15 | 2013-04-20 09:05 | 2013-05-29 11:05 | 28000 | gallons | C30-19A by L/S C29-40 Sycamore Golf Course Ground Beal Taylor Ditch | Rain 4.2 inches |  | SSO Affected Private Property; SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37225 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 21:45 | 2013-04-19 09:45 | 2013-05-29 11:05 | 30000 | gallons | C35-12 11230 Dell Lock Way C35-9 11235 Dell Lock Way Rd Beal Taylor Ditch | Untreated Release Rain 4.2 inches |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 36204 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 21:45 |  | 2013-04-19 09:01 | 0 |  | L 35-2 L 35-9 | Precipitation event triggered untreated release from multiple manholes to receiving waters |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 36198 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 22:00 |  | 2013-04-19 09:02 | 0 |  | D 30-33 FieldD 31-131 D31-120 | Precipitation event triggered untreated release from multiple manhole locations. |  | SSO Reached Public Land
15295 | 37226 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 22:00 | 2013-04-19 10:05 | 2013-05-29 11:05 | 22000 | gallons | 030-55 Groundy Covington 030-33 Field Ground | Untreated Release Rain 4.2 inches |  | SSO Affected Private Property
15295 | 37216 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 22:00 | 2013-04-19 18:40 | 2013-04-20 09:15 | 19000 | gallons | 031 - 131 3535 031-120 West Lake Dr Ground | Rain 4.2 inches |  | SSO Affected Private Property
15295 | 36535 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 22:00 | 2013-04-19 18:40 | 2013-04-20 08:52 | 19000 | gallons | Manhole D31-131 3535 Wuterton CourtManhole D31-120 West Lake Drive | Precipitation event(s) exceeded the capacity of the sanitary sewer collection system resulting in untreated overflow from manholes to surrounding ground and retention pond. |  | SSO Reached Public Land
15295 | 36130 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 22:00 | 2013-04-19 10:05 | 2013-04-19 12:09 | 22000 | gallons | 030-55 Lift Station030-33 Field | Precipitation event(s) caused untreated release from manhole and lift station to surrounding ground. |  | SSO Reached Public Land
15295 | 36200 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-18 22:00 |  | 2013-04-19 09:01 | 0 |  | D 30-55 | Precipitation event triggered an untreated release from Lift Station to surrounding ground |  | SSO Reached Public Land
15295 | 37231 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-24 04:30 | 2013-04-25 15:30 | 2013-05-29 11:05 | 20000 | gallons | C30-19A at Sycamore L/S Ground Beal Taylor Ditch | Untreated Release Rain 1.9 inches Heavy rain over night 3:30pm to 8:00am 4.24/13 1.7 plus all rain from last week of 5.5 inches. |  | SSO Affected Private Property; SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 36609 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-24 04:30 | 2013-04-25 15:30 | 2013-04-25 15:14 | 20000 | gallons | C30-19A Sycamore Lift Station | Precipitation event(s) exceeded the capacity of a lift station resulting in untreated release to surrounding ground and receiving water. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 36635 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-24 04:30 | 2013-04-24 22:30 | 2013-04-25 08:40 | 85000 | gallons | Manhole C29-40 on golf course | High flows from precipitation event(s) cause an untreated release from a manhole to surrounding ground and receiving water. |  | SSO Reached Public Land; SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37227 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-24 04:30 | 2013-04-24 22:30 | 2013-05-29 11:05 | 85000 | gallons | C29-40 on Golf Course Ground Beal Taylor Ditch | Untreated Release Rain 1.9 inches Ground and Beal Taylor Ditch |  | SSO Affected Private Property; SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 36281 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-24 04:30 | 2013-04-24 04:30 | 2013-04-24 08:49 | 0 |  | C30-19A at Sycamore C29-40 on Golf Course Ground Beal Taylor Ditch | Untreated Release Rain 1.7 inches None at this time | Heavy rain over night 330pm 4/23/13 to 8:00am 4/24/13 1.7 inches and still raining. | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 36632 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-24 07:30 | 2013-04-24 17:45 | 2013-04-25 08:40 | 13000 | gallons | Manhole D31-120 West Lake Drive | High flow resulting from precipitation event(s) caused untreated release from a manhole to surrounding ground and an unnamed pond. |  | SSO Reached Public Land
15295 | 36286 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-24 07:30 |  | 2013-04-24 08:49 | 0 |  | D31-120 West Lake Drive Ground | Untreated Release Rain 1.7 inches Heavy rain over night 3:30pm 4/23/13 to 4/24/13 1.7 inches and still raining. |  | SSO Affected Private Property
15295 | 37229 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-04-26 07:30 | 2013-04-24 17:45 | 2013-05-29 11:05 | 13000 | gallons | D31-120 West Lake Dr Ground | Rain 1.9 inches Heavy rain over night 3:30pm 4/23/13 to 8:00am 424/13 1.7 plus all rain from last we4ek of 5.5 inches. |  | SSO Affected Private Property
15295 | 37569 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 | 2013-06-01 22:00 | 2013-06-02 12:01 | 50000 | gallons | Manhole C29-44 Golf CourseManhole C29-40 Golf Course | Follow Up report to incident report numbers 37529 and 37531 to reflect overflow stop times and overflow estimates. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37606 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 | 2013-06-02 21:00 | 2013-06-03 08:14 | 6000 | gallons | C31-7 Eggman Rd | Rain 5 inches Manhole Very heavy rain over night starting 10:00pm |  | SSO Affected Private Property
15295 | 37529 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 |  | 2013-06-01 15:13 | 0 |  | Manhole C29-21 Golf CourseManhole C29-44 Golf Course | Precipitation event triggered SSO from manholes to receiving waters. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37533 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 |  | 2013-06-01 15:08 | 0 |  | Manhole C30-20 near Sycamore Lift Station | Precipitation event triggered an untreated release from a manhole to receiving water. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37566 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 | 2013-06-01 17:45 | 2013-06-02 12:01 | 50000 | gallons | Manhole C29-50 Golf CourseManhole C29-21 Golf Course | Precipitation event flow exceeded capacity of sanitary sewer system resulting in untreated release from manholes to receiving water. | Follow up report to Incident Report 37529 reflecting time at which overflow stopped. | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37528 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 |  | 2013-06-01 15:15 | 0 |  | Manhole C29-50 Golf CourseManhole C31-7 Eggman Road | Precipitation event triggered SSO from manholes to receiving water. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37531 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 |  | 2013-06-01 15:14 | 0 |  | Manhole C29-40 Golf CourseManhole C29-22 Golf Course | Precipitation event exceeded capacity of sanitary system resulting untreated release from manholes to receiving waters. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37567 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 | 2013-06-01 18:00 | 2013-06-02 12:01 | 40000 | gallons | Manhole C29-22 Golf CourseManhole C30-20 near Sycamore Lift Station | Follow up report to incident report number 37533 to reflect overflow stop times. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37527 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 00:05 | 2013-06-01 04:00 | 2013-06-01 15:11 | 2000 | gallons | Manhole D30-55 Field off Covington Road | Precipitation event exceeded capacity of system resulting in SSO from manhole.
15295 | 37532 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 00:15 |  | 2013-06-01 15:15 | 0 |  | Manhole D31-120 10414 West Lakes Drive | Precipitation event exceeded the capacity of the sanitary sewer system resulting in an untreated release from manhole.
15295 | 37526 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 00:15 | 2013-06-01 04:00 | 2013-06-01 15:11 | 10000 | gallons | Aboite Meadows Lift StationManhole D31-2 on Turf Lane | Precipitation event coupled with power loss resulted in SSO from manhole and lift station. | Brought portable generator to lift station and returned it to pumping status.
15295 | 37570 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 00:15 | 2013-06-01 17:00 | 2013-06-02 12:02 | 20000 | gallons | Manhole D31-120 10414 West Lake Drive | Follow up report to indident report number 37532 to reflect overflow stop times and overflow estimates.
15295 | 37522 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 02:00 | 2013-06-01 06:25 | 2013-06-01 15:10 | 1000 | gallons | Manhole C35-12 11230 Dellock Way | Precipitation event triggered SSO
15295 | 39258 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 02:00 | 2013-06-01 06:25 | 2013-06-01 15:20 | 0 |  | C 35-12 11230 Dellock Way | Rain 5 inches very heavy rain starting at 1:00pm 5/31/13
15295 | 37521 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 04:00 | 2013-06-01 06:00 | 2013-06-01 15:08 | 5000 | gallons | Manhole E34-22 Liberty Mills Road | Precipitation event triggered SSO. |  | SSO Occurred at Treatment Plant
15295 | 39276 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 09:15 | 2013-06-02 21:00 | 2013-06-03 08:20 | 0 |  | C31 - 7 Eggman Rd. | Rain 5 inches very heavy rain over night starting at 10:00pm
15295 | 39263 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 12:00 | 2013-06-01 22:00 | 2013-06-02 12:25 | 0 |  | C2944 C29-40 Golf Course | Rain 5 inches very heavy rain over night starting 10:00pm 5/31/2013 |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37525 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 12:15 | 2013-06-01 04:00 | 2013-06-01 15:10 | 5000 | gallons | Manhole D31-5 Tnaf Lane | Precipitation event coupled with power loss resulted in loss of power to a lift station and SSO. | Brought portable generator to lift station to provide power for the station.
15295 | 39259 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 14:04 | 2013-06-01 04:00 | 2013-06-01 15:20 | 0 |  | D 31-5 Turf Lane | Rain 5 inches was do the L/S Aboite meadows losing power until I got generator there and running. Very heavy rain starting at 10::pm 5/31/13
15295 | 39260 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 14:13 | 2013-06-01 04:00 | 2013-06-01 03:20 | 0 |  | Aboite meadows L/S D31-2 on Turf Ln | Rain 5 inches. Lost power to station got gen there back up and running. Very heavy rain starting 10:pm 5/31/13
15295 | 39264 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 14:40 | 2013-06-01 17:00 | 2013-06-02 12:25 | 0 |  | 031-120/ 1044 Westake DR | Rain 5 inches very heavy rain over night starting 10:00pm 5/31/13
15295 | 39265 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 14:46 | 2013-06-01 17:45 | 2013-06-02 12:25 | 0 |  | C 29-50 C29 - 21 Golf Course | Rain 5 inches very heavy rain over night starting 10:00pm 5.31-13 |  | SSO Reached Receiving Water
15295 | 39267 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 14:52 | 2013-06-01 18:00 | 2013-06-02 12:25 | 0 |  | C29 - 22 Golf Course C30 - 20 by Sycamore L/S | Rain 5 inches very heavy rain over night starting at 10:00on 5/31/13 |  | SSO Reached Receiving Water
15295 | 37943 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 | 2013-06-13 16:00 | 2013-06-14 09:32 | 6000 | gallons | C29 - 22 Golf Course | Rain 1.8 inches heavy rain over night |  | SSO Affected Private Property
15295 | 37810 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 |  | 2013-06-13 09:40 | 0 |  | C29 - 22 Golf Course | Rain 1.8 inches heavy rain overnight |  | SSO Affected Private Property
15295 | 37812 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 |  | 2013-06-13 08:33 | 0 |  | C29 - 21 Golf Course | Rain 1.8 inches heavy rain over night. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37809 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 |  | 2013-06-13 08:33 | 0 |  | C29 - 40 Golf Course | Rain 1.8 inches heavy rain overnight |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37807 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 |  | 2013-06-13 08:33 | 0 |  | C30 - 20 Bridge Sycamore L/S | Rain 1.8 inches heavy rain over night. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 37939 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 | 2013-06-13 15:30 | 2013-06-14 09:32 | 2000 | gallons | C30 - 20 Beside Sycamore L/S | Rain 1.8 inches Heavy rain over night. |  | SSO Affected Private Property
15295 | 39275 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 | 2013-06-13 16:00 | 2013-06-14 09:40 | 0 |  | C29 - 21 Gold Course | Rain 1.8 inches heavy rain over night. |  | SSO Reached Receiving Water
15295 | 39274 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 | 2013-06-13 16:00 | 2013-06-14 09:40 | 0 |  | C29 - 22 Golf Course | Rain 1.8 inches heavy rain over night
15295 | 39272 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 02:00 | 2013-06-13 15:30 | 2013-06-14 09:40 | 0 |  | C30 - 20 Beside sycamore L/S | Rain 1.8 inches heavy rain over night.
15295 | 39155 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 |  | 2013-06-30 14:40 | 0 |  | C29 - 22 | Rain 3.2 inches. Very heavy rain short time frame. |  | SSO Reached Receiving Water
15295 | 39611 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 | 2013-06-30 23:30 | 2013-07-01 09:52 | 0 |  | C29 21 On Golf Course | Rain 4 inches 3.2 heavy rain 6-29-13 short time frame .8 during the night and early morning 6-30-13 |  | SSO Reached Receiving Water
15295 | 39156 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 |  | 2013-06-30 14:31 | 0 |  | C29 - 21 | Rain ..2 inches. Very heavy rain short time frame |  | SSO Reached Receiving Water
15295 | 39604 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 | 2013-06-30 23:00 | 2013-07-01 09:52 | 0 |  | C29-22 on Golf Course | Rain 4 inches 3.2 heavy rain 6/29/13 short time frame .8 raining the night early morning 6/30/13
15295 | 38258 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 | 2013-06-30 23:30 | 2013-07-01 09:50 | 0 |  | C29 - 22 on Golf Course | Rain 4 inches Manhole 3.2 heavy rain 6/29/13 short time frame. | None | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39277 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 | 2013-06-29 21:30 | 2013-06-30 14:23 | 0 |  | MH D31-120 by pond | Rain 3.2 inches heavy rain in short time frame
15295 | 39153 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 | 2013-06-29 09:30 | 2013-06-30 14:40 | 0 |  | M/H 031-120 by pond | Rain 3.2 inched Heavy rain in short time frame | See Report | SSO Affected Private Property
15295 | 39613 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:35 | 2013-07-01 02:00 | 2013-07-01 09:52 | 0 |  | C29 - 40 on Golf Course | Rain 4 inches 3.2 heavy rains 6/29/13 short time frame .8 during the night early morning 6/30/13 |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39157 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:35 |  | 2013-06-30 14:40 | 0 |  | C29 - 40 Golf Course | Rain 3.2 inches. Very heavy rain short time frame |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 38260 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:35 | 2013-07-01 02:00 | 2013-07-01 09:50 | 0 |  | C29 - 40 on Golf Course | Rain 4 inches Manhole 3.2 Heave rains 6/29/13 short time frame .8 during the night early morning 6/30/13 | 3.2 Heavy rains 6/29/13 short time frame .8 during the night early morning 6/30/13 | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39612 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:35 | 2013-06-30 22:00 | 2013-07-11 09:52 | 0 |  | C29 - 20 By L/S in Sycamore Road | Rain 4 inches 3.2 heavy rain 6/24/13 short time frame .8 during the night early morning 6/30/13
15295 | 38259 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:35 | 2013-06-30 22:00 | 2013-07-01 09:50 | 0 |  | C29 - 20 by L/S in Sycamore Rd | Rain 4 inches Manhole 3.2 Heavy rain 6/29/13 short time frame .8 during the night early morning 6/30/13 | None
15295 | 39722 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 09:30 | 2013-08-03 02:00 | 2013-08-03 11:45 | 0 |  | M/H C35-12 Dell Leak Way | Rain 4.75 inches Light rain 8/2/13 during the day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hour period 4.75 inches. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 40405 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 21:30 | 2013-08-03 02:00 | 2013-09-26 11:30 | 0 |  | M/H C35-12 Dell Lock Way | Light rain 8-2-13 during day had .25 inches by 4:00pm. Very Heavy rain starting about 7:00pm 8/2/2013 4.5 inches. Total 24hr period was 4.75 inches |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39723 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 21:45 | 2013-08-03 01:15 | 2013-08-03 11:45 | 0 |  | D31/120 | Light rain 8/2/13 during the day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hour period 4.75 inches. |  | SSO Reached Receiving Water
15295 | 39727 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 21:45 | 2013-08-03 01:15 | 2013-08-03 11:45 | 0 |  | D30-55 Field | Rain 4.75 inches. Light rain 8/2/13 during day .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hour period was 4.75 inches
15295 | 39669 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 23:45 | 2013-08-05 07:47 | 0 |  | C29 - 21 Golf Course | Rain 4.75 inches. Light rain 8/2/13 during the day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hr period was 4.75 inches. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39700 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 |  | 2013-08-03 11:45 | 0 |  | C29-40 Golf Course | Rain 4.75 inches Light rain 8/2/13 during the day has .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hour period was 4.75 inches. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39697 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 |  | 2013-08-03 11:45 | 0 |  | C29-21 Golf Course | Rain 4.75 inches Light rain 8/2/13 during the day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hour period was 4.75 inches. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39731 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 05:00 | 2013-08-03 11:50 | 0 |  | C 29/44 | Rain 4.75 inches. Light rain on 8/2/13 during the day had .25 inches by 4:00pm. Very Heavy rain started at 7:00pm on 8/2/13 until morning 8/3/13. Total in 24 hours 4.75 inches.
15295 | 39701 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 |  | 2013-08-03 11:45 | 0 |  | C29 - 22 Golf Course | Rain 4.75 Light rain 8/2/13 during the day had .25 inches by 4:00pm Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/2013 4/5 inch. Total 24 hour period was 4.75 |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39679 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 23:45 | 2013-08-05 07:47 | 0 |  | C29 - 22 Golf Course | Rain 4.75 inches Light rain 8/2/13 during day had .25 inches by 4:00pm. very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches total 24 hour period was 4.75 |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39730 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 11:18 | 2013-08-03 11:45 | 0 |  | At Sycamore L/S | Rain 4.75 Light rain 8/2/13 during the day .24 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total 24 hour period was 4.75
15295 | 39736 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:30 | 2013-08-02 23:30 | 2013-08-03 14:29 | 0 |  | Aertator Main Aboite WWTP | Rain 5 inches Receiving stream backed up high enough to impede discharge from WWT facility. | See Report | SSO Occurred at Treatment Plant
15295 | 39729 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-08-03 22:00 | 2013-08-03 11:18 | 2013-08-03 11:45 | 0 |  | C30-20 | Rain 4.75 inches Light rain 8/2/13 .25 inches by 4:00pm. Very heavy rain at 7:00pm 8/2/13 until morning 8/3/13 4.5 inches. Total in 24 hours was 4.75 inches.
15295 | 40601 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-10-01 10:00 | 2013-10-01 14:00 | 2013-10-02 12:15 | 0 |  | Forcemain on Eggeman Rd | Construction Related | Repaired Pipe See Report
15295 | 41430 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-10-29 13:30 | 2013-10-29 15:30 | 2013-10-30 13:15 | 0 |  | Manhole on West Hamilton Rd MH-B28-47 | Grease in sewer main caused backup and manhole release. Aqua crews were able to jet the sewer main and release the plug in the line. | Removed Blockage See Report | SSO Reached Public Land
15295 | 42828 | IN0035378 | Aboite Waste Water Treatment Plant | Allen | 2013-12-21 11:30 | 2013-12-23 04:30 | 2013-12-21 15:00 | 0 |  | Sycamore Hills Lift Station MHC29-40 MHC29-2 MH at station | Rain 2/0 inch Constant Rainfal and Snow Melt | See report | SSO Reached Receiving Water | Taylor Ditch
15295 | 40849 | IN0035378 | Aboite Wastewater Treatment Plant | Allen | 2013-10-03 08:30 | 2013-10-03 09:00 | 2013-10-03 13:30 | 0 |  | 8 Fprcemain on Eggeman Road | Construction Related During installation of a new 18 sewer force main on Eggman Rd contractor struck existing 8 forcemain. This caused that release of the contents in the 8 sewer forcemain. | Repair Pipe See Report
15295 | 37945 | IN0035378 Beal Taylor Ditch | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 | 2013-06-13 16:00 | 2013-06-14 09:32 | 6000 | gallons | C29 - 21 Golf Course Beal Taylor Creek | Rain 1.8 inches heavy rain over night. |  | SSO Reached Receiving Water
15295 | 37942 | IN0035378 Receiving Water- Beal Taylor Creek | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 | 2013-06-13 15:30 | 2013-06-14 09:32 | 46000 | gallons | C29 - 40 Golf Course Beal Taylor Creek | Rain 1.8 inches heavy rain over night. |  | SSO Reached Receiving Water
15295 | 39247 | IN0035378 (Main Aboite Plant) | Aboite Wastewater Treatment Plant | Allen | 2013-06-01 04:00 | 2013-06-01 06:00 | 2013-06-01 15:20 | 0 |  | E 34-22 Liberty Mills Rd | Rain 5 inches very heavy rain starting at 10:00pm 5/31/13
15295 | 40414 | IN0035378 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 21:45 | 2013-08-03 01:15 | 2013-09-26 11:30 | 0 |  | 030-55 Field | Rain 4.75 inches Manhole Light rain 8/2/13 during day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8/2/13 till early morning 8/3/13 4.5 inches. Total in 24 hr period was 4.75 inches.
15295 | 40431 | IN0035378 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 11:18 | 2013-09-26 11:30 | 0 |  | 9T sycamore L/S | Rain 4.75 inches Manhole Light rain 8-2-13 during day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8-2-13 till early morning 8-3-13 4.5 inches. Total in 24hr period was 4.75 inches.
15295 | 40439 | IN0035378 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 23:45 | 2013-09-26 11:30 | 0 |  | C29 - 22 Golf Course | Rain 4.75 inches Light rain 8-2-13 during day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8-2-13 till early morning 8-3-13 4.5 inches. Total in 24 hr period was 4.75 inches |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 40437 | IN0035378 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 23:45 | 2013-08-03 07:55 | 0 |  | C29 - 21 Golf Course | Rain 4.75 inches Light rain 8-2-13 during the day had .25 inches by 4:00pm. Very heavy rain starting about 7:00pm 8-2-13 till early morning 8-3-13 4.5 inches. Total in 24hr period was 4.75 inches |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 40417 | IN0035378 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 11:18 | 2013-09-26 11:30 | 0 |  | C30-20 Cov Rd by Sta | Rain 4.75 inches Light rain 8-2-13 during day had .25 inches by 4:00pm. Very heavy rain starting about 7pm 8/2/13 till early morning 8.3/13 4.5 inch. Total in 24hr period was 4.75 inches.
15295 | 40432 | IN0035378 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-03 05:00 | 2013-09-26 11:30 | 0 |  | C 29/44 Brermen Dr | Rain 4.75 Light rain 8-2--13 during day had .25 inches by 4:00pm. Very heavy rain starting about 7pm 8-2-13 till early morning 8-3-13 4.5 inches. Total in 24hr period was 4.75 inches.
15295 | 40435 | IN0035378 Main Aboite Plant | Aboite Wastewater Treatment Plant | Allen | 2013-08-02 22:00 | 2013-08-04 13:52 | 2013-09-26 11:30 | 0 |  | C29 -40 Golf Course | Rain 4.75 inch Light rain 8-2-13 during day had .25 inches by 4:00pm. Very heavy rain starting about 7pm 8-2-13 till early morning 8-3-13 4.5 inches. Total in 24hr period was 4.75 inches. |  | SSO Reached Receiving Water | Beal Taylor Ditch
15295 | 39273 | IN0035378 Waterbody: Affected BEAL TAYLOR CREEK | Aboite Wastewater Treatment Plant | Allen | 2013-06-13 01:40 | 2013-06-13 15:30 | 2013-06-14 09:40 | 0 |  | C29 - 40 Golf Course | Rain 1.8 inches heavy rain over night. |  | SSO Reached Receiving Water
1568 | 37205 | IN0042391 | UTILITY CENTER INCORPORATED MIDWEST WASTE WATER TREATMENT PLANT | Allen | 2013-04-18 23:45 | 2013-04-09 05:40 | 2013-04-19 09:24 | 0 |  | E-31-18 Brainwork L/S and Ground | Untreated Release Precipitation 4.2 inches. heavy rain overnight and rain during the week |  | SSO Affected Private Property
1568 | 36195 | IN0042391 | UTILITY CENTER INCORPORATED MIDWEST WASTE WATER TREATMENT PLANT | Allen | 2013-04-18 23:45 | 2013-04-19 05:40 | 2013-04-19 08:02 | 0 |  | E 31-18 Briarwood Lift Station | Precipitation event caused an untreated release from lift station to surrounding ground. |  | SSO Reached Public Land
4040 | 36472 | IN0045292 | HESSEN UTILITIES INCORPORATED | Allen | 2013-04-18 18:30 | 2013-04-19 08:45 | 2013-04-19 14:24 | 10000 | gallons | Lift Station #1 on Benzenger Road | Precipitation event and I & I contribution resulted in local flooding untreated non permitted release from submerged lift station to surrounding ground and unnamed ditch. | Lift station under water during bypass event. Monitored station during wet weather. Continuing to search for I & I issues. | SSO Reached Public Land
8956 | 35109 | IN0061727 | CHESTNUT HILLS WATER TREATMENT PLANT | Allen | 2013-01-29 09:30 | 2013-01-29 11:30 | 2013-01-29 13:52 | 500 | gallons | Lift Station at 12208 Illinois Road Fort Wayne IN | An undersized fuse blew in the Lift Station causing an Iron Sludge spill in the station. | Spill was contained in the station. No release to outside waters. Iron Sludge spill was cleaned up. Back washing of filters was discontinued to prevent operation of gravity plate settler discharge until an electrician could arrive. Replaced blown fuse with the correct size. | SSO Occurred at Treatment Plant
15295 | 38257 | IN035378 | Aboite Wastewater Treatment Plant | Allen | 2013-06-29 17:30 | 2013-06-30 23:00 | 2013-07-01 09:50 | 0 |  | C29 - 22 on Golf Course | Rain 4 inches Manhole 3.2 Heavy rain 6/29/13 short time frame.
15295 | 42613 | N0035378 | Aboite Waste Water Treatment Plant | Allen | 2013-12-21 11:30 |  | 2013-12-21 15:00 | 0 |  | Sycamore Hills Lift Station MHC29-30 MHC29-21 MH at Station | Constant rainfall and snow melt. | See Report
108750 | 43815 | No NPDES Permit | Leo-Cedarville Regional Sewer District | Allen | 2013-02-12 15:00 | 2013-02-12 22:00 | 2014-02-13 02:13 | 0 |  | Force main along SR #1 275 South of Willow Creek Dr | Pipe Failure failure of 35 year old restrains rods allowed fittings to partially separated detrition pe line pressure pressure loads subzero temps all contributed. | See Report | SSO Affected Private Property
6851 | 34482 | No NPDES Permit | GRABILL TOWN | Allen | 2013-03-11 19:00 | 2013-03-12 04:00 | 2013-03-12 11:00 | 5000000 | gallons | Page Rd Lift Station and Manhole | Untreated Release rain 2.0 inches 10 inch snow melt |  | SSO Affected Private Property
6851 | 37813 | No Permit | GRABILL TOWN | Allen | 2013-06-13 | 2013-06-13 08:00 | 2013-06-13 09:01 | 0 |  | Manhole 2-4 and page Rd Lift Station Ditch and Ground | Rain 2.75 inches Manhole 2-4 discharge at Page Rd Lift Station. |  | SSO Affected Private Property
| 36471 | Not permitted | Town of Grabill | Allen | 2013-04-19 03:30 | 2013-04-19 14:00 | 2013-04-19 14:24 | 1000 | gallons | Manhole on Walker Mill Court | Precipitation event and I & I contribution resulted in an unpermitted untreated release from a manhole to receiving water. | Stations pumping full capacity dead heading into Fort Wayne. Grabill still looking into I & I issues. | SSO Reached Receiving Water | Marsh Ditch
| 38700 | Terminated Permit - Town of Huntertown - IN0023116 |  | Allen | 2013-06-12 22:30 | 2013-06-13 01:30 | 2013-06-13 13:30 | 5000 | gallons | 16339 Lima road - Manhole West roadside ditch to storm sewer to Willow Ditch | Rain 3 inches This infiltration exceeded the capacity of the sewer system and resulted in overflow through the casting in the sewer manhole in front of H & H Sales on Lima Road. | The Utility Board has awarded a contract to line pipe and to perform manhole rehabilitation on this collection system. The town will continue to investigate the sewer network for observed locations of infiltration and correct any future occurrences will be reported in 24 hours. | SSO Reached Receiving Water | Willow Creek Ditch
513 | 35245 | IN0021253 | HOPE WASTE WATER TREATMENT PLANT | Bartholomew | 2013-01-13 16:13 | 2013-01-13 20:30 | 2013-01-14 10:39 | 5700 | gallons | Manhole 35 519 Race Street Hope In | Precipitation event(s) and snow melt resulted in Untreated Release from manhole to receiving waters | Will clean up any solids when sun thaws the grass. Checking for sump pump connections. | SSO Reached Receiving Water; Storm Sewer | Haw Creek
513 | 42891 | IN0021253 Outfall 001 | HOPE WASTE WATER TREATMENT PLANT | Bartholomew | 2013-12-21 09:30 | 2013-12-22 08:00 | 2013-12-22 09:23 | 81000 | gallons | Manhole 35 519 Race St | Rain 4.25 inches. After heavy snow melt on the 19th & 201th the ground was saturated. 4.25 inches of rain in 30 Hrs overwhelmed the collection system. | See Report | SSO Reached Receiving Water | Haw Creek
14836 | 39428 | IN00323573 | Columbus Waste Water Treatment Plant | Bartholomew | 2013-07-17 10:46 | 2013-07-18 15:30 | 2013-07-19 12:47 | 0 |  | Force Main | Equipment Failure force main from WWTP headwork s station to the WWTP was leaking sewage at an air release valve. The leak was located in a farm field approximately 1/2 mile from the nearest home. Leak only occurred when pumps were operating. | See Report | SSO Affected Private Property
14836 | 39587 | IN0032573 | Columbus Waste Water Treatment Plant | Bartholomew | 2013-07-17 08:52 | 2013-07-18 15:30 | 2013-07-19 12:49 | 0 |  | Force Main Manhole | Equipment Failure force main from WWTP headworks s station to the WWTP was leaking sewage at an air release valve. The leak was located in a farm field approximately 1.2 mile from the nearest home. Leak only occurred when pumps were operating. | See Report | SSO Affected Private Property
14836 | 42335 | IN0032576 Outfall 011 | Columbus Waste Water Treatment Plant | Bartholomew | 2013-12-05 05:00 | 2013-12-05 05:30 | 2013-12-06 10:33 | 0 |  | Inside fenced area of WWTP | Equipment Failure Automatic valve on cannibal system stuck open and sludge came out of manhole onto ground. Sludge was cleaned up using Vac Truck and then covered the ground with six inches of straw. Affected area was contained to the fenced in area of the WWTP | See Report | SSO Occurred at Treatment Plant
521 | 42892 | IN0039349 Manhole #99 | ELIZABETHTOWN WASTE WATER TREATMENT PLANT | Bartholomew | 2013-12-22 | 2013-12-23 | 2013-12-23 09:22 | 50000 | gallons | Manhole and Lift Station | Rain >4.0 inches the EQ Tank was full and that left nowhere to pump to. | See Report | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Little Sand Creek
2059 | 34455 |  | BLACKFORD COUNTY HIGH SCHOOL | Blackford | 2013-03-12 | 2013-03-12 13:55 | 2013-03-12 15:19 | 100 | gallons | Cleat House drain Ground | Untreated Power Failure Voltage control to the panel at the lift station had apparently been damaged during a power outage at the facility yesterday. This seemingly created a situation whereby the pumps were blowing fuses. This power failure also affected the alarm at the station. Custodial personnel noticed the back flow a the cleat house and immediately took action. Maintenance specialists responded and got the lift station back on line. | Building shut down until it could be cleaned and sanitized. Voltage control coil to the west pump to be replaced. | SSO Affected Private Property
1565 | 35133 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-01-23 12:30 | 2013-01-23 14:00 | 2013-01-23 15:36 | 21000 | gallons | Old plant lift station and bypass sites 006 and 007. Hartford City WWT Hartford City IN | Broken line exiting Lift station caused a large sink hole and untreated release into Little Lick Creek | Force pumped lift station dow to the point where pipe could be removed and replaced. replaced approximately 12 feet of ductile pipe with plastic. Fixed problem for now but would like to replace pipe and reroute to different manhole. | SSO Reached Receiving Water | Little Lick Creek
1565 | 34839 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-03-13 15:00 | 2013-03-13 08:30 | 2013-03-14 14:04 | 250000 | gallons | CSO 006 CSO 007 Lick Creek | Untreated Release Equipment Failure Grease buildup on surface of lift station prevented floats from resetting. All floats stuck in off position. | Clean Lift station of grease buildup continued maintenance of grease buildup | SSO Reached Receiving Water | Little Lick Creek
1565 | 34729 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-03-16 10:30 | 2013-10-16 14:00 | 2013-03-28 11:13 | 58000 | gallons | CSO-006 Old Plant and Railroad | Untreated Release Construction Related Maintenance had to clean out grit form box before muffin monster and lift station. | Vac out grit. Hard to stop bypassing completely when maintenance on lift station or forced main. | SSO Reached Receiving Water | Little Lick Creek
1565 | 35466 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-03-16 10:30 | 2013-03-16 14:00 | 2013-03-16 16:01 | 58000 | gallons | CSO #006 Old plant at Railroad Little Lick Creek. | Untreated Release Construction Related Maintenance had to clean out grit from box before muffin monster and Lift Station. | Vac out grit. Hard to stop bypassing completely when maintenance on Lift Station or forced main. | SSO Reached Receiving Water | Little Lick Creek
1565 | 34951 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-03-18 10:00 | 2013-03-18 13:30 | 2013-03-18 14:28 | 69200 | gallons | CSO-006 Old Plant & Railroad CSO-007 Old Plant Lift Station | Untreated Release Construction Related Had to shut down Lift Station in order to repair down stream manhole seal. | Would have preferred to do it when flow was lower needed fixed ASAP. Was able to pull & put new seal and concrete around manhole. This should stop the leak. | SSO Reached Receiving Water | Little Lick Creek
1565 | 34872 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-03-19 14:00 | 2013-03-20 08:00 | 2013-03-20 10:00 | 63290 | gallons | 009 A & W West ST RD 3 South Bridge Little Lick | Untreated Release Equipment Failure This is on our forced main 3/19 we checked 3 manholes down stream all were flowing full. Opened influent at 3PM pm 3/19. Checked again at 7:00AM 3/20 L/S going but reduced. 3/20 at 7:05AM opened influent gate more and by 8PM CSO had stopped. | When flow is not at peak we opened influent gate. this was successful in stopping CSO. This summer when flows are reduced and ground is solid we plan to have forced main cleaned from lift station to the plant. Approximately 1.5 miles also whenever we are having overflows even during rain we are trying to make sure we are taking in as much flow as we possibly can. | SSO Reached Receiving Water | Little Lick Creek
1565 | 35399 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-04-11 09:15 | 4/11/1311 00:00:00 | 2013-04-12 13:29 | 500 | gallons | Basement of residence at 901 North Mill Street Hartford City IN | Rubber gloves obstructing line from group home and precipitation event triggered an Untreated Release into the basement of a residence. | Rodded out obstruction in sewer. Spoke with group home about not disposing of rubber gloves in the sewer. Discovered no check valve in basement. Recommended installation to home owner. Going to jet out the sewer and run video camera through line. | SSO Basement Backup
1565 | 36269 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-04-19 04:30 | 2013-04-19 09:00 | 2013-04-19 10:05 | 250 | gallons | 414 North Monroe Street | Precipitation and 6 sewer obstruction resulted in untreated release into residential basement. | Opened blockage with sewer rodder allowing basement to drain. Going to jet and camera the line. | SSO Basement Backup
1565 | 39960 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-09-03 13:30 |  | 2013-09-04 12:40 | 0 |  | monroe South - Bypass 013 | Barely bypassing. RA Rodder hit something hard couldn t get through. | See Report | SSO Reached Receiving Water
1565 | 40343 | IN0021628 | HARTFORD CITY WASTE WATER TREATMENT PLANT | Blackford | 2013-09-23 08:30 | 2013-09-23 21:00 | 2013-09-24 09:22 | 0 |  | 3Mls at Cross Ave and St Rd 26 E | Check valve failure in dry well of 3M lift station. Water from valve leaking into dry well. Contractors called in plugged wet well side and replaced check valve and 1/4th turn isolation valve. | Repaired Pump Station See Report | SSO Reached Receiving Water | Mud Run
1572 | 37269 | IN0020796 | WHITESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Boone | 2013-05-27 18:00 | 2013-05-27 | 2013-05-28 05:50 | 10000 | gallons | 9451 Lafayette Road Indianapolis Manhole Force main ARV | Equipment Failure Manhole At 6:00PM and the Air Release Valve on the Royal Run Lift Station Force main failed during emergency repair by a contractor to release air from the force main. | The lift station was shut down valves on the force main were shut down to isolate the section of force main that the ARV was located on and a vac truck was called on site. The ARV was repair and put back into service. All affected areas were vaced up. All the Air Relief Valves will be replaced this year on the force main to prevent future failures. | SSO Affected Private Property
1566 | 35551 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-01-10 | 2013-01-11 | 2013-01-14 09:00 | 310000 | gallons | Lebanon Utilities Wastewater | Precipitation event along with snow melt and I & I resulted in Treatment Bypass. Bypass was recombined with final effluent. | $200000 per year is being spent to reline sewers to minimize/eliminate I & I. | SSO Occurred at Treatment Plant
1566 | 35553 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-01-11 | 2013-01-12 | 2013-01-14 09:00 | 590000 | gallons | Lebanon Utilities Wastewater | Precipitation along with snow melt and I & I resulted in a treatment plant bypass to final effluent. | We are spending $200000 per year to reline sewers to minimize I & I in collection system. | SSO Occurred at Treatment Plant
1566 | 35555 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-01-12 | 2013-01-13 | 2013-01-14 09:01 | 3340000 | gallons | Lebanon Utilities Wastewater | Precipitation event along with snow melt and I & I resulted in a Treatment Plant Bypass. | We are spending $200000 per year to reline sewers to minimize I & I in collection system. | SSO Occurred at Treatment Plant
1566 | 36053 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-04-12 | 2013-04-13 | 2013-04-18 09:05 | 330000 | gallons | Lebanon Utilities Wastewater Plant | Precipitation event and sewer line infiltration resulted in a treatment bypass at the WWTP to the final plant effluent. | We are spending $200000 per year relining sewer lines. | SSO Occurred at Treatment Plant
1566 | 36056 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-04-12 | 2013-04-12 | 2013-04-18 09:05 | 1930000 | gallons | Lebanon Utilities Wastewater Treatment Plant | Precipitation event and sewer line infiltration resulted in treatment plant bypass to final effluent. | We are spending $200000 per year relining sewer lines. | SSO Occurred at Treatment Plant
1566 | 36456 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-04-19 | 2013-04-20 | 2013-04-22 16:12 | 3150000 | gallons | Plant Final Plant Effluent | Plant final Plant Effluent | We are spending $200000.00 a year relining sewer lines. | SSO Occurred at Treatment Plant
1566 | 36457 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-04-19 | 2013-04-19 | 2013-04-22 16:16 | 2350000 | gallons | Plant Final Plant Effluent | Plant Final Plant Effluent Sewer Lines Infiltration | We are spending $200000.00 a year relining sewer lines | SSO Occurred at Treatment Plant
1566 | 36455 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-04-20 | 2013-04-21 | 2013-04-22 16:11 | 2910000 | gallons | Plant Final Plant Effluent | Sewer Lines infiltration | We are spending $200000.00 a year relining sewer lines. | SSO Occurred at Treatment Plant
1566 | 36446 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-04-21 | 2013-04-22 | 2013-04-22 16:09 | 800000 | gallons | Plant Final Plant Effluent | Bypass Plant Sewer Lines Infiltration | We are spending $200000.00 A year relining sewer lines. | SSO Affected Private Property
1566 | 36717 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-04-24 | 2013-04-27 | 2013-04-30 06:20 | 4440000 | gallons | Lebanon Utilities Wastewater Treatment Plant | Flow from precipitation event(s) and sewer line infiltration resulted in treatment bypass to final effluent. | We are spending $200000 per year relining sewer lines. | SSO Occurred at Treatment Plant
1566 | 42894 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-12-21 01:00 | 2013-12-21 23:59 | 2013-12-27 09:38 | 2226000 | gallons | Treatment Plant | Rain 1.82 inchesm heavy rain is the main cause of bypass and the melted snow. | See Report | SSO Occurred at Treatment Plant | Prairie Creek
1566 | 42893 | IN0020818 | LEBANON UTILITIES WASTE WATER TREATMENT PLANT | Boone | 2013-12-22 | 2013-12-22 10:00 | 2013-12-27 09:38 | 0 |  | Plant Bypass | Heavy rain is the main cause of bypass an the melted snow. | See Report | SSO Occurred at Treatment Plant | Prairie Creek
589 | 37031 | IN0024589 | THORNTOWN UTILITIES | Boone | 2013-04-19 08:00 | 2013-05-20 08:00 | 2013-05-20 13:02 | 0 |  | Treatment Pond Sugar Creek | Rain 7.7 inches We are no longer overflowing into Sugar Creek |  | SSO Affected Private Property | Sugar Creek
589 | 36381 | IN0024589 | THORNTOWN UTILITIES | Boone | 2013-04-19 08:00 |  | 2013-04-22 11:07 | 0 |  | Treatment pond to Sugar Creek | Precipitation event triggered a treatment plant bypass and untreated release to receiving waters. | Operator not available on the 19th to report overflow. | SSO Reached Receiving Water | Sugar Creek
926 | 35475 | IN0036951 | ZIONSVILLE TOWN HALL | Boone | 2013-04-06 12:00 | 2013-04-06 13:30 | 2013-04-08 08:52 | 50 | gallons | Clean out North of MH#06-48A Ground | Untreated release Sewer line blockage caused by roots. | Clean up ground Line will be added to cleaning schedule for twice/year. | SSO Affected Private Property
926 | 36219 | IN0036951 | ZIONSVILLE TOWN HALL | Boone | 2013-04-19 00:45 | 2013-04-19 05:00 | 2013-04-19 08:50 | 0 |  | Blending at WWTPManhole at WWTP for Boone Village Lift Station | Precipitation event caused untreated release from plant. All available treatment units put into operation. Sampling at end of contact tank because polishing ponds flooded by Eagle Creek and final structure not accessible. Numerous sewers backed up flooded and surcharged during rain event. Bypass was recombined and sampled before discharge. |  | SSO Reached Receiving Water | Eagle Creek; Starkey Branch
926 | 36540 | IN0036951 | ZIONSVILLE TOWN HALL | Boone | 2013-04-19 00:45 | 2013-04-19 23:59 | 2013-04-20 10:20 | 0 |  | Manhole 06-01 at Main Lift Station210 Raintree Drive - Raintree Lift Station | Precipitation event(s) caused area flooding and untreated release from Lift Station and manhole to surrounding ground and receiving water. | Manhole at Main Lift Station and Raintree Lift Station showed eveidence of overflowing after flood waters receded. | SSO Reached Public Land; SSO Reached Receiving Water | Eagle Creek
926 | 39812 | IN0036951 | ZIONSVILLE TOWN HALL | Boone | 2013-08-25 20:00 | 2013-08-26 07:00 | 2013-08-26 12:54 | 0 |  | 9335 Irishman Run Lane 9468 Sullivan Place | Force main blockage in low pressure force main system. Two houses above had failed check valves and home owner s pits overflowed. | Suspect failed check valve in Town s force main system. In the process of digging up inspecting and cleaning blockage. Temporary sewer service is being provided by pumper truck until Town s system is fixed. | SSO Affected Private Property
782 | 36469 | IN0039705 | Advance Municipal Waste Water Treatment Plant | Boone | 2013-04-18 15:30 | 2013-04-19 08:00 | 2013-04-19 14:27 | 0 |  | 414 East Wall Street | Precipitation event caused an untreated release from a common septic system to private ground. | All homes are connected to main sewer via septic tank. Decreases the amount of solids/floatables in bypass/overflow. Lid shoud be screwed down tightly. Verify lids are sealed and tight. Tanks are on homeowners property similar to a cleanout on homes. | SSO Affected Private Property
1612 | 35962 | IN0050989 | ZIONSVILLE WASTE WATER TREATMENT PLANT | Boone | 2013-01-13 02:00 | 2013-01-13 13:15 | 2013-01-14 08:44 | 0 |  | 255 Starkey Road. Northwest corner of property old lift station. | Precipitation event and blocked pumps resulted in and untreated release to surrounding ground and receiving water. | Pulled and cleaned pumps | SSO Reached Receiving Water | Starkey Branch
1612 | 35961 | IN0050989 | ZIONSVILLE WASTE WATER TREATMENT PLANT | Boone | 2013-01-13 04:00 | 2013-01-13 14:05 | 2013-01-14 08:44 | 0 |  | Town of Zionsville WWTP | Precipitation event coupled with snow melt exceeded the capacity of the WWTP and resulted in an internal release that was recombined with final effluent and sampled prior to discharge. | All available tanks put into service. | SSO Occurred at Treatment Plant
241 | 34623 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Boone | 2013-03-08 01:30 | 2013-03-08 02:30 | 2013-03-08 05:00 | 600 | gallons | Manhole #EV-1 Excavation area. | Untreated Release Construction Related No known damage to aquatic lift or receiving stream. Atlas Excavating Inc. removed manhole #EV-1 allowing sanitary sewage to run into the excavation area. The line connects about 15 homes to the sanitary system. | Actions taken to prevent minimize or mitigate damage were to not dewater the site. The dewater pump was removed from the well point and used to pump our the excavation area into the lift station 17 wet well. Contractor education on environment and financial impacts of a bypass/overflows. | SSO Affected Private Property
241 | 36461 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Boone | 2013-04-18 10:40 | 2013-04-19 10:15 | 2013-04-19 03:00 | 0 |  | Manhole #NI-1&SI-7 #CBM-2 CBM-3 & MC3 Ground/Ditch | Untreated Release Rain 4.40 inches 4.40 inches for rain recorded in ten hours; from 1730 on 4/17/2013 (3.38) to 0530 on 4/19/2013 (1:02). Due to excessive rain fall in a short amount of time combined with the saturated ground the lift stations and gravity mains could not keep up. | Monitored lift stations investigated areas for possible I&I and will start clean up as soon as water levels recede. Continue I&I inspections system maintenance and investigate possible bottle necks in the system.
241 | 36463 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Boone | 2013-04-19 09:30 | 2013-04-19 08:00 | 2013-04-19 03:43 | 0 |  | Manhole #SPR-35 Ground & 632 Mayfair Lane Carmel In 46032 Basement | Untreated Release Rain 4.40 inches 4.40 inches of rain recorded in ten hours from 1730 on 4/18/2013 (3:38) to 0530 on 4/19/2013 (1.02). Due to excessive rain fall in a short amount of time combined with the saturated ground the lift stations and gravity mains could not keep up. | Monitored lift station investigated areas for possible I&I and will start clean up as soon as water levels recede. Continue I&I inspections system maintenance and investigate possible bottle necks in they system. | SSO Basement Backup; SSO Affected Private Property
241 | 40256 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Boone | 2013-09-19 19:00 | 2013-09-20 15:05 | 2013-09-20 12:59 | 0 |  | Lift Station 10 Force Main | Construction Related CSU INC Utility contractor bored through the disinfect lift station 10 force main. | Repaired Pipe See Report | SSO Affected Private Property
1857 | 35234 | IN0023876 | NASHVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Brown | 2013-01-09 16:00 | 2013-01-10 23:30 | 2013-01-11 08:30 | 10800 | gallons | Manhole Nashville IN | Tree roots blocking sewer main resulted in Unknown release to storm sewer. | Septic hauler kept receiving manhole empty while using jetter to clear sewer main. Routine jetting of sewer mains. | SSO Reached Public Land; Storm Sewer
1857 | 34963 | IN0023876 | NASHVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Brown | 2013-02-06 04:00 | 2013-02-06 09:30 | 2013-02-06 14:34 | 400 | gallons | Manhole #2 Nashville IN | Lift station lost power and did not call out to notify resulting in a backup and untreated release at Manhole #2 | Reset station. checked alarm system and all is working. Check lift station on a daily basis | SSO Reached Public Land
1857 | 34961 | IN0023876 | NASHVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Brown | 2013-02-06 11:00 | 2013-02-06 11:50 | 2013-02-07 07:07 | 20 | gallons | Residential Lift Station | Pump quit running | Pumped Lift Station down into Storage Tanks. Changed pumps in station. | SSO Reached Public Land
1857 | 36778 | IN0023876 | NASHVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Brown | 2013-05-06 08:00 | 2013-05-06 08:15 | 2013-05-07 07:39 | 100 | gallons | Nashville WWTP | Apparent improper operation of Digester Valve resulted in a partially treated release to surrounding ground at WWTP. | Pumped sludge to drying bed reducing sludge level to stop leaking. Talked to people at plant about working the valve properly. | SSO Occurred at Treatment Plant
1857 | 40150 | IN0023876 | NASHVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Brown | 2013-09-15 12:01 | 2013-09-15 14:00 | 2013-09-16 10:46 | 0 |  | manhole #A5 | Equipment failure Parsley blocked sewer main. | Removed Blockage See Report | SSO Reached Public Land
3992 | 36543 | IN0030325 | BROWN COUNTY STATE PARK | Brown | 2013-04-19 14:00 | 2013-04-20 | 2013-04-20 10:19 | 0 |  | Brown County State Park WWTP | Precipitation event flow and WWTP equipment failure resulted a partially treated release from the WWTP to an unnamed stream. | shutdown of blowers and pumps to reduce sludge washout. Repair and monitor water plant operation. | SSO Occurred at Treatment Plant
3992 | 36425 | IN0030325 | BROWN COUNTY STATE PARK | Brown | 2013-04-21 11:00 |  | 2013-04-22 14:53 | 0 |  | WWIP Stream | Partially Treated Release Equipment Failure Water plant Malfunction. Water plant control process failed causing excessive flush and backwash water to be sent to waste plant. | Close monitoring and reducing flow rates. Contractor for water plant controls due 5-7-13 | SSO Reached Receiving Water
15339 | 36168 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-01 07:00 | 2013-04-19 07:00 | 2013-04-19 06:51 | 1800000 | gallons | EQ tank emergency release point Town of Flora WWTP | Precipitation event(s) caused overflow from the EQ tank to the finishing ponds resulting in a partially treated release blended with final effluent and sampled before discharge | Chlorine and Sodium Bisulfite added prior to discharge to receiving waters. In house sewer repairs and main lines as funds allow us to proceed. T-Bird Design putting bid package together for us to date. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Bachelor Run
15339 | 35410 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-11 07:00 | 2013-04-12 07:00 | 2013-04-12 07:39 | 0 |  | EQ tank emergency release point at the Town of Flora WWTP Flora IN | Precipitation event caused EQ tank to overflow into 2-2 day tertiary ponds. No bypass to receiving waters. Effluent partially treated combinded and sampled. | In house sewer repairs as funds allow. T-Bird Design is putting together a bid package. | SSO Occurred at Treatment Plant
15339 | 35787 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-12 07:00 | 2013-04-13 07:00 | 2013-04-15 06:29 | 1800000 | gallons | EQ Tank Emergenty Release point 2-2 day Tertiary Ponds | Partially Treated Release Blended with Final Effluent & Sampled After 3.63 inches of rain EQ Tank full and overflowing into 2-2 day tertiary ponds. Not bypassing onto Kuns Ditch. | In house collection system remain as funds allow. T-Bird Design putting a bid package together. | SSO Occurred at Treatment Plant
15339 | 35790 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-13 07:00 | 2013-04-14 07:00 | 2013-04-23 10:11 | 1800000 | gallons | EQ Tank Emergency Release Point 2-2 day Tertiary Ponds. | Partially Treated Release Blended with final Effluent & Sampled. EQ Tank overflowing into 2-2 day tertiary ponds after 3.63 inches of rain. Not Bypassing into Kuns Ditch. | In house collection system main as funds allow. T-Bird design putting a bid package together. | SSO Occurred at Treatment Plant
15339 | 35690 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-14 07:00 | 2013-04-15 19:00 | 2013-04-15 06:29 | 1368000 | gallons | EQ Tank Emergency Release Point 2-2 day Tertiary Ponds | Partially Treated Release Blended with Final Effluent & Sampled EQ Tank overflowing into 2-2 day tertiary ponds after 3.63 rain. NOT BYPASSING into Kuns Ditch. | In house sewer main as funds allow. T-Bird Design putting bid package together. | SSO Affected Private Property
15339 | 35822 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-15 07:00 | 2013-04-16 07:00 | 2013-04-16 06:28 | 792000 | gallons | EQ Tank Emergency Release point 2-2 day Tertiary Ponds. | Partially Treated Release Blended with Final Effluent & Sampled. EQ Tank still overflowing into 2-2 day tertiary ponds after previous 3.63 inches plus .34 inches another .34 inches. Receives Chlorine & Sodium Bisulfate prior to discharge into Bachelor Run. Not bypassing into Kuns Ditch. | In house sewer main as funds allow. T-Bird Design putting a bid package together. | SSO Affected Private Property | Bachelor Run
15339 | 36058 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-17 07:00 | 2013-04-18 07:00 | 2013-04-18 06:44 | 1584000 | gallons | Town of Flora WWTP EQ Tank Emergency Release Point | Precipitation event(s) caused partially treated release due to treatment process bypass from EQ tank emergency release point to 2-2 day Tertiary Ponds where the flow is recombined with final effluent and receives Chlorine and Sodium Bisulfite prior to discharge. Final effluent is sampled prior to discharge. | In house sewer repairs and main lines as funds allow us to proceed. T-Bird Design putting together a bid package for us. | SSO Occurred at Treatment Plant
15339 | 35928 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-18 07:00 | 2013-04-17 07:00 | 2013-04-17 08:14 | 186000 | gallons | EQ Tank Emergency Release Point 2-2 Day Tertiary Ponds | Partially Treated Release Blended with Final Effluent & Sampled EQ Tank still overflowing after another 1.12 rain receives chlorine and sodium bisulfate prior to discharge into Bachelor Run. Not Kuns Ditch 17 hours 1/2 pipe 7 hours full pipe. | In house sewer repairs and main lines as funds allow us to proceed. T-Bird Design putting a bid package together for us to date. | SSO Affected Private Property | Bachelor Creek
15339 | 36324 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-19 07:00 | 2013-04-20 07:00 | 2013-04-22 06:46 | 1800000 | gallons | Town of Flora WWTP | Pricipitation event caused overflow from the EQ tank emergency release point to 2-2 day Tertiary Ponds. Partially treated release | Overflow received Chlorine and Sodium Bisulfite and was recombined with final effluent and sampled prior to discharge.In house sewer maintenance as funds allow.T-Bird Design is putting together a bid package. | SSO Occurred at Treatment Plant
15339 | 36326 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-20 07:00 | 2013-04-21 07:00 | 2013-04-22 06:47 | 1368000 | gallons | Town of Flora WWTP | Precipitation event triggered a partially treated release from EQ tank to 2-2 day tertiary ponds. | Overflow received chlorine and Sodium Bisulfite. Blended with final effluent and sampled prior to discharge.In house sewer maintenance as funds allow.T-Bird Design putting together a bid package. | SSO Occurred at Treatment Plant
15339 | 36323 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-21 07:00 | 2013-04-22 07:00 | 2013-04-22 06:47 | 1368000 | gallons | EQ Tank Emergency Release Point Town of Flora WWTP | Precipitation event triggered a partially treated release from WWTP. EQ tank overflowing into 2-2 day tertiary ponds. No bypass to receiving waters. | Overflow received Chlorine and Sodium Bisulfite and was recombined with final effluent and sampled before discharge. In house sewer maintenance as funds allow.T-Bird Design is putting together a bid package. | SSO Occurred at Treatment Plant
15339 | 36112 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-22 07:00 | 2013-04-23 07:00 | 2013-04-23 06:26 | 792000 | gallons | EQ Tank emergency Release Point 2-2 day Tertiary Ponds | Partially Treated Release Blended with Final Effluent & Sampled. Flow starting to slow down after 3.82: of rain . EQ Tank overflowing into 2-2 day tertiary ponds. Not bypassing into Kuns Ditch. Receives CL2 and Sodium Disulfide before discharge into Bachelor Run. | In house sewer main as funds allow. T-Bird Design putting a bid package together. | SSO Occurred at Treatment Plant
15339 | 36114 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-23 07:00 | 2013-04-24 07:00 | 2013-04-24 06:26 | 990000 | gallons | EQ Tank Emergency Release Point 2-2 day Tertiary Ponds. | Partially Treated Release Blended with Final Effluent & Sampled Another 1.30 of rain after 3.80 (5.10 ). EQ tank overflowing into 2-2 day tertiary ponds. Not bypassing into Kuns Ditch. Receives CL2 & Sodium Disulfide before discharge to Bachelor Run. | In house sewer main as funds allow. T-Bird Design putting a bid package together. | SSO Occurred at Treatment Plant | Bachelor Creek
15339 | 36624 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-24 07:00 | 2013-04-25 07:00 | 2013-04-25 06:25 | 1800000 | gallons | Town of Flora WWTP | Precipitation event(s) caused a partially treated release from EQ tank emergency release point to the 2-2 tertiary ponds. | Bypassed effluent receives Chlorine and Sodium Bisulfite treatment before discharge into Bachelor RunIn house sewer maintenance as funds allow.T-Bird Design putting together a bid package. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Bachelor Run
15339 | 36656 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-25 07:00 | 2013-04-26 07:00 | 2013-04-26 06:27 | 1488000 | gallons | WWTP | Precipitation event(s) caused an internal overflow from the EQ Tank Emergency Release point to the 2-2 day tertiary ponds. | Partially treated release. Effluent received c/z and Sodium Bisulfite before discharge to receiving water. Bypass effluent is blended with final effluent and sampled before discharge.In house sewer maintenance as funds allow.T-Bird Design is putting together a bid package. | SSO Occurred at Treatment Plant
15339 | 36692 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-26 07:00 | 2013-04-27 07:00 | 2013-04-29 06:34 | 630000 | gallons | EQ Tank WWTP | Precipitation event(s) exceeded plant capacity and necessitated the partially treated release. EQ Tank released to 2-2day tertiary ponds. | Released effluent received cl2 and sodium bisulfite. Recombined with final effluent and sampled prior to discharge. | SSO Occurred at Treatment Plant
15339 | 36691 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-27 07:00 | 2013-04-28 07:00 | 2013-04-29 06:34 | 984000 | gallons | EQ Tank WWTP | Precipitation event(s) necessitated the partially treated release from the EQ Tank to the 2-2 day Tertiary Ponds. | Effluent was treated with Cl2 and Sodium Bisulfite recombined with final effluent and sampled prior to discharge.In house sewer maintenance as funds allow.Bids to be opened 5/6/13. T-Bird Design | SSO Occurred at Treatment Plant
15339 | 36690 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-28 07:00 | 2013-04-29 07:00 | 2013-04-29 06:33 | 792000 | gallons | EQ Tank at WWTP | Precipitation event(s) exceeded the capacity of the system necessitating the release of effluent from the EQ Tank Emergency Release Point to the 2-2 day tertiary ponds. | The EQ Tank release was recombined with final effluent and received Cl2 and Socium Bisulfite treatment. Final effluent was sampled before discharge.In house sewer maintenance as funds allow.Bids to be opened 5/6/13. T-Bird Design | SSO Occurred at Treatment Plant
15339 | 36723 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-29 07:00 | 2013-04-30 07:00 | 2013-04-30 06:27 | 792000 | gallons | EQ Tank Emergency Release point to 2-2 day Tertiary Ponds. | Precipitation event(s) resulted in partially treated release from EQ Tank to 2-2 day tertiary ponds an finally to receiving water. | Bypass receives Cl2 and Sodium Bisulfite before discharge to receiving water.In house sewer maintenance as funds allow.Bids to be opened 5/6/13. T-Bird Design | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Bachelor Run
15339 | 36746 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-04-30 07:00 | 2013-05-01 07:00 | 2013-05-01 06:37 | 630000 | gallons | Town of Flora WWTP | Precipitation event(s) exceeding capacity of WWTP resulting in partially treated release from the EQ tank to the 2-2 day Tertiary pond and then to receiving water. | Overflow is combined with final effluent and receives Cholroine and Sodium Bisulfite prior to discharge to receiving water.In house sewer maintenance as funds allow.Bids to be opened 5/6/13. T-Bird Design | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Bachelor Run
15339 | 36781 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-05-01 07:00 | 2013-05-02 07:00 | 2013-05-02 06:30 | 0 |  | EQ Tank to 2-2 day Tertiary Ponds Flora WWTP | Flow from preciptation event(s) exceeded capacity of WWTP requiring in plant bypass of treatment from EQ Tank Emergency Release to the 2-2 day Tertiary Ponds. | EQ tank overflowed into 2-2 day Tertiary Ponds. DID NOT bypass to Kerns Ditch. Effluent is recombined and receives Chlorine and Sodium Bisulfite treatment prior to discharge to Bachelor Run.In house sewer maintenance as funds allow.Bid opening 5/6/13. T-Bird Design | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Bachelor Run
15339 | 36750 | IN0020141 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-05-02 07:00 | 2013-05-02 19:00 | 2013-05-03 06:27 | 36000 | gallons | Town of Flora WWTP. EQ tank to Tertiary Ponds | Precipitation event(s) flow exceeding the capacity of the WWTP and collection system resulting in a partially treated release to 2-2 day Tertiary Ponds and finally to receiving water. | Plant and collection system catching up after 9.37 of rain for April. EQ tank overflowing into 2-2 day tertiary ponds. NOT bypassing to Kuns Ditch. Receives Chlorine and Sodium Bisulfite before discharge to Bachelor Run.We do in house sewer maintenance as funds allow.Bids to be opened 5/6/13. T-Bird Design. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Bachelor Run
15339 | 42921 | IN0020141 Outfall 001 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-12-21 02:00 | 2013-12-22 07:00 | 2013-12-26 11:43 | 174000 | gallons | EQ Tank Overflow | Rain 1.9 inches EQ Tank filled after .04 12/19 26 12/20 and 19 inches 12/21. Overflowed into 2 2 day tertiary ponds. Did not bypass to Kuna Ditch. | See Report | SSO Occurred at Treatment Plant | Bachelor Creek
15339 | 42918 | IN0020141 Outfall 001 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-12-23 07:00 | 2013-12-24 01:00 | 2013-12-26 11:43 | 426000 | gallons | EQ Tank Overflow | Rain Plant and collection system caught up after 2.22 inches of rain caused EQ tank to fill and overflow into 2nd 2 day Tertiary ponds. Not bypass into Kuns Ditch. | See Report | SSO Occurred at Treatment Plant | Bachelor Creek
15339 | 42916 | IN0020141 Outfall 001 | Flora Municipal Waste Water Treatment Plant | Carroll | 2013-12-22 07:00 | 2013-12-23 07:00 | 2013-12-26 11:43 | 1644000 | gallons | EQ Tank Overflow | Rain .02 inches EQ Tank filled after 2.22 of rain. Overflowed into 2 day tertiary ponds. No bypass to Kuns Ditch. | See Report | SSO Occurred at Treatment Plant | Bachelor Creek
1564 | 36766 | IN0021377 | DELPHI MUNICIPAL WASTE WATER TREATMENT PLANT | Carroll | 2013-04-11 | 2013-04-26 | 2013-05-03 14:35 | 10000 | gallons | Manholes at Illinois Street and Water Street | Precipitation event(s) saturated ground local flooding and I & I contribution resulted in untreated release from manholes to public and private land. | Pumps were set up to pump out storm water around the clock during flooding. All areas were limed debris cleaned up. Flood waters entered area over a levee along Deer Creek. Levee is an old Interurban road bed not a flood levee. | SSO Reached Public Land; SSO Affected Private Property
1564 | 36594 | IN0021377 | DELPHI MUNICIPAL WASTE WATER TREATMENT PLANT | Carroll | 2013-04-11 | 2013-04-26 | 2013-05-03 13:00 | 10000 | gallons | (2) Manholes Illinois Street & Water St | Rain 6-9 inches Due to heavy rains and already saturated ground flood waters and infiltration sewers were surcharged - discharge escaped from (2) manholes in same vicinity and collected in side ditches and yards. Storm water pumped and all areas limited. | Pumps were set up to pump out storm water around the clock during flooding. All areas were limed debris cleaned up. Flood waters entered area over a levee along Deer Creek. Levee is old interurban road bed. | SSO Affected Private Property | Deeds Creek
15051 | 40205 | IN0030562 | Camden Municipal Waste Water Treatment Plant | Carroll | 2013-09-16 10:30 | 2013-09-16 11:30 | 2013-09-17 08:51 | 0 |  | 197 S Monroe St | Equipment Failure Wastewater backed up in basement drain at 197 S Monroe St. App # 3 deep and then went back down floor drain to sewer main. Had sewer jetted found roots in main. | Removed Blockage See Report | SSO Basement Backup
11292 | 40204 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Carroll | 2013-09-13 13:30 | 2013-09-13 17:30 | 2013-09-17 08:51 | 0 |  | 5302 Stratford Road Storm Sewer | Equipment FailureCrew responded to service request for odor from 4905 Stratford Road. Upon investigation it was determined that main sewer was obstructed and releasing into storm sewer. Crew cleaned main sewer to remove obstruction release eliminated. | Remove Blockage See Report | SSO Reached Receiving Water | Dry Branch
55346 | 40249 | IN0054445 | WHITE OAKS ON THE LAKE | Carroll | 2013-09-18 08:00 | 2013-09-18 20:15 | 2013-09-20 11:26 | 0 |  | Upper Park Lift Station | Lift station did not pump on auto level raised allowing seepage. Slight shallow pooling for soft visually confirmed following morning. | See Report | SSO Reached Receiving Water
56318 | 34900 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | Carroll | 2013-02-10 13:03 | 2013-02-10 13:18 | 2013-02-11 07:16 | 50 | gallons | 12018 North Upper Lakeshore Drive Monticello IN | Bad curb stop creating Untreated Release | 13:03 Call to pager13:13 Arrived at site13:15 Checked G.U.13:18 Shut off curb stop to stop flow13:20 Pump out G.U. into barrel13:25 Called in locates13:31 Called contractor to fix problem13:34 spread lime on affected area13:40 called backup for 2nd barrel15:15 locators arrived16:05 Jim overbeck arrived17:00 changed grommet on pump17:35 tested repair for leaks17:40 back filled hole17:45 pump barrels into G.U. and test G.U.18:05 job completePut new check valve on curb stop | SSO Reached Public Land; Surface Soil
56318 | 34608 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | Carroll | 2013-03-01 15:00 | 2013-03-01 16:26 | 2013-03-01 19:48 | 150 | gallons | 9576 N State Rd 421 Grinder Ground | Untreated Release Equipment Failure Failure of backflow preventer and grommet/ seal @ grinder allowed sewage from low pressure sewer to backflow into Grinder vault and overflow onto grand. | 3:01pm called Bud Helms: 4:32pm - 5:40pm J Overbeck excavated & replaced curb stop & backflow preventer. 3:20pm B Helms @ site: 4:40pm - 6:30pm B Helms evacuates grinder vault 3:56pm R Fain @ site: evaluated grinders4:25pm curb stop/shutoff located: Grommets replaced one grinder4:26pm curb stop/shutoff closed: 6:15pm - 6:40pm: Lime applied to contaminated area. Replaced faulty equipment | SSO Affected Private Property
1636 | 35463 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-10 18:15 | 2013-04-10 18:45 | 2013-04-10 18:50 | 36000 | gallons | Michelle Ln Caldasak Michelle Ln Extended Phillips Ditch | Untreated Release Rain Had pump fail at lift station at high level while it was maintaining. Wasn t able to catch up with flow after it got reset. Flow has stop coming out of bypass. | Working on infiltration problems from Agreed Order. Working on all INT in town via Smoke Test. | SSO Reached Receiving Water | Phillips Ditch
1636 | 35641 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-10 18:15 |  | 2013-04-11 18:35 | 0 |  | Michelle Ln Caldasak Michelle Ln Extended Phillips Ditch | Untreated Release No aquatic life damage rain into Phillips Ditch before effluent enters stream. | Had pump fail at lift station at high level while it was maintaining. Wasn t able to catch up with flow. Working on all INI in town via smoke testing. | SSO Reached Receiving Water | Phillips Ditch
1636 | 36524 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-18 15:45 | 2013-04-19 20:40 | 2013-04-20 07:10 | 0 |  | Turner Terrace Extended cleanoutChurch and Pearl Street manhole | Precipitation event(s) causing some flooding which keeps storm drains on east side of town from flowing due to flooding of the ditch into which a 36 storm drain empties north of town. Multiple manholes under water. Untreated release to receiving waters. | Contact engineering company to get further information on infiltration problems. | SSO Reached Receiving Water | Phillips Creek
1636 | 36525 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-18 15:45 | 2013-04-19 20:40 | 2013-04-20 07:10 | 0 |  | 615 Michelle Lane cleanoutMichelle Lane cul-de-sac backflow preventer | Precipitation event(s) exceeded capacity of storm sewer system resulting in flooding and submersion of the sanitary sewer system causing untreated release to receiving waters. | Contact engineering company to get further information on infiltration problems. | SSO Reached Receiving Water | Phillips Creek
1636 | 36159 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-18 15:45 | 2013-04-18 19:45 | 2013-04-19 07:33 | 0 |  | Kissel Court Extended clean outChurch and Pearl Street manhole | Precipitation event resulted in untreated release from manholes to receiving waters. Storm drains on east side of town not flowing due to flooding of ditch that 36 storm drain dumps into north of town. Multiple manholes under water on east side of town. Davis SI under 18 water. Storm water not escaping. Sewer manhole under pond of water. | Contact engineering company to get further information on infiltration problem. | SSO Reached Receiving Water | Phillips Creek
1636 | 36169 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-18 15:45 |  | 2013-04-19 07:33 | 210000 | gallons | 615 Michelle Lane cleanoutMichelle Lane cul de sac. backflow preventer | Precipitation event caused flooding of storm drains and put several sanitary manholes under water. Result was an untreated release to receiving waters. | Contact engineering company to get further information on infiltration problems. | SSO Reached Receiving Water | Phillips Creek
1636 | 36217 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-19 08:15 |  | 2013-04-19 08:53 | 0 |  | Bishop and Davis Street manhole. | Storm drains on east side of town not flowing due to flooding of ditch that 36 storm drain dumps into north of town. Multiple manholes under water on east side of town. Davis Street under 18 of water. Storm water not escaping. Sewer manhole under pond of water. Untreated release to receiving waters. | Contact engineering company to get further information on infiltration problems. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Phillips Creek
1636 | 36526 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-19 08:15 | 2013-04-19 12:30 | 2013-04-20 07:10 | 0 |  | Bishop and Davis Streets Manhole | Precipitation event(s) exceeded the capacity of the storm sewer system which resulted in the submersion of sanitary sewer manholes and caused untreated release. | Contact engineering company to get more information on infiltration problems. | SSO Reached Public Land; Storm Sewer
1636 | 36154 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-04-24 06:00 | 2013-04-24 11:15 | 2013-04-24 11:58 | 500000 | gal/ft^2/day | Michelle Ln caldasak backflow preventor Phillip s Ditch | Untreated Release Rain 1.63 inches Plant and sewer lines weren t back to normal from the rain events last week. | Meeting with engineering corp next week to talk about out problems and try to come up with a plan of attack for the problems. | SSO Reached Receiving Water | Phillips Ditch
1636 | 37814 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-06-13 00:30 | 2013-06-13 06:00 | 2013-06-20 14:59 | 0 |  | Michelle Ln cal-de - 5cc 513 N Main | Rain 2.67 inches | Once overflow stops we will clean-up area and neutralize with Aq Lime. Talking to engineering group and have some idea s that they have to mitigate problem until we fix our I&I problem. | SSO Reached Receiving Water | Phillips Ditch
1636 | 37926 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-06-13 00:30 | 2013-06-13 15:45 | 2013-06-14 09:08 | 0 |  | Michelle Ln CAL-DE-SCC 513 N Main | Rain 2.67 inches 513 N Main is a clean out for two houses attached to Turner Terrace. | Once overflow stops we will clean up area and neutralize with AG Lime. Talking to Engineering group and have some idea s that they have to mitigate problem until we fix our I&I problem. | SSO Affected Private Property | Phillips Ditch
1636 | 37835 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-06-13 00:30 |  | 2013-06-13 08:58 | 0 |  | Michelle Ln CAL-SE-SCC | Rain 2.67 inches | Once overflow stops we will clean-up area and neutralize with AG lime. Talking to engineering group and have some idea s that hey have to mitigate problem until we fix our I&I problem. | SSO Reached Public Land; SSO Reached Receiving Water | Phillips Ditch
1636 | 37834 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-06-13 06:00 | 2013-06-13 07:00 | 2013-06-13 09:02 | 0 |  | Church St. & Pearl St Manhole | Rain 2.67 Manhole | Neutralize area with AG lime. Taking to Engineering group and have some idea s that they have to mitigate problem until we fix our I&I problem. | SSO Affected Private Property
1636 | 37838 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-06-13 06:00 | 2013-06-13 07:00 | 2013-06-13 08:58 | 0 |  | Church ST & Pearl ST Manhole | Rain 2.67 inches | Neutralize area with AG Lime. Talking to Engineering Group and have some idea s that they have to mitigate problem until we fix out I&I problem. | SSO Affected Private Property
1636 | 37929 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-06-13 06:00 | 2013-06-13 13:30 | 2013-06-14 09:08 | 0 |  | 513 N Main Phillips Ditch | Rain 2.67 inches 513 N Main is clean out for two houses attached to Turner Terrace. | Once overflow stops we will clean up area and neutralize with AG lime. Talking to Engineering group and have some idea s that they have to mitigate problem until we fix our I&I problem. | SSO Reached Public Land; SSO Reached Receiving Water | Phillips Ditch
1636 | 37837 | IN0020354 | WALTON MUNICIPAL WASTE WATER TREATMENT PLANT | Cass | 2013-06-13 06:00 |  | 2013-06-13 08:58 | 0 |  | 513 N Main Phillips Ditch | Rain 2.67 inches Phillips Ditch | Once overflow stops we will clean-up area and neutralize with AG Lime. Talking to engineering group and have some idea s they have to mitigate problem until we fix our I&I problem. | SSO Reached Public Land; SSO Reached Receiving Water | Phillips Ditch
14858 | 36109 | IN0023604 | Logansport Municipal Utilities Waste Water Treatment Plant | Cass | 2013-04-18 21:00 |  | 2013-04-19 11:26 | 600000 | gallons | Kloenne Street from Culbertson - Bartlett Streets | Untreated release caused by extreme pricipitation event(s). Rivers and tributaries are approaching flood stage. Low lying areas are flooded. Collection system is overburdened with inflow. In some areas collection system is submerged. Bypass pumping has been going on since 21:00 4/18/13 continuously to prevent additional property damage and to permit use of the sewage system. | WWTP operating at capacity. All regulated CSOs are discharging at full capacity along with 4 dewatering stations pumping at capacity. Lift station serving the flooded area is pumping at capacity as well. Rivers are scheduled to peak on 4/21-4/22. Difficult to make progress until rivers subside.LMU has multiple LTCP projects underway to help alleviate problems in this area. Work scheduled to be completed by 4/2014. These projects should lessen the impact of collection system flooding in this area. Follow up report to be submitted 4/22. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Goose Creek; Wabash River
14858 | 36128 | IN0023604 | Logansport Municipal Utilities Waste Water Treatment Plant | Cass | 2013-04-24 04:00 |  | 2013-04-24 02:35 | 337500 | gallons | Intersection of Bartlett & Kloenne Streets Goose Creek & Wabash River | Untreated Release Rain 1.67 inches. Logansport ant he surrounding Cass Co. area received additional rainfall last night and through today on top of the flooding that had occurred over the weekend. The river levels groundwater levels and collection system levels had barely receded since the weekend events and with the rain received over night all of these levels rose considerably requiring LMU to dewater in the area listed above. It is anticipated that dewatering operations (bypassing) will continue into the evening hours of 4/24. There is no projected of forecasted rainfall in the near future so it is our hope to wrap-up this reporting event. Please see the initial submitted reports of 419 and 4/22 for further information. | LMU crew are bypass bypass pumping from a low-lying neighborhood (flood plane) in order to prevent flood damage to the area residential homes and to permit use of the wastewater collection system. This area has been a problematic and histories source of flooding due to high water conditions in the groundwater table as well as high water levels in Goose Creek and they Wabash River. The area is just southeast of the Goose Creek confluence with the Wabash River. LMU continues to fully utilizes in-system storage maintain maximum dewatering efforts at the regulated CSO points and maintain maximum flow through the WWTP in order to minimize the volume of bypassed waters from this area. LMU is in the middle of the three LTCP projects that will help considerably with reducing these events in the future. The projects are scheduled to be fully completed by April 2014. | SSO Reached Receiving Water | Goose Creek; Wabash River
14858 | 36607 | IN0023604 | Logansport Municipal Utilities Waste Water Treatment Plant | Cass | 2013-04-24 04:00 | 2013-04-25 10:00 | 2013-04-25 15:30 | 700000 | gallons | Bartlett and Kloenne Streets | Final Report. Update on flooding issues. The area of tow near the Goose Creek confluence with the Wabash River is in a flood plane and LMU personnel have been bypass pumping from the collection system in order to prevent flooding of the neighborhood and in order to permit the use of the collection system by the area residents. reiver and creek levels as well as the groundwater table are very high and thus inundating the collection system. Crews have been closely monitoring this situation since Thursday night 4/18 - 21:00. Bypass pumping has been off & on since that time. By 1000 this morning 4/25 LMU believes the levels to be low enough to handle normal operations. LMU crews have been on site for nearly one week solid. | Bypass pumping to reduce property damage and permit use of the collection system and to prevent combined sewage from spilling onto the ground in low lying areas. Clean up operations have been continuous. LMU is currently conducting multiple LTCP projects in this affected area that should help consideragly in reducing future events. These projects are scheduled for completion by April 2014. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Goose Creek; Wabash River
666 | 35541 | IN0020419 | Sellersburg Waste Water Treatment Plant | Clark | 2013-01-13 17:00 | 2013-01-13 23:00 | 2013-01-18 18:16 | 4000 | gallons | Manhole SSO #7 Paradise Avenue | Precipitation event caused an Untreated Release from SSO manhole to surrounding ground and storm drain. | Cleaning up area disturbed. Engineers are looking into some type of upgrade for this area. | SSO Reached Public Land; Storm Sewer
666 | 35543 | IN0020419 | Sellersburg Waste Water Treatment Plant | Clark | 2013-01-13 18:30 | 2013-01-13 22:00 | 2013-01-18 18:16 | 1000 | gallons | Manhole at corner of Forrest Drive North and Forrest Drive South | Precipitation event along with saturated ground resulted in Manhole overflow to surrounding ground and storm ditch. | All downstream lift station pumps online. Cleaned part of sewer and did remove some roots. Cleaned up area. Planning on having this main line TVed this week to see what is going on and do a sump pump inspection. | SSO Reached Public Land; Storm Sewer
666 | 34885 | IN0020419 | Sellersburg Waste Water Treatment Plant | Clark | 2013-03-18 08:00 | 2013-03-18 15:00 | 2013-03-18 16:00 | 10000 | gallons | SSO #4 overflowed out of manhole High School LS by 441 N Indiana Ave. | Untreated Release Rain 2.60 inches. Due to 2.60 inches of rain and snow melting the manhole overflowed. All pumps are working. | We will clean up the mess that was made. A engineer is looking on improvement that are needed. | SSO Affected Private Property
666 | 34882 | IN0020419 | Sellersburg Waste Water Treatment Plant | Clark | 2013-03-18 09:00 | 2013-03-18 16:00 | 2013-03-18 16:00 | 0 | gallons | Manhole SSO #07 Paradise Ave. Ran out of manhole on to ground and some went into a storm drain. | Untreated Release Rain 2.6 inches Due to the heavy rains and melting snow we had a overflow all pumps are running. We had 2.6 of rain today. | We are cleaning up the mess that was made. Engineers are looking into some type of upgrade for this area. | SSO Affected Private Property
666 | 42002 | IN0020419 Outfall 001A | Sellersburg Waste Water Treatment Plant | Clark | 2013-11-17 09:00 | 2013-11-17 18:00 | 2013-11-18 15:40 | 0 |  | SSO 4 442 North Indiana Ave | Rain 4.00 inches Exceeded Max Capacity Due 3 inches of rain in 2 hours and a total of 4 inches in 5 hours our creeks & streets were flooded. | See Report | SSO Affected Private Property; SSO Reached Receiving Water
666 | 42004 | IN0020419 Outfall 001A | Sellersburg Waste Water Treatment Plant | Clark | 2013-11-17 10:00 | 2013-11-17 19:00 | 2013-11-18 03:40 | 0 |  | SSO 7 Paradise Ave | Rain 4.00 inches Due to 3 inches of rain in 2 hours and a total of 4 inches in 5 hours our creeks & streets were flooded. | See Report | SSO Affected Private Property; SSO Reached Receiving Water
516 | 35484 | IN0020508 | CHARLESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT & WATER TREATMENT PLANT | Clark | 2013-01-13 | 2013-01-13 | 2013-01-14 13:40 | 5000 | gallons | manhole 3-151 | Precipitation event resulted in untreated release from manhole to receiving waters. | Cleaned up any mess in the area and will flush lines and check for any obstructions. | SSO Reached Receiving Water | Pleasant Run Creek
516 | 34983 | IN0020508 | CHARLESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT & WATER TREATMENT PLANT | Clark | 2013-03-18 | 2013-03-19 | 2013-03-19 14:54 | 50000 | gallons | Spring St station retention basin Pleasant Run Creek | Untreated release Rain 2.8 inches We received rain 0.5 of rain on 3/17/13 then changed over to 2 of snow and then on 3/18/13 we had storms with another 0.3 of rain. | All pumps and controls in operations. Will be back to point repairs as soon as weather breaks. | SSO Reached Receiving Water | Pleasant Creek
516 | 42895 | IN0020508 | CHARLESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT & WATER TREATMENT PLANT | Clark | 2013-12-21 10:15 | 2013-12-21 07:00 | 2013-12-22 07:47 | 7000 | gallons | Manhole 3-155 HWY 62 Station | Rain 4.1 inches All precipitation was received in about a 24hr period and ground is already saturated. | See Report | SSO Reached Receiving Water | Pleasant Run Creek; Fourteenmile Creek
516 | 42898 | IN0020508 | CHARLESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT & WATER TREATMENT PLANT | Clark | 2013-12-22 09:00 | 2014-01-14 04:15 | 2013-12-22 16:47 | 3000 | gallons | Basement at 444 madison & 1115 Water | Roots and grease in main. | See Report | SSO Basement Backup
516 | 39438 | IN0020508 (Affected Waterbody - Unnamed Ditch | CHARLESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT & WATER TREATMENT PLANT | Clark | 2013-07-18 13:30 | 2013-07-18 13:50 | 2013-06-18 15:35 | 0 |  | Hwy 62 Lift Station | Power Failure Pump Station Failure Glitch in incoming power. | See Report | SSO Reached Receiving Water
516 | 41902 | IN0020508 Outfall 001 | CHARLESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT & WATER TREATMENT PLANT | Clark | 2013-11-17 05:45 | 2013-11-17 05:45 | 2013-11-17 12:00 | 0 |  | Hwy 62 lift station manhole 3-155 & 3-171 | Rain 3.5 inches All rain was received in a short period of time. | See Report | SSO Reached Receiving Water | Fourteenmile Creek
516 | 40971 | IN0020508 Outfall 001 | CHARLESTOWN MUNICIPAL WASTE WATER TREATMENT PLANT & WATER TREATMENT PLANT | Clark | 2013-10-06 06:00 | 2013-10-06 10:00 | 2013-10-06 15:18 | 0 |  | Hwy 62 Lift Station Manholes 3.151 & 3-274 | Rain 4.8 inches Extremely heavy downpours occurred in long periods. | See Reports | SSO Reached Receiving Water | Fourteenmile Creek
650 | 35531 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-01-13 09:00 |  | 2013-01-14 10:31 | 0 |  | Riverport II manholes | Precipitation event triggered an untreated release from manholes to storm drain. | Manholes are allowed to overflow during heavy rainfall to prevent damage to property in the area. New treatment plant is expected to be online in mid to late summer of 2013. At that time this flow will be diverted to the new plant in turn eliminating the SSO during heavy rainfall. | SSO Reached Public Land; Storm Sewer
650 | 35128 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-01-13 09:00 | 2013-01-18 08:30 | 2013-01-25 09:04 | 0 |  | Riverport II manholes Jeffersonville IN | Precipitation event caused overflow of Riverport II manholes with untreated release. | No action taken. Manholes are allowed to overflow during heavy rainfall to prevent damage to property in the area. New Treatment Plant is expected to be online in Mid-late summer 2013. At that time this flow will be diverted to the new plant thus eliminating SSO during heavy rainfall. | SSO Reached Public Land; Storm Sewer
650 | 35514 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-01-13 19:00 | 2013-01-13 22:00 | 2013-01-14 10:31 | 576000 | gallons | Mill Creek Lift Station - manhole at CVS pharmacy | Precipitation event overwhelmed the collection system and resulted in untreated release from lift station manhole to storm drain | An 8 pump was set up to relieve pressure in the line and to attempt to prevent property damage. | SSO Reached Public Land; Storm Sewer
650 | 35221 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-01-30 10:45 | 2013-01-30 22:00 | 2013-01-31 14:23 | 0 |  | Manhole Jeffersonville IN | Precipitation event resulted in an untreated release from manhole to storm drain | Allowed to overflow to prevent property damage in the area. North Plant is expected to be online in June 2013 at that time much of the flow from this area will be diverted to the new plant this will eliminate the reoccurring overflow. | SSO Reached Public Land; Storm Sewer
650 | 35092 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-01-30 10:45 |  | 2013-01-30 12:50 | 0 |  | Jeffersonville IN | Precipitation event triggered manhole overflow into storm drain | Overflow allowed to happen to prevent property damage in the area. North plant is expected to be online in June of 2013. At that time much of the flow from this area will be diverted to the new plant an will eliminate this reoccurring overflow. | SSO Reached Public Land; Storm Sewer
650 | 34775 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-02-26 22:00 |  | 2013-02-28 09:30 | 0 |  | Riverport II - manholes | Intermittent heavy rainfall causing Riverport II manholes to back up and overflow as an untreated release. | Manholes are allowed to overflow to prevent property damage to area properties. New plant as well as new lift stations and force mains will eliminate this overflow. New plant should be online in late summer 2013. | SSO Reached Public Land; Storm Sewer
650 | 34510 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-02-26 22:00 | 2013-02-27 07:30 | 2013-03-11 14:00 | 0 |  | RiiverportII Manholes Storm Drain | Untreated Release Rain .53 inches Rainfall was heavy at times causing Riverport II to back up. | Manholes are allowed to overflow to prevent property damage to area properties. new plant as well as new lift station and force mains will eliminate this overflow. new plant should be online in late summer 2013 | Storm Sewer
650 | 34517 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-03-11 10:00 |  | 2013-03-12 09:15 | 0 |  | Riverport II manholes (Port Road) | Untreated Release Rain 1.2 inches | Allowed to overflow to minimize/prevent property damage in the area. The North wastewater treatment plant is scheduled to go online 8/1/13 at this time Riverport II will be diverted to the new plant taking this flow off the area. | SSO Affected Private Property
650 | 34783 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-03-11 10:00 | 2013-03-14 10:30 | 2013-03-14 14:11 | 0 |  | Riverport II manholes (Port Road) | Untreated Release Rain 1.2 inches. | Allowed to overflow to minimize/prevent property damage in the area. Cleaned and stabilized area with Vactor and Lime. The North Wastewater treatment plant is scheduled to go online 8-01-2013 at this time Riverport II will be diverted to the new plant taking this flow off the area. | Storm Sewer
650 | 34771 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-03-13 10:00 |  | 2013-03-18 10:10 | 0 |  | Riverport II Manholes (Port Road) Storm Drain | Untreated Release Rain 1.85 inches manholes are allowed to overflow to prevent property damage. | Manholes are allowed to overflow to prevent property damage. North Plant expected to be online August 1st 2013. At this time flow from this area will be diverted to North Plant. | Storm Sewer
650 | 36650 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-04-24 13:00 | 2013-04-25 07:45 | 2013-04-25 09:05 | 0 |  | Manhole in Riverport II | Precipitation event caused manhole overflow of untreated release to storm drain. | Manholes allowed to overflow to prevent property damage. Pumper truck used to try and keep wet well level down.North plant to be started up on August 1 2013. This flow will then be diverted to the new plant. | SSO Reached Public Land; Storm Sewer
650 | 36150 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-04-24 13:00 |  | 2013-04-24 02:42 | 0 |  | Manhole overflowing from Riverport II Storm Drain | Untreated Release Rain .80 Manholes allowed to overflow to prevent property damage. | Pumper truck was used to try and keep wet well level down. North Plant to be started up on August 1st 2013. This flow will then be diverted to the new plant. | Storm Sewer
650 | 37047 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-05-21 06:30 | 2013-05-21 08:30 | 2013-05-21 03:45 | 0 |  | Mill Creed Lift Station Ground/Drainage Ditch | Untreated Release Equipment Failure The mill Creek Lift Station Analog input card faulted causing the last accurate level of 6.1ft to continue showing on the SCADA. None of the pumps were operating due to the fact that the PLC was reading a level of 6ft in the wet well. The back-up floats were engaged but inhibited by the PLC due to the incorrect level being detected. In turn no level alarms were sent out. The station does have redundant PLC s but only one analog input card. | Collection System staff utilized both a aquatech and a pumper truck to help return the wet well to a normal level. To prevent any repeat of this in the future the Department has bypassed the control relay that inhibits the back-up float operation. The floats are being controlled by relays only with no PLC reliance and added auxiliary contracts on the VFD s to allow the pump relay to run the VFD s at full speed. | SSO Affected Private Property; SSO Reached Receiving Water
650 | 39561 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-06-26 18:45 | 2013-07-12 07:15 | 2013-07-17 08:25 | 0 |  | Riverport II Manholes Port Road Storm Drain | Manholes are allowed to overflow to prevent property damage. | See Report | SSO Affected Private Property
650 | 39433 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-07-21 10:30 | 2013-07-21 15:30 | 2013-07-21 16:10 | 0 |  | Riverport Lift Station manhole (Loop Rd) | VFD on pump#2 faulted at around midnight on 7/21/13 pump shut down and alarm failed to call out. Overflow was discovered at around 11:00am 7/21/13 | See Report | SSO Affected Private Property
650 | 40777 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-10-06 01:30 |  | 2013-10-06 13:30 | 0 |  | Storm Drain | Rain 4.60 inches manholes are allowed to overflow to prevent property damage. | Assisted by using the pumper to truck to take as much out of wet well as possible. Current construction projects are nearly completed that will divert this flow to new wastewater treatment plant. | SSO Affected Private Property
650 | 40779 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-10-06 03:00 |  | 2013-10-06 13:30 | 0 |  | Mill Creek Lift Station | Pumping with 8 pump at this time to prevent back-ups and property damage. The City received nearly 5 of rain in approximately 12 hours causing flooding problems throughout the City. | Pumping into nearby manhole to prevent property damage to area homes and businesses.
650 | 41931 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-11-17 09:14 |  | 2013-11-18 09:00 | 0 |  | Maholes along Port Rd Storm Drain | manholes are allowed to overflow to storm drain to prevent property back-ups in the area. | See Report
650 | 42006 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-11-17 09:14 | 2013-11-18 18:00 | 2013-11-19 15:29 | 0 |  | Manhole along Port Rd. | Rain 2.75 inches Manholes are allowed to overflow to storm drain to prevent property back-ups in the area. | See Report
650 | 41932 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-11-17 10:15 | 2013-11-17 04:25 | 2013-11-18 09:00 | 0 |  | Mill Creek manhole at Rite-Aid | Rain 2.75 inches Heavy rainfall in the area overwhelmed system. | See Report | SSO Affected Private Property
650 | 42897 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-12-21 13:30 |  | 2013-12-21 14:45 | 0 |  | Riverport II Manhole Drainage area ( ditch) | Rain Ongoing issue construction on Lentzier Creek Force main to be complete in January 2014. Once this construction is complete current flow will be diverted to North Plant taking the excessive flow off of the current system. | See Report | SSO Affected Private Property
650 | 42902 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-12-22 | 2013-12-22 06:30 | 2013-12-23 07:39 | 0 |  | Mill Creek Lift Station | Rain 2.54 inches Heavy rains throughout the day. | See Report
650 | 38940 | IN0023302 Ground- Storm Drain | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clark | 2013-06-26 18:45 | 2013-06-26 20:45 | 2013-06-26 20:45 | 0 |  | Riverport II M/H Ground Storm Drain | M/H allowed to overflow to prevent property backups. | See Reports | SSO Affected Private Property
1574 | 36769 | IN0023965 | OAK PARK CONSERVANCY DISTRICT | Clark | 2013-05-04 12:02 | 2013-05-04 14:40 | 2013-05-06 10:39 | 46 | gallons | 154 Forest Drive | Blockage in the main sewer line (root ball and cloth toilet wipe) resulted in untreated release to residential basement. | Blockage was easily cleared with nozzle from sewer cleaner. The roots may have been introduced into the main sewer line from on of the home laterals in the area. Untreated release drained out of basement as soon as blockage was removed. The backup may have resulted from the home not maintaining or having a back flow preventive device. Affected area will be monitored closely until that section of the sewer line can be videotaped by OPCD personnel. The affected homeowner will be informaed about the requirement of a backflow prevention device within the OPCD system if it is found that one is not installed on their lateral line as well as the required maintenance of such a device. | SSO Basement Backup
1574 | 36876 | IN0023965 | OAK PARK CONSERVANCY DISTRICT | Clark | 2013-05-14 04:43 | 2013-05-14 06:56 | 2013-05-15 13:25 | 56 | gallons | 222 Webster Drive and 300 Webster Drive Jeffersonville Indiana 47130 Basements | Equipment Failure Undetermined blockage in main sewer line resulted in system surge that backed up into basements. Both homes are on a common lateral. Neither home has a back flow prevention device installed o n the laterals coming from the homes. This is a violation of the OPCD Wastewater Regulations. | The effected area was cleaned by OPCD personnel using the company owned O Brien Sewer Cleaner. OPCD personnel remained at the location until the levels in the sewer line returned to normal. Property owners for both homes will be sent Notices of Violation letters as it pertains to the required back-flow prevention devices. | SSO Basement Backup
1574 | 38659 | IN0023965 | OAK PARK CONSERVANCY DISTRICT | Clark | 2013-05-24 12:02 | 2013-05-24 02:40 | 2013-05-06 10:30 | 46 | gallons | 154 Forest Drive Jeffersonville In 47130 | Untreated Release Equipment Failure On the morning of 5613 I was informed of a backup in the main sewer line by the responding OPCD personnel that had occurred on 5/24/13. the system backup resulted from a blockage in the main sewer line caused by a root ball and cloth toilet wipe accumulation. As blockage was easily cleared with nozzle from sewer cleaner the roots may have been introduced into the main sewer line from one of the home laterals in the area. The estimated 46 gallons of liquid that backed up in to the basement at 154 Forest Drive drained back into the sewer system after the blockage was cleared. | The basement backup may have resulted from the home not maintaining or having a back flow prevention device. Effected area will be monitored closely until that section of the sewer line can be videoed by OPCD personnel. The effected homeowner will be informed about the requirement of a back flow prevention device within OPCD system if it is found that one is not installed on their lateral line as well as the required maintenance of such a device. | SSO Basement Backup
1574 | 39793 | IN0023965 | OAK PARK CONSERVANCY DISTRICT | Clark | 2013-08-18 09:24 | 2013-08-18 09:24 | 2013-08-19 14:52 | 0 |  | 11 Dellinger Drive Jeffersonville In 47130 | On Monday August 19th the property owner of 11Dellinger Dr came to the plant and reported and SSO he had discovered on Sunday August 18th. OPCD personnel promptly checked the collection lines in the area of 11 Dellinger Drive and found the lines were surged due to root ball that was recovered when the line was cleared. The property owner estimated that 30 gallons of liquid had entered the basement of the home. | The property owner was informed that OPCD regulation require that all properties with low lying drains are to have a back-flow prevention device installed on the property lateral. And that failure to have such a device installed on the lateral line in a violation of the OPCD Regulations. | SSO Basement Backup
1574 | 40162 | IN0023965 | OAK PARK CONSERVANCY DISTRICT | Clark | 2013-08-18 13:46 | 2013-08-18 13:46 | 2013-09-17 08:40 | 0 |  | 11 Dellinger Drive Jeffeersonville In 47130 | On Monday August 19th the property owner of 11 Dellinger Drive came to the plant and reported and SSO that he had discovered on Sunday august 18th. OPCD personnel promptly checked the collection lines in the area of 11 Dellinger Drive and found the lines were surged due to a root ball that was recovered when the line was cleared. The property owner estimated that 30 gallons of liquid had entered the basement of the home. | See Report | SSO Basement Backup
1614 | 42913 | IN0035521 | MEMBERSHIP SANITATION CORPORATION | Clark | 2013-12-21 08:40 | 2013-12-21 22:45 | 2013-12-24 12:47 | 11000 | gallons | Lift Station | Overflow from Pine Dr lift station | See Report | SSO Reached Receiving Water | Miller Creek
14958 | 35792 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-01-13 14:30 | 2013-01-13 23:30 | 2013-01-14 11:57 | 10000 | gallons | manholes located at North Clark & Washington and McKinley & Carter Avenue | Precipitation event triggered untreated release from manholes to storm sewers | We are in the process of building a new plant with a 22MGD capacity. | SSO Reached Public Land; Storm Sewer
14958 | 35244 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-01-13 20:15 | 2013-01-13 23:30 | 2013-01-14 11:57 | 100 | gallons | Station 23 3011 Blackstone Mill Road Clarksville IN | Precipitation event(s) resulted in Untreated Release to storm drain |  | SSO Reached Public Land; Storm Sewer
14958 | 35132 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-01-23 08:00 | 2013-01-23 10:00 | 2013-01-24 11:34 | 500 | gallons | Clarksville Wastewater Treatment Plant Clarksville IN | The plant scum line froze and broke popping the clean out apart creating a partially treated release and bypass of treatment process. | Shut down all scum pumps watiting for the thaw. We will vactor scum pit unt that time. The line itself will be repaired today or tomorrow. It needs to be warm enough to glue plastic pipe. We will monitor the situation more closely during extreme temperatures. | SSO Occurred at Treatment Plant
14958 | 34975 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-03-18 06:00 | 2013-03-18 09:30 | 2013-03-19 08:48 | 5000 | gallons | N Clark & Washington McKinley & Carter | Untreated Release Rain 2.0 inches | We are in the design stage of a new 22MGD plant. | Storm Sewer
14958 | 35135 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-03-27 13:00 | 2013-03-27 13:30 | 2013-03-28 08:13 | 50 | gallons | SIA 109 Linda Ave Ground | Untreated Release Equipment Failure The force main from out pump station developed a leak | We were able to turn off the station and vactor out the sewage to provide service for our customers. The broken line will be repaired today. We will be replacing the station with a new station within the next 2years. | SSO Affected Private Property
14958 | 39795 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-08-21 02:00 | 2013-08-21 09:00 | 2013-08-21 13:36 | 0 |  | Sta 21 103 Potters Lane Drainage Ditch | A free fall on line and knocked out power. Our generator did not start automatically to restore power and we were not contacted by the station. | See Report | SSO Affected Private Property
14958 | 40977 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-10-06 09:30 | 2013-10-06 14:00 | 2013-10-07 08:15 | 0 |  | N Clark & Washington McKinley & Carter (Storm Drain) | Rain 6 inches | See Report
14958 | 40978 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-10-06 10:00 | 2013-10-06 14:00 | 2013-10-06 10:00 | 0 |  | Station #16 747 W Hanson Ave Storm Drain | Rain 6 inches
14958 | 41349 | IN0047058 | Clarksville Waste Water Treatment Plant | Clark | 2013-10-25 13:15 | 2013-10-25 14:30 | 2013-10-26 10:50 | 0 |  | Harrison Ave & Clark Blvd | While repairing a line the contractor was digging out gravel and getting water in his bucket at the same time. When he loaded the trucks with the gravel some of the water ran out. | The cleaned up the streets after the work was completed.
14958 | 42295 | IN0047058 Outfall 010 | Clarksville Waste Water Treatment Plant | Clark | 2013-11-17 08:00 | 2013-11-17 21:00 | 2013-11-18 10:45 | 0 |  | McKinley & Carter | Rain 3.84 inches We overflowed out of manholes at both locations. | See Report | SSO Reached Receiving Water | Mill Creek; Ohio River
14958 | 42294 | IN0047058 Outfall 010 | Clarksville Waste Water Treatment Plant | Clark | 2013-11-17 08:00 | 2013-11-17 21:00 | 2013-11-18 10:45 | 0 |  | N Clark & Washington | Rain 3.84 inches We overflowed out of manholes at both locations. | See Report | SSO Reached Receiving Water | Mill Creek; Ohio River
14958 | 42292 | IN0047058 Outfall 010 | Clarksville Waste Water Treatment Plant | Clark | 2013-11-17 11:45 | 2013-11-17 16:00 | 2013-11-18 11:15 | 0 |  | Manhole at 1046 Redwood Dr | Rain 3.84 inches our lines were surcharged due to the large amount of rain in a short period of time and could not drain out fast enough. | See Report | SSO Basement Backup; SSO Reached Public Land
14958 | 42619 | IN0047058 Outfall 010 | Clarksville Waste Water Treatment Plant | Clark | 2013-12-21 11:30 | 2013-12-22 08:00 | 2013-12-22 11:17 | 0 |  | N Clark & Washington | See Report | See Report | SSO Reached Public Land
14958 | 42620 | IN0047058 Outfall 010 | Clarksville Waste Water Treatment Plant | Clark | 2013-12-21 11:30 | 2013-12-22 08:00 | 2013-12-22 11:17 | 0 |  | Mckinley & Carter | See Report | See Report | SSO Reached Public Land
14958 | 42618 | IN0047058 Outfall 010 | Clarksville Waste Water Treatment Plant | Clark | 2013-12-21 21:00 | 2013-12-21 21:15 | 2013-12-22 11:40 | 0 |  | Primary Clarifiers | See Report | See Report | SSO Reached Public Land
14958 | 38909 | IN0047058 Storm Sewer | Clarksville Waste Water Treatment Plant | Clark | 2013-06-26 17:35 | 2013-06-27 01:30 | 2013-06-07 12:30 | 0 |  | N Clark & Washington Intersection McKinley & Carter Intersection | Rain 2.27 inches | Construction of a 22 MGD plant is to begin withing a few months. | SSO Affected Private Property
673 | 35168 | IN0021211 | BRAZIL MUNICIPAL WASTE WATER TREATMENT PLANT | Clay | 2013-01-30 08:30 | 2013-01-30 09:18 | 2013-01-30 11:57 | 500 | gallons | Forest Green - Lift Station Brazil IN | Precipitation event caused a power loss to Lift Station resulting in untreated release to the ground. | Re-set lift station pumps. Cleaned up area. currently upgrading lift stations and adding back-up generators. Checiing the area for illicit hook-ups | SSO Reached Public Land
673 | 34777 | IN0021211 | BRAZIL MUNICIPAL WASTE WATER TREATMENT PLANT | Clay | 2013-03-13 09:50 | 2013-03-13 10:30 | 2013-03-14 09:45 | 500 | gallons | Hendricks Street Lift Station Ground | Power Failure. Loss of power due to Duke Energy blowing a fuse and lighting arrestor on their line. | The overflow was contained and cleaned up. Lime was put down in area of overflow. | SSO Affected Private Property
673 | 42914 | IN0021211 | BRAZIL MUNICIPAL WASTE WATER TREATMENT PLANT | Clay | 2013-12-23 09:15 | 2013-12-23 10:50 | 2013-12-23 15:49 | 8000 | gallons | Graig Park Manhole | Lift station at Craig Park had rags and debris in the pump valve casing the pumps not to create flow.The City experienced snow melt and almost these inches of rain. The manhole discharge had a lot of snow melt and rain infiltration. | See Report | SSO Affected Private Property; SSO Reached Receiving Water
650 | 39813 | IN0023302 | JEFFERSONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Clay | 2013-08-18 11:00 | 2013-08-18 14:00 | 2013-08-19 07:48 | 0 |  | French Quarter Wet Well | Power Failure Main disconnect was turned off at the distribution panel. Both pumps were off under a locked cover. Station check was performed on Friday 8/16/13. Both pumps appeared to run approximately one hour after inspection. | Lock-out/Tag-out equipment has been placed on station until further inspection. | SSO Reached Receiving Water
1614 | 42904 | IN0035521 Outfall 002 | MEMBERSHIP SANITATION CORPORATION | Clay | 2013-12-21 10:30 | 2013-12-22 02:30 | 2013-12-24 12:47 | 0 |  | Lift Station | Rain 3.8 inches Overflow from lift station. | See Report | SSO Reached Receiving Water | Miller Fork
526 | 39087 | IN0039861 | CLAY CITY MUNICIPAL WASTE WATER TREATMENT PLANT | Clay | 2013-06-26 05:00 | 2013-06-26 09:00 | 2013-06-26 05:00 | 0 |  | Corner of Nye and 1st L/S Clay City Storm Ditch | Rain 3 inches Heavy Rain |  | SSO Affected Private Property
515 | 35532 | IN0020443 | COLFAX MUNICIPAL WASTE WATER TREATMENT PLANT | Clinton | 2013-01-13 10:00 | 2013-01-14 08:00 | 2013-01-14 09:20 | 0 |  | Manhole in Meridian Street | Precipitation event(s) along with snow melt triggered an untreated release from overflow manhole to private property and receiving water.(Called Weir Creek) | We will lime the area when water goes down in the field. | SSO Affected Private Property; SSO Reached Receiving Water | Weir Lake
515 | 36447 | IN0020443 | COLFAX MUNICIPAL WASTE WATER TREATMENT PLANT | Clinton | 2013-04-19 | 2013-04-21 | 2013-04-21 11:05 | 0 |  | Manhole Meridian Street | Precipitation event(s) caused untreated release from manhole to farm field to drain to weir creek. | We will lime area when water goes down in fiels | SSO Affected Private Property; SSO Reached Receiving Water
515 | 36163 | IN0020443 | COLFAX MUNICIPAL WASTE WATER TREATMENT PLANT | Clinton | 2013-04-24 | 2013-04-24 23:00 | 2013-04-24 01:11 | 0 |  | Manhole Meridian St Farm Field to Drain to Weir Creek | Untreated Release Rain 1.5 inches This was on top of the rain we had last week. | We will lime area when water goes down in field. | SSO Reached Receiving Water
1861 | 36606 | IN0020630 | KIRKLIN MUNICIPAL WASTE WATER TREATMENT PLANT | Clinton | 2013-04-18 19:30 | 2013-04-19 15:00 | 2013-04-20 08:28 | 150000 | gallons | MH# 2346 MH# 2627 #7 Ground/ Storm Sewer | Untreated Release Rain 4.25 rain MH 2&3 located in WWTP drive MH#4 located 750 N Main St- Stopped MH#6 located @ intersection of Francis ST & Ohio St- Stopped 7:30pm 4-19-13. MH# 26 & 27 located @ intersection of Washington St & Main St. - stopped 3:00pm 4-19-13 MH#7 Located @ intersection of Ohio St & Stowers St- stopped 3:00pm 4-19-13 | After release stops debris to be removed and lime applied. Town is currently under Agreed Order #2010-19534-W | SSO Affected Private Property; Storm Sewer
1861 | 36237 | IN0020630 | KIRKLIN MUNICIPAL WASTE WATER TREATMENT PLANT | Clinton | 2013-04-18 19:30 | 2013-04-18 22:15 | 2013-04-19 07:20 | 24750 | gallons | Manholes 234626277 | Precipitation event triggered untreated release from multiple manholes to surrounding ground and storm sewers. | Debris will be removed and lime applied after release stops.Town is currently under Agreed Order # 2010-19534-W | SSO Reached Public Land; Storm Sewer
654 | 36288 | IN0022934 | FRANKFORT WASTE WATER TREATMENT PLANT | Clinton | 2013-01-19 11:00 | 2013-01-19 | 2013-04-24 09:30 | 67200000 | gallons | CSO Structure Plant Property | Bypass of a Treatment process Rain 2.28 inches All equipment in place and operating pumping raw sewag4e 67.2 MGD. Larger influx flow. |  | SSO Occurred at Treatment Plant
1618 | 36478 | IN0031976 | MULBERRY WASTE WATER TREATMENT PLANT | Clinton | 2013-04-18 23:00 | 2013-04-19 15:00 | 2013-04-20 07:18 | 100000 | gallons | Main St Lift Stations MH #131 MH #120 MH#34 | Rain 3 inches Heavy rain plus we had a power failure at Main St Lift Stations | We re out after bypass stopped and put lime around area to neutralize. | SSO Affected Private Property
1864 | 36729 | IN0020214 | ODON MUNICIPAL WASTE WATER TREATMENT PLANT | Daviess | 2013-04-28 16:30 | 2013-04-28 16:40 | 2013-04-30 13:37 | 1200 | gallons | East Lift Station | Failure of a hose on the lift station bypass pump resulted in an untreated release to surrounding ground ditch and highway. | Replaced blown hose with a temporary to regain service while repairs are made to the lift station. This is a temporary situation until repairs are complete. | SSO Reached Public Land; Paved Surface
1864 | 39098 | IN0020214 | ODON MUNICIPAL WASTE WATER TREATMENT PLANT | Daviess | 2013-06-26 09:00 | 2013-06-27 08:00 | 2013-06-27 18:45 | 0 |  | Lift Station #003 | Rain 5 inches | See Report | SSO Reached Receiving Water | Kane Ditch
1864 | 40755 | IN0020214 | ODON MUNICIPAL WASTE WATER TREATMENT PLANT | Daviess | 2013-10-05 09:55 | 2013-10-05 04:00 | 2013-10-05 10:09 | 0 |  | Lift Station 505-003 | Equipment Failure | No Discharge | SSO Reached Receiving Water | Kane Ditch
1864 | 42631 | IN0020214 | ODON MUNICIPAL WASTE WATER TREATMENT PLANT | Daviess | 2013-12-21 11:00 | 2013-12-22 03:00 | 2013-12-22 20:30 | 0 |  | Lift Station 003 at S west and E Race St | Rain 6 inches Excessive rainfall lift station ran approximately 16.5 hrs. | See Report | SSO Affected Private Property
1864 | 42632 | IN0020214 | ODON MUNICIPAL WASTE WATER TREATMENT PLANT | Daviess | 2013-12-21 11:00 | 2013-12-22 03:00 | 2013-12-22 20:30 | 0 |  | Lift Station 003 at S West and E Race St | Rain 6 inches Excessive rainfall lift station ran approximately 16.5 hrs | See Report |  | Kane Ditch
8961 | 42971 | IN0039985 Outfall 001 | ELNORA MUNICIPAL WASTE WATER TREATMENT PLANT | Daviess | 2013-12-22 | 2013-12-22 13:00 | 2013-12-23 09:30 | 176000 | gallons | 300 E Indian Street | Rain 6 inches Do to the flooding we had in town we had high flow come in to the plant it starting to upset the plant we had to bypass the plant at the surge tank the bypass water was aeration and some of the solids was removed in the surge tank. | See Report | SSO Reached Receiving Water | Vertrees Ditch
1862 | 36170 | IN0020711 | WATERLOO MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-04-19 01:00 |  | 2013-04-19 10:03 | 0 |  | Waterloo | Precipitation event caused many sanitary manholes and cleanouts to overflow to surrounding ground and receiving waters. | Maximizing flow to WWTP. Investigating sources of I & I to the collection system and removing these sources as they are capable. WWTP is running at capacity and all efforts are being made to transport all flows to the WWTP for treatment. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Cedar Creek
1862 | 37648 | IN0020711 | WATERLOO MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-06-01 07:00 |  | 2013-06-01 07:40 | 0 |  | Manhole at WWTP | Precipitation event triggered overflow of manhole at WWTP. | Maximizing flow at WWTP.The Town of Waterloo is actively investigating sources of I&I to the collection system and removing these sources as they are capable. WWTP is running at capacity and all efforts are being made to transport all flows to the WWTP for treatment. | SSO Occurred at Treatment Plant
1862 | 40654 | IN0020711 | WATERLOO MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-10-02 08:30 | 2013-10-02 11:30 | 2013-10-03 08:13 | 0 |  | Industrial Pkwy Lift Station 105 Industrial Pkwy | Equipment Failure Pump failure the breaker at the service entrance shutting down all controls & redundant pump. WPDC staff reset the breaker and began troubleshooting the failed pump. It was determined that the pump was clear but the motor had an internal electrical fault. A backup pump is being installed today (10-03-13) while the failed pump is being inspected & repaired by a contracted repair service. | Repaired Pump Station See Report | SSO Reached Public Land
1862 | 41116 | IN0020711 | WATERLOO MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-10-10 09:30 | 2013-10-10 10:00 | 2013-10-10 15:45 | 0 |  | Industrial Pkwy Lift Station 105 Industrial | Equipment Failure A clogged pump caused the pump to not be able to keep up with flow coming into the station. This station was operating on one pump - a lag pump and back-up pump had failed during the previous week & were at a motor repair shop. | Repaired Pump Station See Report | SSO Reached Public Land
1862 | 42291 | IN0020711 | WATERLOO MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-11-26 12:00 | 2013-12-03 15:30 | 2013-12-12 09:15 | 0 |  | Gravity manhole immediately upstream of US6 Lift Station | The street department investigated a backup complaint in the vicinity of the lift station and found sewage flowing from the manhole upstream of the lift station. They notified the WPC on -call and opened the panel & found the main breaker tripped. The breaker was reset & the overflow stopped within 5 minutes. A clogged pump was identified as the cause of the breaker trip. Start of overflow is assumed based solely on SCADA information but cannot be verified due to a failure of the SCADA unit. Worst case scenario is assumed when estimating start date/time and total flow. The station is equipped with a visual alarm & because no calls were received prior to Dec 3rd it is highly likely that the overflow did not begin until much more recently. | Repaired Pump See Report | SSO Reached Public Land; SSO Reached Receiving Water
209 | 35497 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-01-13 00:30 | 2013-01-13 06:05 | 2013-01-14 13:02 | 122236 | gallons | CSO Outfall 003 WWTP | Precipitation event exceeded capacity of WWTP and resulted in Untreated Release from CSO Outfall 003 to receiving water. | The flow to and through the WWTP s activated sludge single stage nitrification units was maximized and the flow to and through the wet weather treatment components were maximized. Wet weather treatment components activated and ran as designed. | SSO Reached Receiving Water | Big Run
209 | 35194 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-01-30 03:15 | 2013-01-30 04:20 | 2013-01-30 13:27 | 9144 | gallons | IOutfall 003 Butler WWTP Butler IN | Rain event triggered an untreated release from the WWTP as a result of the Storm Water Plant being out of service due to a broken pipe | The WWTp and storm water pump station were operated as designed. the flow was maximized to and thru the WWTP and the overall duration and volume of discharge from Outfall 003 was decreased because of these actions. The City cleaned the 60 main sewer line to the treatment plant which has helped to maximize storage capacity in that line. Continue to operate using the wet weather operating proceduresn that utilize storage in the collection system to maximize flow to and thru the WWTP and wet weather components. Determine if additional sewer repairs and sewer separation could remove additional volumes of extraneous water which the broken pipe will be fixed as soon as possible. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Big Run
209 | 34495 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-03-11 01:20 | 2013-03-11 10:45 | 2013-03-12 10:44 | 341000 | gallons | Outfall 003 Big Run | Untreated Release Rain .69 inches the discharge on the 11th lasted 7 hours and 25 minutes caused by .69 inches of rain. The frozen ground caused most to run off into the collection system. | The WWTP and storm water pump station were operated as designed. The flow was maximized to and thru the WWTP and the overall duration and volume of discharge from outfall 003 was decreased because of these actions. The City has cleaned the 60 main sewer line to the treatment plant which has help to maximize storage capacity in the line. Continue to operate using the wet weather operating procedures that utilize storage in the collection system to maximize flow to and thru the WWTP and wet weather components. Determine if additional sewer repairs and sewer separation could remove additional volumes of extraneous water. | SSO Reached Receiving Water | Big Run
209 | 35414 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-04-11 04:05 | 2013-04-11 07:20 | 2013-04-12 10:44 | 137662 | gallons | Butler WWTP Outfall 003 Butler IN | Precipitation event triggered an Untreated Release from Outfall 003 as a result of WWTP operating as designed. | The WWTP and storm water pump station were operated as designed. The flow was maximaized to and thru the WWTP and the overall duration and volume of discharge from Outfall 003 was decreased because of these actions. The city has cleaned the 60 main sewer line to the treatment plant which has helped to maximize storage capacity in that line. Continue to operate using the wet weather operating procedures that utilize storage in the collection system to maximize flow to and thru the WWTP and wet weather components. determine if additional sewer repairs and sewer separation could remove additional volumes of extraneous water. | SSO Reached Receiving Water | Big Run
209 | 36376 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-04-19 16:55 | 2013-04-19 20:30 | 2013-04-22 11:07 | 4333169 | gallons | CSO Outfall 003 Butler WWTP | Precipitation event triggered a treatment center bypass to receiving waters. | The wet weather treatment pump station activated but there was no discharge at Outfall 001. The WWTP and storm water pump were operated as designed. The flow was maximized to and through the WWTP and the overall duration and volume of discharge from Outfall 003 has been decreased because of these actions. Continue to operate using the wet weather operating procedures that utilize storage in the collection system to mazximize flow to and through the WWTP and wet weather components. Determine if additional sewer repairs and sewer separation could remove additional volumes of extraneous water. | SSO Reached Receiving Water | Big Run
209 | 36616 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-04-23 22:00 | 2013-04-24 00:45 | 2013-04-25 14:08 | 0 |  | WWTP Outfall 003 | Precipitation event resulted in untreated release from CSO Outfall 003 to receiving water. | The wet weather treatment pump station activated and discharged to outfall 001. The WWTP and storm water pump station were operated as designed. The flow was maximized to and through the WWTP and the overall duration and volume of discharge from Outfall 003 has been decreased because of these actions. Continue to operate using the wet weather operating procedures that utilize storage in the collection system to maximize flow to and through the WWTP and wet weather components. Determine if additional sewer repairs and sewer separation could remove additional volumes of extraneous water. | SSO Reached Receiving Water | Big Run
209 | 37194 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-05-28 06:35 | 2013-05-28 07:15 | 2013-05-29 12:55 | 4000 | gallons | CSO Outfall 003 Big Run Ditch | Untreated Release Rain .71 inches The discharge on the 28th was of short duration (45 min) and caused by approcimately.71 inches. The wet weather treatment pump station activated but there was no discharge at Outfall 001. | The WWTP and storm water pumps station were operated as designed. The flow was maximized to and the thru the WWTP and the overall duration and volume of discharge from outfall 003 has been decreased because of these actions. Continue to operate using the wet weather operating procedures that utilize storage in the collection system to maximize flow to and thru the WWTP and wet weather components. Determine if additional sewer repairs and sewer separation could remove additional volumes of extraneous water. | SSO Reached Receiving Water | Big Run
209 | 38262 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-06-29 23:40 | 2013-06-30 00:20 | 2013-07-01 00:20 | 0 |  | Outfall 003 | Rain .39 inches CSO Outfall 003 The WWTP was at max of 3.34 mgd and the wet weather pump station was running at max. The VFD control on influent pump #1 is broken and has been ordered and will be replaced as soon as possible. The pump was turned on hand to run. | Run WWTP at peak flow when raining run storm pump station at max when it rains. Continue to run wet weather system at max and treatment at max. A study is currently being don on removing storm water from the combined system. | SSO Reached Receiving Water
209 | 39515 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-07-06 13:55 | 2013-07-06 15:25 | 2013-07-08 11:06 | 0 |  | Outfall #003 | Rain .39 inches The WWTP was at max of 3.43 mgd and the wet weather pump station was running at max. | See Report | SSO Reached Receiving Water
209 | 39514 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-07-07 14:30 | 2013-07-07 21:55 | 2013-07-08 12:52 | 0 |  | Outfall #003 | Rain 1.27 inches The WWTP was at max of 3.500 mgd and the wet weather pump station was running at max. | See Report | SSO Reached Receiving Water
209 | 39532 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-07-08 22:05 | 2013-07-09 15:00 | 2013-07-09 13:23 | 0 |  | Outfall #003 | Rain 1>28 inches The WWTP was at max of 3.9mgd and the wet weather pump station was running at max of 3.2 mgd. We received rainfall of 1.28 inches in 50 minutes. We have had 3.5 inches of rain in the last three days. | See Report | SSO Reached Receiving Water | Big Run Ditch
209 | 39454 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-07-20 04:20 | 2013-07-20 06:15 | 2013-07-22 14:24 | 0 |  | Outfall 003 | Rain .93 inches The WWTP was at max of 2673 gpm and the wet weather pump station was running at max. | See Report
209 | 39770 | IN0022462 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-08-12 23:00 | 2013-08-12 23:05 | 2013-08-13 13:35 | 0 |  | Outfall #003 | The WWTP was pumping at max of 3.35 mgd and the wet weather pump station was running at max. | See Report | SSO Reached Receiving Water | Big Run Ditch
209 | 38908 | IN0022462 Waterbody - Big Run Ditch | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-06-26 19:25 | 2013-06-27 20:45 | 2013-06-27 01:25 | 0 |  | Outfall 003 | The WWTP was at max of 3.56 mgd and the wet weather pump station was running at max. The VFD control on influent pump #1 is broken and has been ordered and will be replaced as soon as possible. the pump was turned on hand to run. | See Report | SSO Reached Receiving Water
209 | 42982 | IN0022462 Outfall 003 | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-12-21 09:44 | 2013-12-22 06:30 | 2013-12-30 13:08 | 942600 | gallons | Outfall 003 | Rain 2.1 inches The wwtp was pumping at max of 3.35 mgd and the wet weather pump station was running at max. We had 2.1 inches of rain and 4 inches of snow melt. The site that records all information was down when fixed they sent me what information they could recover. | See Report | SSO Reached Receiving Water | Big Run Ditch
209 | 37605 | IN0022462 Affected Waterbody is: Big Run Ditch | BUTLER MUNICIPAL WASTE WATER TREATMENT PLANT | De Kalb | 2013-06-01 02:40 | 2013-06-01 07:05 | 2013-06-03 10:48 | 486000 | gallons | Outfall 003 Big Run Ditch | Rain 1.59 inches CSO Outfall 003 The WWTP was at max of 3.56 mgd and the wet weather pump station was running at max 1800gpm. | Run WWTP at peak flow when raining run storm pump station at max when it rains. Continue to run wet weather system at max and treatment at max. A study is currently being done on removing storm water from the combined system. | SSO Reached Receiving Water
1858 | 36316 | IN0022969 | GARRETT WASTE WATER TREATMENT PLANT | De Kalb | 2013-04-18 04:39 | 2013-04-19 06:30 | 2013-04-20 11:36 | 1253000 | gallons | SSO #002 (manhole prior to Headworks) Garrett City Ditch | Untreated Release Rain 3.06 inches A total of 3.06 inches of rain was received between 0700 on 4/18 and 0700 on 4.19. This precipitation was onto saturated soils and represents a 10 year storm event. The cumulative total flow for the 10 day period ending on the 19th was 5.15 inches of precipitation which contributed to the soil saturation and excess runoff. The overflow duration (26 hours) and volume (1253000 gallons approximately 800 gpm average) was minimized by the WWTP staff being on site to manually regulate influent pumping maximizing flow to and through the WWTP. The second reserve clarifier tank had been placed into service on 4/11/13 in response to prior precipitation and this helped the WWTP preserve biomass during this extraordinary event. | The wet weather operating operating procedure (to Preserve biomass/prevent biomass from washing out of the system; to dampen the flow surge; and to prevent local basement backups) was immediately implemented and the three (3) influent pumps were manually operated to reduce the volume and duration of the overflow to insure that the maximum flow was processed thru the WWTP and that the overflow event was minimized to the extent possible considering the short duration/ high intensity of the storm event. In addition the staff had previously placed the reserve clarifier into service as part of the wet weather operation. The Garrett WWTP staff will continue to utilize its wet weather operate g procedure to achieve three (3) objectives: (1) maximize flow to and through the WWTP without endangering treatment or losing biomass; (2) prevent basement flooding and overflows in the collection system and (3) minimize the duration and volume of overflows at Outfall 002 to the extent possible. In addition a construction permit application is pending at IDEM for expansion of the WWTP s hydraulic capacity to treat high flows from storm events and elimination of Outfall 002. | SSO Reached Receiving Water | Garrett City Ditch
1858 | 36309 | IN0022969 | GARRETT WASTE WATER TREATMENT PLANT | De Kalb | 2013-04-24 13:00 | 2013-04-24 18:00 | 2013-04-24 14:54 | 24000 | gallons | SSo #002 (Manhole prior to Headworks) Garrett City Ditch | Untreated release Rain 1.19 inches 1.19 inches of rain was received between 0700 on 4/23 and 0700 on 4/24. This precipitation was onto saturated soils and the cumulative total precipitation over the past 5- days (3.06 inches on 4/18 &19) represents as 5 to 10 year storm event. Rainfall over the previous 10 day period was identified in the report submitted on 4/20. The overflow duration (5 hours) and volume (29000 gallons approximately 97 gpm average) was minimized by the WWTP staff responding to a high level wet well alarm (first alarm at 2100 hours on 4/23) and being on site (after the second high level alarm at approximately 0050 hours on the 24th to manually regulate influent pumping operating all 3 influent pumps in the hand mode maximizing flow to and through the WWTP. The second reserve clarifier tank in service (since 4/11/13) in response to the prior precipitation and this helped the WWTP preserve biomass during this and the prior event. | The wet weather operating procedure (to preserve biomass/prevent biomass from washing out of the system: to dampen the flow surge and to prevent local basement backups) was immediately implemented and the three (3) influent pumps were manually operated taken out of PLC mode and operated in the hand mode (from approximately 0050 hours on 4/24 until 1245 hours on the 24th) to reduce the volume and duration of the overflow to insure that the maximum flow was processed thru the WWTP and that the overflow event was minimized to the extent possible considering the duration/intensity of this precipitation event and the precedent precipitation events. In addition as noted the staff had previously placed the reserve clarifier into service as part of the wet weather operation. The Garrett WWTP staff will continue to utilize its wet weather operating procedure to achieve three (3) objectives: (1) Maximize flow to and through the WWTP without endangering treatment or losing biomass; (2) prevent basement flooding and overflows in the collection system: and (3) minimize the duration and volume of overflows at Outfall 002 to the extent possible. As noted on the 4/20/13 report a construction permit application is pending at IDEM for expansion of the WWTP s | SSO Reached Receiving Water
1858 | 37156 | IN0022969 | GARRETT WASTE WATER TREATMENT PLANT | De Kalb | 2013-05-22 | 2013-05-22 | 2013-05-24 11:58 | 100 | gallons | Manhole Upstream of miller s merry Manor Pump Station. Ground around MH No wastewater reached any waterway. | Untreated Release Equipment Failure The Miller s Merry Manor Pump Station (Ejector) was not operating properly and kept alarming because flow into the PS was inadequate to allow the probe to detect a water level to activate the ejector. The alarm light was on but was not immediately reported to the WWTP staff by Miller s Maintenance Department or noted by the random drive-bys performed by the Garrett Police. The initial response to the PS indicated and electrical failure but no electrical issues were detected. Approximately 25 gallons of wastewater was discharged at the manhole on the first day and approximately 100 gallons of wastewater was discharged on the second day. After trouble-shooting all electrical and mechanical components it was found that the influent sewer check valve was partially stuck open with a toilet paper roll spring struck in the check valve. This blockage restricted flow into the pump station causing the periodic problem over the 2 day period ie accumulation of materials flushed down the toilet by the residents and included such items in addition to the toilet paper roll spring as wash cloths towels and lotion bottles. A 5 gallon bucket of material was removed from the blockage. | The problem was addressed over a 2 day period and the influent sewer cleaned and the check valve returned to it s proper operation. WWTP Staff met with the Miller s Merry manor Administrator to explain the problem and to request that closer attention be pain by Manor Staff and Maintenance department to try and prevent materials from being improperly flushed down the toilet. | SSO Affected Private Property
1858 | 37636 | IN0022969 | GARRETT WASTE WATER TREATMENT PLANT | De Kalb | 2013-06-01 03:00 | 2013-06-01 09:00 | 2013-06-02 22:01 | 211000 | gallons | Garret WWTP Outfall 002 | Precipitation event(s) flow exceeded capacity of WWTP influent pumps resulting bypass to Outfall 002 identified as SSO. Reached receiving water. | All 3 influent pumps run in hand mode to maximize pumping to and thru the WWTP to minimize overflow duration and volume.The Garrett WWTP staff will continue to utilze its wet weather operating procedure to achieve 3 objectives: (1) maximize flow to and through the WWTP without endangering treatment or losing biomass; (2) prevent basement flooding and overflows in the collection system; (3) minimize the duration and volume of overflows at Outfall 002 to the extent possible. In addition a construction permit is pending at IDEM for WWTP improvements (expanded influent pumping a 3rd secondary clarifier RAS/WAS distribution modification expanded UV disinfection) that will allow the elimination of Outfall 002. Construction should be initiated in July 2013 and completed by June 2014. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Garrett City Ditch
1858 | 42980 | IN002969 Outfall 002 | GARRETT WASTE WATER TREATMENT PLANT | De Kalb | 2013-12-21 20:30 | 2013-12-22 08:00 | 2013-12-23 12:47 | 70000 | gallons | Outfall 002 | Exceeded Max Capacity Rain 2.5 inches IN excess of 2.5 inches of precipitation (rain and snow/ice melt) on frozen soils was received during the 48 hours before and during the event. | See Report | SSO Reached Receiving Water | Garrett City Ditch
517 | 42972 | IN0022781 | DILLSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Dearborn | 2013-01-21 20:00 | 2013-12-22 04:00 | 2013-12-23 09:07 | 0 |  | Main Lift Station | Rain 3.5 inches3 Inches fell in a short period of time. | See Report | SSO Reached Receiving Water
3996 | 44065 | IN0042056 Outfall 001 | NORTH HOGAN MOBILE HOME PARK | Dearborn | 2013-02-18 09:30 | 2014-02-19 09:30 | 2014-02-19 02:06 | 24000 | gallons | Manhole | Unknown Manhole line to WWTP was inhibited by grease blockage. | Removed Blockage | SSO Occurred at Treatment Plant
1599 | 34999 | IN0050903 | AURORA CITY | Dearborn | 2013-02-04 08:00 |  | 2013-02-04 14:00 | 5000 | gallons | Moore Street Lift Station Manhole Aurora IN | Ohio River back flowing into our collection system & Lift Station manhole at Moore Street. Powerless at this point to prevent it. River stage at 47.64 feet. Expected to start falling in next few days. | Wash down solids. Planned $4.5 million re-design of force mains to carry all this water away. | SSO Reached Receiving Water; Storm Sewer; Surface Soil | Ohio River
1599 | 34800 | IN0050903 | AURORA CITY | Dearborn | 2013-02-26 18:00 | 2013-02-27 09:45 | 2013-02-27 11:00 | 100 | gallons | 10439 Millstone Drive Aurora IN Force Main | Apparent overflow at Force Main location due to problems with air lock or blockage | Constant problems with this stretch of Force Main with eithr airlock or blockage. Removed air relief and relieved pressure on the line that way. Installed another air relief on cleanout spot. Washed down solids. | SSO Reached Public Land; Surface Soil
1599 | 36803 | IN0050903 | AURORA CITY | Dearborn | 2013-04-01 |  | 2013-04-01 09:17 | 250 | gallons | 10623 Millstone Drive | 3 force main leaking untreated release to surrounding ground where a cleanout had been previously installed. | After repair vac truck will be dispatched to clean the affected area.Quit using glue fittings on a pressure system. | SSO Reached Public Land; Subsurface Soil (> 6 inches deep)
1599 | 36353 | IN0050903 | AURORA CITY | Dearborn | 2013-04-21 18:00 | 2013-04-22 08:00 | 2013-04-22 10:51 | 50 | gallons | 10583 Millstone Drive | Failed air relief valve resulted in an untreated release to surrounding ground. | Turned valve off. Removed the air relief washed down solids. | SSO Affected Private Property
1599 | 36603 | IN0050903 | AURORA CITY | Dearborn | 2013-04-25 12:30 | 2013-04-25 13:00 | 2013-04-25 12:53 | 1000 | gallons | 5642 Wilmington Pike | Bolts holding the bonnet on the siphon pit had rusted away allowing an untreated release to surrounding ground and storm drain. | Secured bonnet temporarily until new nuts and bolts can be installed. New nuts and bolts will be stainless steel. Washed down solids from the affected area. | SSO Reached Public Land
1599 | 42358 | IN0050903 | AURORA CITY | Dearborn | 2013-12-09 07:45 |  | 2013-02-09 13:50 | 0 |  | Intersection of U.S 50 and George St | Equipment Failure One of two 8 force mains has failed at the intersection of U.S 50 and George St. possibility that this will be a difficult fix. Pipe depth anywhere between 10 to 30 ft deep. Crew will be working tomorrow 12/10 to see what exactly is leaking and if it can be fixed without rerouting a 500ft section of 8 force main. Currently we are bypassing through CSO #006. | Repaired Pipe See Report | SSO Reached Public Land
1853 | 34972 | IN0053759 | PICNIC WOODS DEVELOPMENT | Dearborn | 2013-03-18 08:30 | 2013-03-18 09:00 | 2013-03-19 09:25 | 1500 | gallons | Equipment Failure Rain 1.7 inches | Equipment Failure Rain 1.7 inches | Reverse and unclogged three -phase pump impeller. Plan to pull and inspect pumps and pump parts. | SSO Reached Receiving Water | Salt Fork
1853 | 35926 | IN0053759 | PICNIC WOODS DEVELOPMENT | Dearborn | 2013-04-16 08:30 | 2013-04-16 12:00 | 2013-04-16 16:28 | 0 |  | Brookestone Lift station Ground | Untreated Release Equipment Failure. Discharge was minimal pump barely maintaining proper flow due to impeller wear. | Replaced malfunctioning lift station pump with rebuilt pump. Rebuild old lifts station pumps. | SSO Affected Private Property
1853 | 39592 | IN0053759 | PICNIC WOODS DEVELOPMENT | Dearborn | 2013-07-24 10:00 | 2013-07-24 11:00 | 2013-07-25 08:55 | 0 |  | Brookstone Lift Sstation Ground | Equipment Failure Damage caused by vandalism. | Pumped sewage with Vac Truck replaced broken 1.2 inch steel pressure gauge piping damaged by vandalism. Replaced broken lock post N Trespassing signs. | SSO Affected Private Property
581 | 34793 | INJ063321 | GREENDALE MUNICIPAL SEWAGE TREATMENT PLANT | Dearborn | 2013-03-15 22:15 | 2013-03-15 15:00 | 2013-03-15 23:26 | 2000 | gallons | 10 Forcemain Ground | Notice small leak coming from the ground crack in 10 force main at the joint. City installing new c900 dr18 pipe and going to abandon the sdr21 thin wall pipe in area of break. Line is off and we are draining forcemain back into lift station. | Replace the old SDR21 at the C900 piping restrained joint at hinge L. Plan on replacing entire forcemain in next four years. City will vac up any liquid plus lime area. | SSO Affected Private Property
581 | 40035 | INJ063321 | GREENDALE MUNICIPAL SEWAGE TREATMENT PLANT | Dearborn | 2013-09-09 09:47 | 2013-09-09 07:30 | 2013-09-09 09:15 | 0 |  | South Schenleg Lift Station | Air release valve body had a crack. Isolated valve. | Repaired Pump Station See Report | SSO Affected Private Property
581 | 41062 | INJ063321 | GREENDALE MUNICIPAL SEWAGE TREATMENT PLANT | Dearborn | 2013-10-07 09:45 | 2013-10-07 10:15 | 2013-10-17 10:00 | 0 |  | See Report | Break in exact location Gas Company (Sycamore Gas) dug 2 weeks ago. Not sure if they nicked pipe. | Repaired Pipe See Report | SSO Affected Private Property
439 | 42975 | IN0020133 | Greensburg Waste Water Treatment Plant | Decatur | 2013-12-22 02:20 |  | 2013-12-22 08:38 | 0 |  | Greensburg Wastewater Treatmenrt Plant Outfall 007 950 Broadway Greensburg In 47240 | Due to the rain total rainfall of 3.40 from December 20th thru December 21 the Greensburg Wastewater Treatment plant had to bypass partially treated flow. the bypass stated at 2:20 am on December 22 2013. A completed report will be faxed once the bypass has stopped. |  | SSO Reached Receiving Water
439 | 42979 | IN0020133 Receiving Stream- Gass Creek | Greensburg Waste Water Treatment Plant | Decatur | 2013-12-22 02:20 | 2013-12-02 17:30 | 2013-12-23 15:24 | 0 |  | Greensburg WWTP Outfall 007 950 S Broadway Greensburg In 47240 | Rain 3.40 inches Due to the rain total rainfall of 3.40 form December 20 thru December 21 the Greensburg WWTP had to bypass partially treated flow. The bypass started a 2:20am on December 22 2013. The CSO related bypass stopped at 5:30pm. | See Report | SSO Reached Receiving Water
15299 | 35898 | IN0020842 | SAINT PAUL WASTE WATER TREATMENT PLANT | Decatur | 2013-01-14 06:00 | 2013-01-14 12:00 | 2013-01-18 16:00 | 100000 | gallons | Riverbend Lift Station | Precipitation event caused untreated release from lift station to receiving waters. | Working on rehabilitating pump fixtures that are leaking. In process of working Midwest Engineering to find and correct I & I. | SSO Reached Receiving Water | Flatrock River
15299 | 37272 | IN0020842 | SAINT PAUL WASTE WATER TREATMENT PLANT | Decatur | 2013-05-29 06:00 | 2013-05-30 10:30 | 2013-05-30 10:00 | 60000 | gallons | Riverbend Lift Station | At the time of pump failure detection a vacuum service was engaged and continues to pump until a pump can be re-installed. That work should be completed in sometime today. | Repaired pump Station. Will suggest to ST Paul s Town Council that pumps need to be upgraded or at least have a spare available. | SSO Reached Receiving Water | Flatfork Creek
15299 | 42978 | IN0020842 Outfall 001 | SAINT PAUL WASTE WATER TREATMENT PLANT | Decatur | 2013-12-21 14:30 | 2013-12-22 08:00 | 2013-12-23 14:57 | 1000000 | gallons | Riverbend Lifstation Conger Wash Manhole | Rain 4.75 inches | See Report | SSO Reached Receiving Water | Flatrock River
518 | 35940 | IN0024830 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-01-11 07:30 | 2013-01-11 15:47 | 2013-01-13 15:47 | 0 |  | Lift Station on South West Street | Precipitation event coupled with snow melt triggered an untreated release from the lift station to receiving waters. | Cleaned areas as needed. AG 2003-130-94w | SSO Reached Receiving Water | Millstone Creek
518 | 35874 | IN0024830 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-01-13 |  | 2013-01-13 17:00 | 0 |  | Lift station at South West Street | Precipitation event caused lift station overflow of untreated release to receiving waters | Clean areas as needed. AG 2003-130-94w | SSO Reached Receiving Water | Millstone Creek
518 | 35031 | IN0024830 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-01-30 | 2013-01-31 | 2013-02-01 14:47 | 0 |  | Lift Station at South West Street Westport IN | 1/30/2013 found Lift Station overflowing. !.15 inch rain event triggered untreated release from Lift Station. Overflow had stopped by morning of 1/13/2013. | Clean areas as needed. AG 2003-130-94w | SSO Reached Receiving Water | Millstone Creek
518 | 34945 | IN0024830 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-03-18 | 2013-03-18 | 2013-03-18 16:49 | 0 |  | Lift STation @ S. West ST manhole 74a7696a973 | Untreated release rail 2.0 inches. Found Lift Station and manholes listed overflowing on morning of 3-18-13. Received 2 inches of rain in early am. Stream flow at 60+ mgd for dilution. | Clean area as needed AG 2003-130-94W | SSO Reached Receiving Water | Millstone Creek
518 | 40346 | IN0024830 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-09-12 12:10 | 2013-09-20 12:10 | 2013-09-24 16:01 | 0 |  | Effluent structure at final lagoon. | Exceeded Max Capacity Started discharging 9-20-13 in am with lagoons level dropped to a comfortable level. Weekly samples taken during period of discharge. Receiving stream monitored with no problems noticed. Sample results BOD 8.8 SS 10 PH 8.9 AMN 3.33 E. Coli 33.2 at start. Sample results at end BOD 9.6 SS 9 PH 8.5 AMN 4.0 E. Coli 124 | See Report | SSO Reached Receiving Water | Millstone Creek
518 | 40123 | IN0024830 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-09-12 15:16 |  | 2013-09-13 15:19 | 0 |  | Effluent structure at final lagoon | Exceeded Max Capacity Started discharging because lagoons are full. Stream flow is 0 so dilution ratio cannot be met. Talked with our inspector Kevin Holtz and discussed amount of water to discharge. Samples will be taken until discharge is stopped. Weekly reports will be sent regarding flow and sample results. | See Report | SSO Reached Receiving Water | Millstone Creek
518 | 41798 | IN0024830 Outfall 001 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-11-12 09:00 |  | 2013-11-13 09:25 | 0 |  | Effluent structure at final lagoon | Exceeded Max Capacity Started discharging because lagoons are full. Stream flow is .521mgd so the need to discharge more than the dilution ration will allow. Samples will be taken and weekly reports will be sent regarding flow and samples. | See report | SSO Reached Receiving Water | Millstone Creek
518 | 41886 | IN0024830 Outfall 001 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-11-14 15:04 | 2013-11-15 09:15 | 2013-11-15 10:07 | 0 |  | M H #3 at the Lift Station | Equipment Failure The fuse that controls the pumps and alarm system blew. Chart showed that pump station last pumped about 2:30 on 11-14. 60000 gallon estimate was based on amount pumped 11-14 to amount from 11-13. Overflow ran across lift station property to Millstone Creek | Repaired pump Station See Report | SSO Reached Receiving Water | Millstone Creek
518 | 42976 | IN0024830 Outfall 001 | WESTPORT SEWAGE TREATMENT PLANT | Decatur | 2013-12-21 | 2013-12-22 | 2013-12-23 09:30 | 0 |  | MH 7476788083 | Rain 3.85 inches Received 3.85 inches of raon and had flooding of all streams and roadways in town. | See Report | SSO Reached Receiving Water
665 | 35870 | IN0020150 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-01-11 |  | 2013-01-11 | 0 |  | 601 CR600 Lift Station to receiving location 9608 West Lone Beech Drive | Precipitation event causes large amount of untreated release from lift station to receiving waters. |  | SSO Reached Receiving Water
665 | 35462 | IN0020150 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-01-13 07:00 | 2013-01-14 07:00 | 2013-01-14 08:30 | 0 |  | Manhole at WWTP | Precipitation and snow melt caused an overflow of untreated release from the WWTP manhole to ground surrounding it. High Plant flows caused wash out of pin flock from final clarifiers. Wet well full. Plant at max flow. | Regulated return sludge flow rate. I & I study. Reduction of I &I orange in place. Pumps pumping at max flow. Grout sealing of manholes.
665 | 36034 | IN0020150 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-04-16 19:00 | 2013-04-16 21:40 | 2013-04-17 19:50 | 0 |  | WWTP | Precipitation event and river flooding cause some washout of solids from final clarifiers. | Construction of new sewer main manhole not set in place. Let rain runoff run into sewer. Set manhole casting. Talked with construction company about the importance of covering all manholes and end of pipe at the end of each day. | SSO Occurred at Treatment Plant
665 | 36494 | IN0020150 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-04-18 | 2013-04-18 09:00 | 2013-04-19 15:35 | 0 |  | Town of Yorktown WWTP | Precipitation event resulted in wash out of solids from final clarifiers at WWTP. Partially treated release . | Regulated return sludge flow rate and flow to finals. I & I reduction ordinance in place. | SSO Occurred at Treatment Plant
665 | 39959 | IN0020150 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-09-03 15:30 | 2013-09-03 16:30 | 2013-09-05 10:47 | 0 |  | Lift station force main sewage air valve | Equipment Failure Sewage air valve on force main stuck open 50 gallon of sewage on ground at lift station. | Removed Blockage See Report | SSO Affected Private Property
665 | 42990 | IN0020150 Outfall 001 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-12-21 21:30 | 2013-12-23 14:00 | 2013-12-23 15:54 | 0 |  | Manhole at WWTP | Rain 4.90 inches 4.90 rain white river at flood stage. | See Report | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
665 | 42987 | IN0020150 Outfall 001 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-12-21 21:30 |  | 2013-12-23 09:41 | 0 |  | Manhole at WWTP | Rain 4.90 inches 4.90 rain white river at flood stage. | See Report | SSO Reached Public Land; SSO Occurred at Treatment Plant | White River
665 | 42989 | IN0020150 Outfall 001 | YORKTOWN WASTE WATER TREATMENT PLANT | Delaware | 2013-12-23 22:00 |  | 2013-12-23 09:41 | 0 |  | Primary Digestor over flowed. | Equipment Failure Rain 4.90 inches Primary sludge valve did not close and allowed to pump to run. Operators are to told to stay with pump until don pumping sludge. | See Report | SSO Reached Public Land; SSO Occurred at Treatment Plant
15338 | 34709 | IN0021652 | EATON MUNICIPAL SEWAGE TREATMENT PLANT | Delaware | 2013-02-26 10:00 | 2013-02-26 15:00 | 2013-02-26 15:15 | 30000 | gallons | cso #2 AI plant | Untreated Release and Bypass of Treatment Process caused by power failure to the entire town of Eaton IN on 2/26/2013 | Power restored to the City of Eaton which brought the plant back online | SSO Reached Receiving Water | Mississinewa River
14830 | 35789 | IN0025631 | MUNCIE WASTE WATER TREATMENT PLANT | Delaware | 2013-01-13 11:00 | 2013-01-13 23:55 | 2013-01-14 11:03 | 122687 | gallons | Benson Overflow Manhole | Precipitation event coupled with snow melt resulted in untreated release from overflow manhole to receiving waters. | System overwhelemed. Overflow ceased as soon as was possible. Situation was monitored closely. | SSO Reached Receiving Water | Jakes Creek
14830 | 38864 | IN0025631 | MUNCIE WASTE WATER TREATMENT PLANT | Delaware | 2013-06-22 16:40 | 2013-06-22 11:43 | 2013-06-24 13:57 | 0 |  | Port Ave | Manhole | Sewer maint. Will be jet rodding sanitary to determine cause. Will monitor results of sewer maint. | SSO Reached Receiving Water | Buck Creek
14830 | 40063 | IN0025631 | MUNCIE WASTE WATER TREATMENT PLANT | Delaware | 2013-09-10 11:31 | 2013-09-10 12:15 | 2013-09-01 12:38 | 0 |  | CSo #28 (Franklin St) | Contractor bypass pumping interceptor caused CSO #28 to surcharge. Condition modified immediately to cause overflow. | See Report | SSO Reached Receiving Water | White River
14830 | 42985 | IN0025631 Outfall 021A | MUNCIE WASTE WATER TREATMENT PLANT | Delaware | 2013-12-21 23:00 |  | 2013-12-21 22:49 | 0 |  | Benson/ Jakes Creek | Rain 3.15 inches | See Report | SSO Reached Receiving Water | Jakes Creek
14830 | 42986 | IN0025631 Outfall 21A | MUNCIE WASTE WATER TREATMENT PLANT | Delaware | 2013-12-21 21:40 | 2013-12-22 18:00 | 2013-12-23 10:09 | 0 |  | Benson Manhole | Exceeded Max Capacity Rain 3.5 inches Rainfall/snow melt 12/21 12/22 exceeded 3.5 - 4 - exceeded all system capacities. All equip preformed correctly overflow occured @ manhole. | See Report | SSO Reached Receiving Water | Jakes Creek
14830 | 48801 | IN0025631 Waste goes to Muncie Plant | MUNCIE WASTE WATER TREATMENT PLANT | Delaware | 2013-02-27 05:15 | 2013-02-27 06:00 | 2013-02-27 | 0 |  | Gate Valve 600W | Caused by pump failure. | Removed Blockage See Report | SSO Reached Receiving Water
14830 | 48802 | IN0025631 Waste goes to Muncie Plant | MUNCIE WASTE WATER TREATMENT PLANT | Delaware | 2013-12-21 10:00 | 2013-12-21 10:20 | 2013-12-24 09:22 | 0 |  | CR 600 W Lift Station Gate Valve | Snow Melt 21/2 inches rain and snow melt caused creek to go over it s banks causing water to flow over the gate valve. | See Report | SSO Reached Receiving Water
664 | 42992 | IN0020834 Outfall 001 | JASPER MUNICIPAL WASTE WATER TREATMENT PLANT | Dubois | 2013-12-23 14:00 | 2013-12-22 13:00 | 2013-12-23 10:24 | 0 |  | Treatment Plant | Exceeded Max Capacity Rain 4.0 inches Due to the ground being saturated after receiving 7 inches of snow in the last 2 weeks and then being hit with 4 inches of rain on 12/21/13 the plant s capacity was exceeded causing the surge tanks to overflow. The overflow was metered and blended with final effluent along with being sampled. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Patoka River
664 | 35246 | IN0020834 | JASPER MUNICIPAL WASTE WATER TREATMENT PLANT | Dubois | 2013-01-13 14:30 | 2013-01-13 19:00 | 2013-01-14 10:39 | 175000 | gallons | Jasper Wastewater Treatment Plant Jasper IN | Precipitation event(s) and snow melt pushed treatment plant to maximum and beyond causing need for treatment operation bypass and reblending and sampling of effluent. | Continue to look for I & I along with continuing our programs like inspecting real estate when there is a change of ownership and our Holy Family I & I project. | SSO Occurred at Treatment Plant
664 | 35140 | IN0020834 | JASPER MUNICIPAL WASTE WATER TREATMENT PLANT | Dubois | 2013-03-27 13:30 | 2013-03-27 14:00 | 2013-03-27 15:50 | 2500 | gallons | Force Main | Untreated Release Equipment Failure Air relief failed | Shut off lift station Repaired air relief | SSO Affected Private Property
1627 | 42991 | IN0023124 001A | Huntingburg Municipal Waste Water Treatment Plant | Dubois | 2013-12-21 15:00 | 2013-12-21 20:30 | 2013-12-23 06:35 | 10000 | gallons | SSO Outfall 003 ready mix lift station | Rain 2.4 snow melt | See Report |  | Patoka River
15232 | 40032 | IN0052698 | Patoka Lake Regional Water & Sewer District | Dubois | 2013-09-07 09:15 | 2013-09-07 15:30 | 2013-09-09 10:19 | 0 |  | Force Main 10 Patoka Lake | Gasket leaking on fitting. | Replaced some piping and put new 10 valve in. | SSO Reached Receiving Water | Patoka Lake
12068 | 35586 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-01-04 09:08 |  | 2013-01-14 14:04 | 200 | gallons | 252 East Market Street | City sewer blockage resulted in untreated release into residential basement. | Vacuumed water from manhole and jetted sewer line to remove obstruction. Increase the preventive cleaning of sewer. | SSO Basement Backup
12065 | 35588 | IN0021466 | Maple Leaf Farms Incorporated | Elkhart | 2013-01-07 15:15 | 2013-01-07 16:10 | 2013-01-08 16:04 | 20 | gallons | 158 North Madison Street | Residential sewer blockage resulted in untreated release into residential basement. | Vacuumed manhole cleaned city line minor rehabilitation of manhole. | SSO Basement Backup
12068 | 35037 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-01-31 12:30 | 2013-01-31 13:15 | 2013-01-31 16:01 | 1600 | gallons | 50 Broad Street Nappanee IN | Basement Back Up | Jetted sewer clearing blockage. Reclean at 60 days and monitor closely. | SSO Basement Backup
12068 | 34488 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-03-10 02:00 | 2013-03-10 03:45 | 2013-03-12 13:15 | 100 | gallons | 405 North Madison St - Basement Backup | Equipment Failure Sewer clog located in line approximately 15 feet downstream of residence. | The sewer was jetted to remove the blockage. Additional cleaning of the sewer is planned for June of 2013 | SSO Basement Backup
12068 | 36068 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-04-17 09:50 | 2013-04-17 16:30 | 2013-04-18 15:31 | 1500 | gallons | 507 North Elm | Precipitation event and I & I contribution resulted in an untreated release to a residential basement | Sewers running but full of combined sanitary and storm water. Working with homeowner to install back flow preventer. Cleaned up sewer solids. Investigating backflow preventer. | SSO Basement Backup
12068 | 36066 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-04-17 21:45 | 2013-04-17 23:45 | 2013-04-18 15:31 | 1900 | gallons | 752 West Walnut | Precipitation event and I & I contribution resulted in a backup into a residential basement. | Sewers running but full of combined sanitary and stormwater. Addressed sewer solids. Implementing CSO LTCP. | SSO Basement Backup
12068 | 36069 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-04-17 21:45 | 2013-04-17 21:55 | 2013-04-18 15:32 | 1500 | gallons | 507 North Hartman | Precipitation event and I & I contribution resulted in backup to a residential basement. | Sewers running but full of combined sanitary and storm water. Addressed sewer solids. Working with homeowner to address potential furnace damage. Working to implement CSO LTCP. | SSO Basement Backup
12068 | 36067 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-04-17 22:00 | 2013-04-17 22:00 | 2013-04-18 15:31 | 50 | gallons | 901 West VanBuren | Precipitation and I & I contribution resulted in an untreated release to a residential basement. | Sewer running but full of combined sanitary and stormwater. Addressed sewer solids.Working to implement CSO LTCP | SSO Basement Backup
12068 | 36468 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-04-18 | 2013-04-19 | 2013-04-19 14:11 | 10 | gallons | 462 East Market Street | Precipitation event triggered untreated release into residential basement. | No action taken. Now water standing. Only customer reported evidence of event.Implementation of LTCP | SSO Basement Backup
12068 | 39744 | IN0021466 | Nappanee Waste Water Treatment Plant | Elkhart | 2013-08-07 17:15 | 2013-08-07 17:30 | 2013-08-08 14:13 | 0 |  | 161 S Main | Property roof drains tired to sanitary sewer. High intensity rain event caused lateral backup. | Advised property owner to redirect roof drains to surface of alley behind building instead of sanitary sewer lateral. Follow up with property owner in 60 day to confirm renovation. | SSO Basement Backup
33028 | 37162 | IN0023761 | MIDDLEBURY WASTE WATER TREATMENT PLANT | Elkhart | 2013-05-23 19:00 | 2013-05-24 07:30 | 2013-05-24 15:58 | 35000 | gallons | WWTP RAS pump 121 York Drive | Equipment Failure Pipe Failure. On the RAS structure there was an 8 Inch endplate with a 1.50 inch treaded end cap in the drywell. The treaded endcap below out the end the drywell flooded and approximately 35000 gallons discharged on the property. Flow was stopped before the stream. | Pumped drywell and repaired 1.5 inch treaded plug. Going to replace 8 inch end caps with standard blinds. This will eliminate the threaded plugs. | SSO Affected Private Property
11960 | 35884 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-01-12 13:06 | 2013-01-12 14:20 | 2013-01-11 17:26 | 516 | gallons | 913 Princeton | Grease and plastic blockage of main sewer line caused residential back up | Cleaned sewer to remove obstruction.The City of Elkhart proactively maintains over 200 miles of sewer with a preventive maintenance program that cleans sewers on a four year rotation and catch basins annually. We have an ongoing BMP sweeping program in the City of Elkhart with a three week rotation interval during non-winter weather. We also have a CSO inspector who checks our CSOs on a daily basis. The City monitors and controls its lift stations using telemetry systems to provide accurate and timely information on potential mechanical or electrical problems that may lead to system overflows. Our plant and lift stations are designed with firm capacity and we keep a critical spare parts inventory. Our equipment is on a preventive maintenance program. Our staff has multidisciplinary skills and experience in diagnosing and correcting problems. The City of Elkhart views bypasses of treatment or overflows as emergencies and mobilizes all available and appropriate resources to deal with these events when all our preventive measures come up short. | SSO Basement Backup
11960 | 35091 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-01-29 18:24 |  | 2013-01-30 12:08 | 100 | gallons | 1714 Roys Avenue Elkhart IN | Basement back up as a result of extensive snow melt causing wide spread flooding. | Upon inspection sewer main was not obstructed and was likely hydraulically overloaded at the time of the back up. Will clean main line on 1/30 to ensure maximum hydraulic capacity is available. Resident will be made aware of our basement valve program. | SSO Basement Backup
11960 | 34903 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-02-11 20:30 | 2013-02-12 00:25 | 2013-02-12 08:47 | 1653 | gallons | Resident basement at 1600 Brookwood Elkhart IN | Basement backup. Clogged main sewer line. Untreated Release into customer basement | When responding to the call staff found the main sewer line was plugged with roots and grease. The plug was isolated that section of sewer was immediately cleaned and the backup subsided. Resident made aware of basement valve program. The City of Elkhart proactively maintains over 200 milles of sewer with a preventive maintenance program that cleans sewers on a four year rotation and catch basins annually. We have an ongoin BMP sweeping program in the City of Elkhart with a thre week rotation interval during non-winter weather. We alsohave a CSO inspector who checks our CSO s on a daily basis. The City monitors and controls its lift stations using telemetry systems to provide accurate and timely information on potential mechanical or electrical problems that may lead to system overflows. Our plant and lift stations are designed with firm capacity and we keep a critical spare parts inventory. Our equipment is on a preventive maintenance program. Our staff has multidisciplinary skills and experience in diagnosing and correcting problems. The City of elhart view bypasses of treatment or overflows as emergencies and mobilizes all available and appropriate resources to deal with these events when all our preventive measures come up short. | SSO Basement Backup
11960 | 34352 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-02-11 20:30 | 2013-02-12 00:25 | 2013-02-12 09:00 | 1653 | gallons | 1600 Brookwood | Received call - staff found the main sewer line was plugged with roots and grease. | The plug was isolated that section of sewer was immediately cleaned and the backup subsided. The amount that entered the resident s basement is estimated to be 1653 gallons. This stretch of sewer was last cleaned in 2010. The sewer in this area is shallow and runs in the tree lawn. This entire stretch is being cleaned today. | SSO Basement Backup
11960 | 35306 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-02-11 20:30 | 2013-02-12 00:25 | 2013-04-01 09:00 | 11653 | gallons | 1600 Brookwood Basement Back-up | When responding to the call staff found the main sewer line was plugged with roots and grease. The plug was isolated that section of sewer was immediately cleaned and the backup subsided. The amount that entered the residents basement is estimated to be 1.653 gallons. This stretch of sewer was last cleaned in 2010. The sewer in this area is shallow and runs in the tree lawn. This entire stretch of sewer is being cleaned today. | Resident will be made aware of our basement valve program. The City of Elkhart proactively maintains over 200 miles of sewer with a preventive maintenance program that cleans sewers on a four-year rotation and catch basins annually. We have an ongoing BMP sweeping program in the City of Elkhart with a three-week rotation interval during non-winter weather. We also have a CSO inspector who checks our CSO s on a daily Basis. The City monitors and controls it lift stations using telemetry systems to provide accurate and timely information on potential mechanical or electrical problems that may lead to system overflows. Our plant and lift stations are designed with firm capacity and we keep a critical spare parts inventory. Our equipment is on a preventive maintenance program. Our staff has multidisciplinary skills and experience in diagnosing and correcting problems. The City of Elkhart views bypasses of treatment or overflows as emergencies and mobilizes all available and appropriate resources to deal with these events when all our preventive measures come up short. | SSO Basement Backup
11960 | 35486 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-04-04 09:30 | 2013-04-04 09:26 | 2013-04-05 08:57 | 60 | gallons | Private lateral clean-out @ Bridge Street N Sidewalk Street Catch Basin Storm Sewer St Joseph River | Untreated Release A private lateral at Bridge Street backed up and discharged out of the manhole cleanout located in the sidewalk. he immediately called the pumper truck then checked the storm sewer outfall which was not yet discharging. By the time the pumper came cleaned the line from the cleanout to the main and the flow in the street approximately 60 gallons of water (combination of flow from the cleanout overflowing and wash water from the pumper truck cleaning up the street) was discharged to the river. | City pumper truck dispatched to site to clean street and stop flow. The owner was contacted and informed the entire line must be cleaned which was don. Dye tests were conducted to determine which properties contributed to this line. The owner was told this problem must be addressed and was given information regarding the City s sewer insurance program. | SSO Affected Private Property; SSO Reached Receiving Water; Storm Sewer | Saint Joseph River
11960 | 35482 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-04-04 09:30 | 2013-04-04 09:36 | 2013-04-05 08:54 | 60 | gallons | Private lateral clean-out @ Bridge Street N sidewalk | Untreated Release A private lateral at Bridge Street backed up and discharged out of the manhole cleanout located in the sidewalk. Our CSO Inspector was making his rounds and observed it flowing into the street to the catch basin. he immediately called the pumper truck then checked the storm sewer outfall which was not yet discharging. By the time the pumper came cleaned the line from the cleanout to the main and the flow in the street approximately 60 gallons of water (combination of flow from the cleanout and wash water from the pumper truck cleaning up the street) was discharged to the river. | City pumper truck dispatched to site to clean street and stop flow. The owner was contacted and informed the entire line must be cleaned which was done. Dye tests were conducted to determine which properties contributed to this line. The owner was told this problem must be addressed and was given information regarding the City s sewer insurance program. | SSO Affected Private Property; SSO Reached Receiving Water; Storm Sewer | Saint Joseph River
11960 | 36763 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-05-03 07:59 | 2013-05-03 08:24 | 2013-05-03 11:42 | 234 | gallons | CSO 23 8th and Franklin | High system volumes with the addition of hydrant flushing exceeded the capacity of the combined sewer system resulting in CSO untreated overflow into receiving water. | Immediately upon discovery of the overflow the hydrant flushing was stopped and the overflow stopped as well.The City of Elkhart proactively maintains of 200 miles of sewer with a preventive maintenance program that cleans sewers on a rour-year rotation and catch basins annually. We have an ongoing BMP sweeping program in the City of Elkhart with a three-week rotation interval during non-winter weather. We also have a CSO inspector who checks our CSOs on a daily basis. The City monitors and controls its lift stations using telemetry systems to provide accurate and timely information on potential mechanical or electrical problems that may lead to system overflows. Our plant and lift stations are designed with firm capacity and we keep a critical spare parts inventory. Our equipment is on a preventive maintenance program. Our staff has multidisciplinary skills and experience in diagnosing and correcting problems. The City of Elkhart views bypasses of treatment or overflows as emergencies and mobilizes all available and appropriate resources to deal with these events when all our preventive measures come up short. | SSO Reached Receiving Water | Saint Joseph River
11960 | 38672 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-05-03 07:59 | 2013-05-03 08:24 | 2013-05-03 11:45 | 234 | gallons | CSO 23 8th & Franklin St Joe River | Untreated Release Combined system was hydraulically overloaded due to inflow and annnual hydrant flushing. | Volumes i the collection system have been extremely high for the past couple of weeks due to inflow caused by too extensive rain in mid-late April. The Water Utility has been conducting annual hydrant flushing resulting compounding the hydraulic loading of the collection system. When the overflow was discovered hydrant flushing in the basin was immediately stopped and the overflow then stopped. | SSO Reached Receiving Water | Saint Joseph River
11960 | 36772 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-05-06 07:47 | 2013-05-06 09:25 | 2013-05-06 15:25 | 844 | gallons | CSO 16 Goshen and Superior | High system volumes with the addition of hydrant flushing exceeded the capacity of the combined sewer system resulting in CSO untreated overflow into receiving water. | Immediately upon discovery of the overflow the hydrant flushing was stopped and the overflow stopped as well.The City of Elkhart proactively maintains of 200 miles of sewer with a preventive maintenance program that cleans sewers on a four-year rotation and catch basins annually. We have an ongoing BMP sweeping program in the City of Elkhart with a three-week rotation interval during non-winter weather. We also have a CSO inspector who checks our CSOs on a daily basis. The City monitors and controls its lift stations using telemetry systems to provide accurate and timely information on potential mechanical or electrical problems that may lead to system overflows. Our plant and lift stations are designed with firm capacity and we keep a critical spare parts inventory. Our equipment is on a preventive maintenance program. Our staff has multidisciplinary skills and experience in diagnosing and correcting problems. The City of Elkhart views bypasses of treatment or overflows as emergencies and mobilizes all available and appropriate resources to deal with these events when all our preventive measures come up short. | SSO Reached Receiving Water | Elkhart River
11960 | 38675 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-05-06 07:47 | 2013-05-06 09:25 | 2013-05-06 03:35 | 844 | gallons | CSO 16 Goshen and Superior Elkhart River | Combined system was hydraulically overloaded due to inflow and annual hydrant flushing. | CSO 16 Goshen and Superior Elkhart River | SSO Reached Receiving Water | Elkhart River
11960 | 37044 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-05-21 05:15 | 2013-05-21 05:50 | 2013-05-21 16:51 | 0 |  | 144 1462 1464 Hudson St Basement back-up | Untreated Release Rain .5 inches Responding to the call following an extremely intense rainfall during the morning hours of 5-21-31 staff found the flow in the main line flowing normal and no sign of any obstruction. As a precaution the main on Hudson was cleaned from the manhole upstream of the callers address to the CSO chamber as well as the effluent and overflow line leaving the CSO chamber. During the cleaning of the overflow line debris was encountered and it was broken loose. It is suspected this debris restricted flow in the overflow line from the CSO chamber resulting in the back-up of the upstream basements on Hudson. | The City of Elkhart proactively maintains over 200 miles of sewer with a preventive maintenance program that cleans sewers on a four-year rotation and catch basins annually. We have an ongoing BMP sweeping program in the City of Elkhart with a three-week rotation interval during non-winter weather. We also have a CSO inspector who checks our CSOs on a daily basis. The City monitors and controls its lift stations using telemetry systems to provide accurate and timely information on potential mechanical or electrical problems that may lead to system overflows. Our plant and left stations are designed with firm capacity and we keep a critical spare parts inventory. Our equipment is on a preventive maintenance program. Our staff has multidisciplinary skills and experience in diagnosing and correcting problems. The City of Elkhart views bypasses of treatment or overflows as emergencies and mobilizes all available and appropriate resources to deal with these events when all our preventive measures come up short. | SSO Basement Backup
11960 | 37092 | IN0025674 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-05-21 05:15 | 2013-05-21 05:50 | 2013-05-23 14:08 | 0 |  | 1438144214621464 Hudson 201 Troxel | Rain 0.5 inches Intense rain compounded by an overflow line from a CSO chamber which was found partially plugged with debris resulted in the basement back-ups at these locations. | Removed Blockage On 5.21 we cleaned the sewer main along Hudson and the overflow pipe from CSO chamber. We encountered debris in overflow pipe leaving CSO chamber during cleaning and full capacity was restored. Will evaluate if practical to add occasional inspection of overflow lines leaving CSO chamber to CSO inspections. | SSO Basement Backup
11960 | 38819 | IN0025674 Outfall 005 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-11-17 16:10 | 2013-11-17 16:50 | 2013-11-18 12:57 | 0 |  | 1531 Manor | Rain 1.3 inches Intense rain of 0.29 inches in 5 minutes. | See Report | SSO Basement Backup
11960 | 39503 | IN0025674 Outfall 035 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-09-30 10:15 | 2013-09-30 11:00 | 2013-09-30 17:36 | 0 |  | 2630 Roys Ave | Plugged sewer main | Blockage removed. See Report | SSO Basement Backup
11960 | 42401 | IN0025674 Outfall 035 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-12-09 18:41 | 2013-12-09 20:41 | 2013-11-11 17:08 | 0 |  | Jefferson St CSO 29 | See Report | Removed Blockage See Report | SSO Reached Receiving Water | Saint Joseph River
11960 | 42540 | IN0025674 Outfall 035 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-12-15 20:50 | 2013-12-15 22:30 | 2013-12-16 08:37 | 0 |  | 3220 Peoria | Basement Back-up | Removed Blockage See Report
11960 | 43036 | IN0025674 Outfall 035 | Elkhart Waste Water Treatment Plant | Elkhart | 2013-12-21 16:10 | 2013-12-21 18:45 | 2013-12-22 12:17 | 1870 | gallons | 1173 Willowdale | Call came in at 4:10pm on 12/22/13; crews immediately called about to evaluate and found blockage. Cleared the line of blockage back-up subsided. | See Reports | SSO Basement Backup
11960 | 38676 | IN0025674 - Terminated Permit | Elkhart Waste Water Treatment Plant | Elkhart | 2013-05-21 05:15 | 2013-05-21 05:50 | 2013-05-20 13:30 | 0 |  | 1438 1442 1462 1464 Hudson 201 Troxel | Rain 0.5 inches Overflow Line from CSO chamber. Intense rain compounded by and overflow line from a CSO chamber which was found partially plugged with debris resulted in the basement back-up at these locations. Responding to the call following extreme rainfall during the morning hours 5-21-13 staff found the flow in the main line flowing normal and so sign of any obstruction. As a precaution the main on Hudson was cleaned from the manhole upstream to the CSO chamber and the effluent and overflow line leaving to CSO chamber. During the cleaning of the overflow line debris was encountered and it was broken loose. It is suspected this debris restricted flow in the overflow line from the CSO chamber resulting in the back-up of the basements on Hudson.Residents of 1438 Hudson and 201 Troxel did not contact us until 5-22-13 | Removed Blockage. On 5/21 we cleaned the sewer main along hudson and the overflow pipe from CSO chamber. We encountered debris in overflow pipe leaving CSO chamber during cleaning and full capacity was restored. The City of Elkhart cleans sewers on a four-year rotation and catch basins annually. We also have a BMP program in the City of Elkhart with a three-week rotation interval during non-winter weather we also have a CSO inspector who checks out CSO s on a daily basis. Our lift station uses telemetry systems to provide accurate and timely information on potential mechanical or electrical problems that may lead to system overflows. The City also keeps critical spare parts inventory. Equipment is on a preventive maintenance program preformed by staff with multidisciplinary skills and experience in correcting problems. The City of Elkhart views bypasses of treatment or overflow as emergencies and mobilizes all available and appropriate resources to deal with these events when all our preventive measures come up short. | SSO Affected Private Property
12071 | 36126 | IN0025755 | Goshen Municipal Waste Water Treatment Plant | Elkhart | 2013-04-17 21:00 | 2013-04-17 22:00 | 2013-04-24 02:30 | 12 | gallons | Sewer Lateral Bath tub and basement floor | Untreated Release Rain 1.78 inches 100 North 9th Street sewer back-up caused sewer main overload by large rain event (1.78) | Customer used shop vacuum to clean up area during event and blocked off drain. Hired plumber to install check valve on floor drain also sewer main scheduled to be replaced with larger main. | SSO Basement Backup
12071 | 40228 | IN0025755 | Goshen Municipal Waste Water Treatment Plant | Elkhart | 2013-09-19 09:45 | 2013-09-19 09:55 | 2013-09-19 12:30 | 0 |  | Headworks Building Roof Vent at WWTP | #2 Grit Washer was not draining properly and noticed water leaving the roof drain downspout. | Remove Blockage See Report
30243 | 37168 | IN0036846 | BRISTOL MUNICIPAL WASTE WATER TREATMENT PLANT | Elkhart | 2013-04-13 | 2013-05-24 | 2013-05-24 12:19 | 0 |  | No flow to Bio-Tower (pump failure) bypassing Bio Tower. We have Pre-Treatment Primary settling tank secondary (activated sludge) final treatment (UV) on line and (2) final clarifier | Equipment Failure Bypass of Treatment Process. (South Bend Maintenance Dept) Underground pipe and valve has ordered parts and have tried to get pumps (2) to run. They will not prime (air Leak). The pumps will not pump to the top of the Bio-Tower. Discussed bypass with Jim Weingert Stacey Pfeffer and Don Daly. | Called underground pipe and valve on 5.14.2013 (Underground Maintenance Foreman) Rick Gilmer phone #574-532-1629. He tried to get Lift pumps to pump with no luck-advised that we order new parts or jumeriple pumps put in. having Underground Pipe and valve work on pumps-may need to be replaced. Meeting all IDEM Lab Test requirements. Meeting all NPDES Effluent limits. | SSO Reached Receiving Water | Saint Joseph River
30243 | 37142 | IN0036846 | BRISTOL MUNICIPAL WASTE WATER TREATMENT PLANT | Elkhart | 2013-04-13 |  | 2013-05-22 14:00 | 0 |  | No flow to Bio-Tower (pump failure) bypassing Bio Tower we have Pre Treatment primary settling tank secondary (Activated Sludge) Final Treatment (UV) on line and 2 final clarifiers. | Bypass of Treatment Process Equipment Failure (South Bend Maintance Dept) Underground pipe and valve has order parts and have tried to get pumps (2) to run. They will not prime (Air Leak). The pumps will not pump to the top of the Bio-Tower. Discussed bypass with Jim Weingert Stacey Pfeffer and Don Daly. | Called underground pipe and valve on 5/14/2013 (Underground Maintance Foreman) Rick Gilmer phone # (574) 532-1609. He tried to get Lift pumps to pump with no luck-advised that we order new parts or jumeriple pumps put in. Having Underground pipe and valve work on pumps - may need to be replaced. Meeting all IDEM Lab Test requirements. Meeting all NPDES effluent limits. | SSO Reached Receiving Water | Saint Joseph River
29632 | 42543 | IN0058025 | NEW PARIS CONSERVANCY DISTRICT | Elkhart | 2013-12-14 22:00 | 2013-12-14 23:00 | 2013-12-16 08:12 | 0 |  | 19412 CRT 146 Sanitary Sewer Overflow Basement Floor Drain | Equipment Failure A high voltage monitor failed for lift station A3 failed causing the pumps in the station not to start. At the same time the high wet well float got caught on piping in the station. This caused the station alarm not to notify operations personal of the problem. The owner notified us of the problem and the lift station was repaired and pumped down. It was estimated that less than 100 gallons of untreated wastewater was released. | See Report
667 | 34955 | IN0032336 | Connersville Waste Water Treatment Plant | Fayette | 2013-01-28 08:10 | 2013-01-28 09:00 | 2013-02-19 13:30 | 0 |  | 418 West 17th Street Connersville IN 47331 | Basement back up due to precipitation event. | Basement back-up. When system returned to normal the back-up drained out of the basement and into mainline sewer. Ran mainline sewer. Sewer separationq | SSO Basement Backup
667 | 44242 | IN0032336 Outfall 004 | Connersville Waste Water Treatment Plant | Fayette | 2013-12-22 | 2013-12-26 08:53 | 2014-01-10 16:36 | 0 |  | Water Street Lift Station | Equipment Failure Exceeded Max Capacity Rain 3.24 inches CSO 004 and Water Street lift station were under flooded conditions. The lift station was not operating. | See Report | SSO Reached Receiving Water | Whitewater River
3734 | 42209 | No NPDES Permit | EVERTON WATER CORPORATION | Fayette | 2013-11-29 10:31 | 2013-11-29 10:31 | 2013-11-30 06:20 | 0 |  | 1901 E Little Bear Rd Connersville IN | Equipment Failure floats failed to activate all floats were checked on Nov 26 2013 system ok. the area affected from the spill was wet most of the water soak into the ground. | Repaired Pump Station See Report
12628 | 35896 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-01-13 17:04 | 2013-01-13 20:47 | 2013-01-18 09:31 | 22300 | gallons | Basin 9-4 Manhole 9-48 Receiving water: Valley View Creek | Precipitation event triggered untreated release from basin and manhole to receiving waters. | This line is at the edge of a local golf course and creek. We will need drier conditions to CCTV and clean. We will schedule to have this investigated by 4/1/13 if weather permits. | SSO Reached Receiving Water
12628 | 35894 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-01-13 17:04 | 2013-01-13 20:47 | 2013-01-18 09:31 | 446 | gallons | Basin 9-4 Manhole 9-47A receiving water. Valley View Creek | Precipitation event triggered untreated release from basin and manhole to receiving water. | This line is at the edge of a local golf course and creek. We will need drier conditions to CCTV and clean. We will schedule to have this investigated by 4/1/13 if weather permits. | SSO Reached Receiving Water
12628 | 35886 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-01-13 18:00 | 2013-01-13 20:34 | 2013-01-18 09:31 | 15400 | gallons | Basin 13-5 manhole 13-C47 | Precipitation event triggered and untreated release from manhole and basin to receiving waters | Sewer lining is taking place in several basins up stream of Basin #13 over the next 2-3 years. It is estimatied that these projects will eliminate the overflows at this locations. | SSO Reached Receiving Water | Falling Run
12628 | 34966 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-02-06 14:00 | 2013-02-06 21:00 | 2013-02-07 09:15 | 0 |  | Basin 19-4 and hillside on private property | A private root obstructed 8 sewer line resulted in an overflow condition of untreated wastewater. | Overflow ran into Basin 19-4 and into storm sewer. found the private line broken in hillside. Notified owner that they would need to contact a private construction firm to repair their line. | SSO Affected Private Property; Storm Sewer
12628 | 34817 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-02-28 | 2013-03-01 21:00 | 2013-03-04 15:30 | 400 | gallons | 317 East 10th Street New Albany IN | Service lateral to 317 East 10th St. was severed by an Indiana American Water main sometime in the last year to two years. Service lateral was overflowing onto the ground at 317 E. 10th | Called in emergency locates and had a contractor repair service lateral. | SSO Reached Public Land; Surface Soil
12628 | 37206 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-04-05 | 2013-04-05 14:00 | 2013-04-10 15:15 | 1000 | gallons | Manhole 96A 917 Woodside Dr. Bain 29-4 Ground | Untreated Release Equipment Failure Sanitary sewer was overflowing at manhole 96A. Flushed sewer with chisel nozzle and broke free. | Returned on the 8th and CCTVed and discovered a root mass. Remove mass with root cutter. Applied chemical root killer to tasks instruction in the preventative maintenance program. | SSO Affected Private Property
12628 | 35487 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-04-05 | 2013-04-05 14:00 | 2013-04-10 14:20 | 1000 | gallons | Manhole 96A 917 Woodside Dr. Basin 29-4 Ground | Untreated Release Equipment Failure Sanitary sewer was overflowing at manhole 96A. Flushed sewer with chisel nozzle and broke free. | Returned on the 8th and CCTVed discovered a root mass. Remove mass with root cutter. Applied chemical root to task instruction in the preventative maintenance program. | SSO Affected Private Property
12628 | 39149 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-06-26 18:50 | 2013-06-26 20:40 | 2013-06-28 14:00 | 0 |  | Manhole 13-C47 Basin 13-5 Ground | Manhole 13-C47 Basin 13-5 Ground | See Report | SSO Affected Private Property
12628 | 38743 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-06-26 18:50 | 2013-06-26 20:40 | 2013-06-28 14:00 | 1100 | gallons | Manhole 13-C47 Basin 13-5 | Untreated Release. Precipitation Event. | New Albany Wastewater Utility is in the process of lining sanitary sewers in Basins #15 #16 and #7 which are directly upstream of Basin #13. | SSO Reached Public Land
12628 | 38742 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-06-26 18:55 | 2013-06-26 20:40 | 2013-07-25 14:59 | 2625 | gallons | Manhole 13-C46 Basin 13-5 | Untreated Release. Precipitation 2.67 inches. | New Albany Wastewater Utility is in the process of lining sanitary sewers in Basins #15 #16 and #7 which are directly upstream of Basin 13. | SSO Reached Public Land
12628 | 39147 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-06-26 18:55 | 2013-06-26 20:40 | 2013-06-28 14:00 | 0 |  | Manhole 13-C46 Basin 13-5 Ground | Rain 2.67 inches | See Report | SSO Affected Private Property
12628 | 39856 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-07-22 16:00 | 2013-07-23 11:00 | 2013-08-29 08:51 | 0 |  | Manhole 9-C64 Basin 9-7 Ground | This overflow has apparently been occurring for some time. It was located in an isolated area on a heavily wooded hillside. | Unstopped blockage with Aquatech Truck and spread lime. There is an offset where the 8 line enters the manhole that could potentially plug up again. We will be taking bids to repair this situation and have it completed ASAP. | SSO Affected Private Property
12628 | 39470 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-07-22 16:00 | 2013-07-23 11:00 | 2013-07-23 15:40 | 0 |  | Manhole 9-C64 Basin 9-7 Ground | Equipment Failure This overflow has apparently been occurring for some time. It was located in an isolated area on a heavily wooded hillside. | See Report | SSO Affected Private Property
12628 | 45923 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-05 22:22 | 2013-10-06 | 2013-10-09 16:00 | 3660 | gallons | Manhole 14-55 Basin 14-6 | Rain 4.87 inches | See Report | SSO Reached Receiving Water | Falling Run
12628 | 41022 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-05 22:22 | 2013-10-06 09:06 | 2013-10-09 16:00 | 0 |  | Manhole 14-55 Basin 14-6 | Rain 4.87 | Currently in the process of relining basin upstream and adjacent to this location. | SSO Reached Receiving Water | Falling Run
12628 | 45920 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 | 2013-10-06 02:06 | 2013-10-09 16:00 | 2448 | gallons | Manhole 13-58 Basin 13-4 | See Report | See Report | SSO Affected Private Property
12628 | 45921 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:03 | 2013-10-06 10:45 | 2013-10-09 16:00 | 11665 | gallons | Manhole 13-58 Basin 13-4 | Rain 4.87 inches | See Report | SSO Affected Private Property
12628 | 41028 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:03 | 2013-10-06 10:45 | 2013-10-09 16:01 | 0 |  | Manhole 13-58 Basin 13-4 Storm Sewer | Rain 4.87 inches | Currently in the process of relining basin upstream and adjacent to this location.
12628 | 41036 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:20 | 2013-10-06 10:57 | 2013-10-09 16:01 | 0 |  | Manhole 14-62 Basin 14-6 | Rain 4.87 inches | Currently in the process of relining basin upstream and adjacent to this location. | SSO Reached Receiving Water | Falling Run
12628 | 45922 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:20 | 2013-10-06 10:57 | 2013-10-09 16:00 | 58653 | gallons | Manhole 14-62 Basin 14-6 | See Report | See Report | SSO Reached Receiving Water | Falling Run
12628 | 41034 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:20 | 2013-10-06 10:57 | 2013-10-09 16:01 | 0 |  | Manhole 13-58A Basin 13-4 Storm Sewer | Rain 4.87 inches | Currently in the process of relining basin upstream and adjacent to this location.
12628 | 45913 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:20 | 2013-10-06 10:57 | 2013-10-09 16:00 | 9165 | gallons | Manhole 13-58A Basin 13-4 | Rain 4.87 inches | See Report | SSO Affected Private Property
12628 | 45919 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:20 | 2013-10-06 10:57 | 2013-10-09 16:00 | 9165 | gallons | Manhole 13-58A Basin 13-4 | Rain 4.87 inches | See Report | SSO Affected Private Property
12628 | 41020 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 08:44 | 2013-10-06 02:05 | 2013-10-09 16:00 | 0 |  | Manhole 13-58 Basin 13-4 Storm Sewer | Rain 4.87 inches | Currently in the process of relining basin upstream and adjacent to this location
12628 | 41027 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 09:49 | 2013-10-06 02:06 | 2013-10-09 16:01 | 0 |  | manhole 13-58 Basin 13-4 Storm Sewer | Rain 4.87 inches | Currently in the process of relining basin upstream and adjacent to this location.
12628 | 41030 | IN0023884 | New Albany Waste Water Treatment Plant | Floyd | 2013-10-06 10:07 | 2013-10-06 02:15 | 2013-10-09 16:01 | 0 |  | Manhole 13-58A Basin 13-4 Storm Sewer | Manhole 13-58A Basin 13-4 Storm Sewer | Currently in the process of relining basin upstream and adjacent to this location.
12628 | 43214 | IN0023884 Outfall 001 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 22:50 | 2013-12-22 01:53 | 2013-12-27 13:30 | 2745 | gallons | MH #13-108A9 Basin 13-1 | Exceeded Max Capacity Rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
12628 | 42037 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 08:25 | 2013-11-17 09:17 | 2013-11-19 14:49 | 0 |  | MH #16-83 Basin 16-1 McLean Lift Station | Rain 3.16 inches | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Silver Creek
12628 | 42038 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 08:45 | 2013-11-17 13:16 | 2013-11-19 14:49 | 0 |  | MH #13-108A9 Basin 13-1 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Falling Run
12628 | 42042 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 08:56 | 2013-11-17 13:18 | 2013-11-19 14:49 | 0 |  | MH #13-58 Basin 13-4 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Falling Run
12628 | 42043 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 08:58 | 2013-11-17 13:18 | 2013-11-19 14:49 | 0 |  | MH #13-58A Basin 13-4 | Rain 3.16 inches exceeded Max Capacity | See report | SSO Reached Public Land; SSO Reached Receiving Water | Falling Run
12628 | 42061 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 09:30 |  | 2013-11-19 14:49 | 0 |  | 1212 Beechwood | Rain 3.16 Exceeded Max Capacity | See Report | SSO Basement Backup
12628 | 42057 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 10:00 |  | 2013-11-19 14:49 | 0 |  | 703 Navajo | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Basement Backup
12628 | 42066 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 10:22 | 2013-11-17 11:22 | 2013-11-19 14:49 | 0 |  | MH #12-29A Basin 12-2 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Public Land
12628 | 42063 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 10:52 | 2013-11-17 13:19 | 2013-11-19 14:49 | 0 |  | MH #13-47 Basin 13-5 | Rain 3.16 inches Exceeded Max Capacity | See Report |  | Falling Run
12628 | 42040 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 11:10 | 2013-11-17 13:26 | 2013-11-19 14:49 | 0 |  | MH #14-62 Basin 14-6 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Falling Run
12628 | 42035 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 18:30 |  | 2013-11-19 14:49 | 0 |  | 201 Ealy St | Rain 3.16 inchesExceeded Max Capacity Collection system surcharged due to rain. | New Albany is currently in the process of CIPP the Sanitary System | SSO Basement Backup
12628 | 43224 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 22:15 | 2013-12-22 03:00 | 2013-12-27 13:30 | 32925 | gallons | MH #16-38 Basin 16-7 | Exceeded Max Capacity Rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
12628 | 42036 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 08:25 | 2013-11-17 09:17 | 2013-11-19 14:49 | 0 |  | MH #16-83 Basin 16-1 Mclean Lift Station | Rain 3.16 inches | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Silver Creek
12628 | 42055 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 08:35 | 2013-11-17 13:45 | 2013-11-19 14:49 | 0 |  | MH #16-31 Basin 16-6 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Silver Creek
12628 | 42065 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 08:55 | 2013-11-17 13:18 | 2013-11-19 14:49 | 0 |  | MH #13-57A Basin 13-4 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Falling Run
12628 | 42045 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 09:35 | 2013-11-17 13:22 | 2013-11-19 14:49 | 0 |  | MH# 14-101 Basin 14-5 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Falling Run
12628 | 42058 | IN0023884 Outfall 007 & 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 12:00 |  | 2013-11-19 14:49 | 0 |  | 308 Pimnlico | Rain 3.16 inches Exceeded Max Capacity Collection system surcharged due to rain. | See Report | SSO Basement Backup
12628 | 42059 | IN0023884 Outfall 007& 100 | New Albany Waste Water Treatment Plant | Floyd | 2013-11-17 10:15 | 2013-11-17 13:33 | 2013-11-19 14:49 | 0 |  | MH #22C-2 basin 22-1 | Rain 3.16 inches Exceeded Max Capacity | See Report | SSO Reached Receiving Water | Falling Run
12628 | 43222 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 22:40 | 2013-12-22 03:22 | 2013-12-21 13:30 | 15362 | gallons | MH #16-31 Basin 16-6 | Exceeded Max Capacity Rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
12628 | 43197 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 22:58 | 2013-12-22 03:04 | 2013-12-27 13:30 | 17850 | gallons | MH #13 58 Basin 13-4 | Exceeded Max Capacity Rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Receiving Water
12628 | 43201 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 22:59 | 2013-12-22 03:04 | 2013-12-27 13:30 | 54000 | gallons | MH #13 58A Basin 13-4 | Exceeded Max Capacity Rain 2.90 inches collection system surcharged due to rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
12628 | 43193 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 23:05 | 2013-12-22 03:11 | 2013-12-27 13:30 | 5820 | gallons | MH #13-47 Basin 13-5 | Rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land
12628 | 43195 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 23:15 | 2013-12-22 03:15 | 2013-12-27 13:30 | 66500 | gallons | MH #13-C47 Basin 13-5 | Exceeded Max Capacity Rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land
12628 | 43216 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-22 | 2013-12-22 03:07 | 2013-12-27 13:30 | 39350 | gallons | MH #14-62 Basin 14-6 | Exceeded Max Capacity rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
12628 | 43219 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-22 | 2013-12-22 01:32 | 2013-12-27 13:30 | 2670 | gallons | MH #14-101 Basin 14-5 | Exceeded Max Capacity Rain 2.90 inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
12628 | 43192 | IN0023884 Outfall 100 & 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-22 22:15 | 2013-12-22 03:00 | 2013-12-27 13:30 | 330 | gallons | MH #12-29a Basin 12-2 | Rain 2.90 inches collection system surcharged due to rain. | See Report | SSO Reached Public Land
12628 | 43196 | IN0023884 Outfall 100& 007 | New Albany Waste Water Treatment Plant | Floyd | 2013-12-21 23:00 | 2013-12-22 03:04 | 2013-12-27 13:30 | 0 |  | MH #13-57A Basin 13-4 | Exceeded Max Capacity Rain 2.90: inches Collection system surcharged due to rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
34765 | 41118 | IN0043923 Overflow went to drainage ditch near lift station name not provided. | WYMBERLY SANITARY WORKS INCORPORATED | Floyd | 2013-10-09 09:12 | 2013-10-09 09:20 | 2013-10-10 11:21 | 0 |  | Forest Springs lift Station | A electrical feed irregularity likely the loss of a phase would not allow the pumps to operate. | See Report | SSO Affected Private Property
105663 | 35368 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-03-06 | 2013-03-06 | 2013-03-03 13:18 | 200 | gallons | Lift Station 1043 Bradstone Ct edge of station | Power Failure Lift station 1043 Bradstone during strong wind limb fell from tree landing on handle to transfer switch box causing power to go out to lift station. | Restored power spread of lime dust over infected area. | SSO Affected Private Property
105663 | 34910 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-03-18 | 2013-03-18 | 2013-03-19 13:03 | 300 | gallons | Manhole drainage ditch located at 9488 St | Rainfall 2.50 inches large amounts of flow coming in had hard time keeping up. | Station caught up with flow spread of lime dust over in affected area. | SSO Affected Private Property
105663 | 35169 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-03-19 | 2013-03-19 | 2013-03-28 15:47 | 10 | gallons | Around Lift Station at 1034 Bankston | Lift station Equipment Failure Capacitors went bad causing both pumps to shut down. | Had pumper truck monitor station until repairs were made spread lime dust round station. | SSO Affected Private Property
105663 | 38907 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-06-26 18:30 | 2013-06-26 18:45 | 2013-06-27 11:00 | 0 |  | 1650 G-Town Lanesville Rd Manhole | 4 inches of rain in short amount of time. Station had hard time keeping up with flow. | See Report | SSO Affected Private Property
105663 | 38906 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-06-26 18:30 | 2013-06-26 18:45 | 2013-06-27 15:44 | 0 |  | 9485 St Rd 64 Manhole | Rain 4 inches. 4 in of rain in short amount of time station had hard time keeping up with flow both overflows on same line. | See Report | SSO Affected Private Property
105663 | 38239 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-07-02 12:00 | 2013-07-02 12:15 | 2013-07-02 12:38 | 0 |  | 1027 Brodstone Ct Lift Station | Equipment Failure Pump Station Failure Pumps tripped causing ovrflow. | Had pump truck vac sewer water from location spread lime dust over infected area. Next week lift station is to be remodified. | SSO Affected Private Property
105663 | 39468 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-07-22 02:00 | 2013-07-22 02:18 | 2013-07-23 14:01 | 0 |  | 9420 St Rd 64 | Rain 3 inches Lift Station having issues keeping up with high flow coming in. | See Report
105663 | 41038 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-10-06 04:30 | 2013-10-06 05:45 | 2013-10-07 13:15 | 0 |  | Manhole - 9420 ST RD 64 | Rain 7.50 inches excessive precipitation | See Report | SSO Reached Receiving Water | George Creek
105663 | 41771 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-11-12 10:00 | 2013-11-12 10:30 | 2013-11-12 13:58 | 0 |  | Lift Station | Equipment Failure Pump Failure | See Report | SSO Affected Private Property
105663 | 41925 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-11-17 07:30 |  | 2013-11-18 09:46 | 0 |  | 9420 St Rd 64 | Excessive Precipitation | See Report | SSO Reached Public Land; SSO Reached Receiving Water
105663 | 41924 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-11-17 07:30 | 2013-11-17 07:30 | 2013-11-18 09:38 | 0 |  | manhole 9485 5th Rd 64 | Excessive Precipitation | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Georgetown Creek
105663 | 41942 | IN0063771 | Georgetown Water Reclamation Facility | Floyd | 2013-11-17 07:30 | 2013-11-17 07:45 | 2013-11-18 10:10 | 0 |  | 1650 G-Town Lanesville Rd Manhole | Rain 4.25 inches excessive precipitation | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Georgetown Creek
105663 | 34911 | IN063771 | Georgetown Water Reclamation Facility | Floyd | 2013-03-18 | 2013-03-18 | 2013-03-19 13:05 | 250 | gallons | Lift station Edge of station located at 1533 Pirtle | Rain 2.50 inches large amount of flow coming in had hard time keeping up. | Stations caught up with flow spread of lime dust over affected area. | SSO Affected Private Property
31158 | 36630 | IN0024716 | VEEDERSBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Fountain | 2013-04-18 16:24 | 2013-04-19 12:30 | 2013-04-20 13:47 | 10000 | gallons | Manhole #1765 Line break between manhole: #4600 & #4913 Ground Stream | Untreated Release Bypass of a Treatment Process Rain 5 inches. there has been 5 inches of rain from Monday through Friday morning. The ground is saturated collection system full from I&I. | Do testing and checking for I & I and correct. | SSO Affected Private Property
32877 | 36755 | IN0039390 | KINGMAN MUNICIPAL WASTE WATER TREATMENT PLANT | Fountain | 2013-04-18 15:00 |  | 2013-04-20 16:23 | 200000 | gallons | 2nd street lift station SSO #3 Vine Street Manhole (2) Treatment Plant Unnamed tributary to Mill Creek | Untreated Release Partially Treated Release Rain 3.9 inches. 2nd St Lift Station (SSO#3) overflow stopped as of 5:00pm 4-19-13 Manholes on Vine St - not overflowing as of 8:30am 4-19-13 Treatment Plant - Return to Full Treatment 3:30pm 4-20-13 | Check lift stations to confirm all pumps running. Per in progress - RCAP | SSO Reached Receiving Water | Mill Creek
32877 | 36301 | IN0039390 | KINGMAN MUNICIPAL WASTE WATER TREATMENT PLANT | Fountain | 2013-04-24 06:50 | 2013-04-24 12:55 | 2013-04-24 19:16 | 4000 | gallons | SSO #3 - 2nd Street Lift StationVine Street Manhole | Precipitation and lift station breaker trip resulted in untreated and partially treated release to receiving waters. | Reset breaker at Lift Station. OER in progress. | SSO Reached Receiving Water | Mill Creek
32877 | 39463 | IN0039390 | KINGMAN MUNICIPAL WASTE WATER TREATMENT PLANT | Fountain | 2013-07-22 07:30 | 2013-07-22 03:30 | 2013-07-22 04:00 | 0 |  | Treatment Plant | Dechlorination bypass at treatment plant - Partial treatment release | Per in progress | SSO Occurred at Treatment Plant | Mill Creek
32877 | 39460 | IN0039390 | KINGMAN MUNICIPAL WASTE WATER TREATMENT PLANT | Fountain | 2013-07-22 07:30 | 2013-07-22 10:30 | 2013-07-22 04:00 | 0 |  | 2nd street lift station | Manhole overflow at 2nd street lift station- untreated release | Per in process | SSO Reached Receiving Water | Mill Creek
32877 | 43038 | IN0039390 | KINGMAN MUNICIPAL WASTE WATER TREATMENT PLANT | Fountain | 2013-12-21 16:00 | 2013-12-22 08:00 | 2013-12-22 09:17 | 9600 | gallons | 2nd Street Lift Station | Rain 3.3 inches Manhole adjacent to Lift Station overflowing. | Confirmed both lift station pumps running. P.E.R in progress - OCRA | SSO Reached Receiving Water | Mill Creek
32877 | 37618 | IN0039390 Unnamed Tributary of Mill Creek | KINGMAN MUNICIPAL WASTE WATER TREATMENT PLANT | Fountain | 2013-06-01 07:00 | 2013-06-01 14:00 | 2013-06-01 16:52 | 0 |  | 2nd Street Lift Station Treatment Plant Unnamed Tributary of Mill Creek | Untreated Release Bypass of a Treatment Process Rain 1.9 inches Manhole upstream of 2nd Street Lift Station overflowing - 2000 gallon est. Dechlorination at WWTP being bypassed 60000 gallons est. | Lift Station check of pumps operating properly PER in progress. | SSO Reached Receiving Water
33008 | 35278 | IN0023973 | OLDENBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Franklin | 2013-03-24 | 2013-03-24 | 2013-03-30 22:28 | 2000 | gallons | Splitter Box Solids over passed splitter box wall because of clog in 4th line. No damage Solids that normally run through 4th pipe to clarifier clogged and solids breached walls of box. | Untreated Release Equipment Failure 4 line from Oxidation Ditch to clarifier clogged that nowhere else to go but on the ground. Cleaned on following Tuesday 3-26-13 | Unclogged line hand made a finer screen for intake. Hand made a finer screen for intake overflow event and not a Bypass. | SSO Affected Private Property
33008 | 42460 | IN0023973 | OLDENBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Franklin | 2013-12-14 11:30 | 2013-12-14 16:10 | 2013-12-14 16:30 | 0 |  | Overflow at Wetwell | A power pole was struck at about 11:00am and all power for Oldenburg had to be shut down for it to be fixed. This pole had all phases of electricity to it our generator did not fire up. Board mtg on 12-17-13 and we ll let someone look at it. | See Report | SSO Reached Receiving Water | Harvey Branch
34731 | 41614 | IN0037168 | BIG CEDAR MOBILE HOME PARK | Franklin | 2013-10-31 10:16 | 2013-10-31 10:17 | 2013-11-05 09:07 | 0 |  | Manhole on W side of road Ground | Rain 1.2 inches Blockage in the troughs of the manhole structure. | Plumber called to site and fixed problem. | SSO Affected Private Property
15848 | 35206 | IN0021661 | ROCHESTER WASTE WATER TREATMENT PLANT | Fulton | 2013-01-30 14:20 | 2013-01-30 15:11 | 2013-01-31 07:34 | 5 | gallons | Basement floor at 1601 Madison Avenue Rochester IN | Manhole invert downstream needs reparied. Floor of manhole allows solids to buid up. Untreated Release. Basement Backup | Manhole vacuumed to remove solids til repairs are completed. Repair manhole invert. | SSO Basement Backup; SSO Affected Private Property
15848 | 34776 | IN0021661 | ROCHESTER WASTE WATER TREATMENT PLANT | Fulton | 2013-03-17 15:08 | 2013-03-17 17:00 | 2013-03-18 20:06 | 1 | gallons | 530 East 15th St Basement | Untreated Release | Ran root cutter in sewer line only reason found was a grease build-up in line. Clean line more often. | SSO Basement Backup
15848 | 35557 | IN0021661 | ROCHESTER WASTE WATER TREATMENT PLANT | Fulton | 2013-04-07 16:20 | 2013-04-07 17:00 | 2013-04-08 07:41 | 5 | gallons | 1414 Court Street Basement | Untreated Release Construction Related | Line was plugged with grease between manhole #44 and #43. This was our first sewer call on this line will monitor situation. | SSO Basement Backup
15848 | 35491 | IN0021661 | ROCHESTER WASTE WATER TREATMENT PLANT | Fulton | 2013-04-10 12:00 | 2013-04-10 12:40 | 2013-04-10 12:56 | 100 | gallons | Plant Drying Beds Ground | Partially Treated Release We were cleaning drying beds and the liquid on top went over wall on the grass inside plant under the fence onto land application field. | We cleaned area with the vactor to stop the spread of the sludge. Told employees to be more careful | SSO Affected Private Property
15848 | 37622 | IN0021661 | ROCHESTER WASTE WATER TREATMENT PLANT | Fulton | 2013-06-01 04:00 | 2013-06-01 09:00 | 2013-06-01 12:14 | 5000 | gallons | City of Rochester WWTP | Precipitation event and lightning cause a failure of the Roto-Mat and resulted in plugging of the bar rack with debris. Influent overflowed to WWTP yard and ludge pits on clarifiers. | Cleaned yard and sidewalks. Pumped water back to head of plant. Reset Roto-Mat and cleaned Bar Rack. | SSO Occurred at Treatment Plant
19966 | 35813 | IN0031798 | CASTON EDUCATIONAL CENTER | Fulton | 2013-04-12 12:00 |  | 2013-04-15 21:03 | 0 |  | Treatment facility Clarifier Through Polishing Pond Bypass to Outfall 001 Neff Ditch | Bypass of a Treatment Process Construction Related On Friday April 12th the polishing pond of the wastewater treatment system serving the Caston Educational Center was taken out of service for cleaning. The pond has has issues with algae contaminating final effluent samples and causing erroneous final effluent Total suspended Solids (TSS) violations. During the bypass Copper Sulfate will be added to the pond in an effort to kill-or reduce significantly reduce the presence of algae. | There is no damage to mitigate. Secondary effluent samples collected the past few months have confirmed that water leaving the treatment facility clarifier is well below permit levels. Water from the clarifier then goes through Chlorine disinfection tablet feeders: to tablet treatment unit being bypassed as such water leaving the treatment facility is fully treated and blow permit limits. Once the polishing pond is free of algae the bypass will cease; IDEM will be notified; and the plant will return to normal operation. | SSO Occurred at Treatment Plant | Neff Ditch
33033 | 34576 | IN0021482 | HAUBSTADT SEWER DEPARTMENT | Gibson | 2013-03-02 | 2013-03-04 09:30 | 2013-03-04 10:34 | 2000 | gallons | Water Tower Place Lift Station Ground | Equipment Failure. This bypass was at a duplex lift station. One of the pumps had a failed starter and the other pump had a blown fuse. | Service techs were called immediately and upon arrival the station was fixed and resumed operation. As instructed by Keith Condra IDEM inspector lime was spread over the affected area. The Town will perform more frequent inspections of the station and also have an audio alarm installed in addition to the existing visual alarm. We also have a pump supply company coming this week to evaluate any conditions that could be improved such as different types of pumps and/or controls systems. | SSO Affected Private Property
33064 | 38264 | IN0021687 | OAKLAND CITY WATER & POLLUTION FACILITY | Gibson | 2013-07-01 08:00 | 2013-07-01 11:00 | 2013-07-01 13:48 | 0 |  | WWTP Effluent 13310 E St Rd 64 Shy Ditch | Rain 3.7 inches We received 3.7 inches of rain in about 1 hour. | None
34826 | 41443 | IN0021687 | OAKLAND CITY MUNICIPAL SEWAGE TREATMENT PLANT | Gibson | 2013-10-30 11:00 | 2013-10-30 12:15 | 2013-10-31 09:30 | 0 |  | Located behind the Dollar Store on Hwy 64 Oakland City In 47660 Lift Station Ground | Float got stuck under piping in lift station. | Change float position. Changing where floats now hang and putting them out away from piping. | SSO Affected Private Property
32662 | 35809 | IN0024392 | PRINCETON MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-01-12 16:45 | 2013-01-13 12:30 | 2013-01-13 13:32 | 26000 | gallons | Manhole between race & Seminary St.Manhole between Prince & Gibson St. | Precipitation event triggered untreated release from manholes to receiving waters | Working on I & I problems. boring and cleaning sewer line 12 interceptor. Seeking grant money for future I & I study on sewer problems. | SSO Reached Receiving Water | Richland Creek
32662 | 35212 | IN0024392 | PRINCETON MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-01-30 03:45 | 2013-01-30 12:30 | 2013-01-30 13:07 | 8000 | gallons | Manhole between Race & Seminary Streets Princeton IN | Precipitation event caused untreated release from manhole between Race & Seminary Streets Treatment bypass to Richland Creek | Working on I&I problems. Checked manholes 7 Sewer lines down stream of Seminary Street manhole. Boring and cleaning 12 interceptor. Smoking and TVing sewer lines for I&I. Seeking grant money for the future I&I study on sewer system. | SSO Reached Receiving Water | Richland Creek
32662 | 34888 | IN0024392 | PRINCETON MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-03-18 01:30 | 2013-03-18 22:00 | 2013-03-19 01:53 | 30000 | gallons | Manhole between Race & Seminary Street; on 12 main interceptor McCarty Lift station | Untreated Release Equipment Failure Rain 3.75 inches. Seminary hydraulically overload McCarty pump failure Basement flooded 310 W Pine St 420 N West St640 E State St. | Check for blockage of sewer lines down stream of Seminary St. Pulling pump for emergency repair. Smoke and TV sewer lines for I&I Bore and clean sewer lines. | SSO Reached Receiving Water | Richland Creek; McCarty Ditch
32662 | 34791 | IN0024392 | PRINCETON MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-03-18 01:30 | 2013-03-18 05:20 | 2013-03-18 10:41 | 0 |  | Manhole between Race and Seminary street on 12 main interceptor. McCarty Liftstation | Untreated Release Equipment Failure Rain 3.75 inches Seminary- hydraulically overload McCarty- pump failure Basement flooded 310 W Pine St 420 N West St 640 E State St | Check for blockage of sewer lines down stream of seminary St. Pulling pump for emergency repair. | SSO Reached Receiving Water | Richland Creek; McCarty Ditch
32662 | 42829 | IN0024392 Outfall 001 | PRINCETON MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-12-21 08:00 | 2013-12-21 08:00 | 2013-12-22 08:00 | 0 |  | Manholes Lift Station | Several manholes Pigeon Lift Station McCarty Lift Station Several Basement Backups. | Check for blockage of sewer lines down stream continue I&I removal program | SSO Basement Backup; SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek; McCarty Ditch
32662 | 42617 | IN0024392 Outfall 001 | PRINCETON MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-12-21 08:00 | 2013-12-31 08:00 | 2013-12-22 08:00 | 0 |  | Manholes Lift Stations | Rain 7 inches Several Manholes Pigeon Lift Station McCarty Lift Station Several Basement Backups. | See Report | SSO Basement Backup; SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek; McCarty Ditch
30913 | 35783 | IN0038288 | OWENSVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-01-12 19:00 | 2013-01-13 13:00 | 2013-01-14 14:14 | 150000 | gallons | Drain at Fire Station Hillcrest Lift Station manhole WWTP | Power failure precipitation event along with snow meltcombined to cause untreated release and bypass of treatment process. Waste went to surrounding ground and unnamed stream. | Dump of sewer at Hillcrest Lift Station to prevent flooding to basements. Power restored to Hillcrest L.S. | SSO Reached Public Land; SSO Reached Receiving Water
30913 | 34946 | IN0038288 | OWENSVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-03-18 02:00 | 2013-03-18 04:30 | 2013-03-18 14:15 | 10000 | gallons | Manhole 1st and Warrick St Ground and Storm Sewer | Untreated Release Rain 3.85 inches WWTP was already operating at designed flow before heavy rain. | None taken to much I&I Town is working on water improvements now money from SRF next project is to replace some sewer mains | Storm Sewer
30913 | 43041 | IN0038288 | OWENSVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-12-21 11:00 | 2013-12-21 11:09 | 2013-12-23 12:32 | 150000 | gallons | Hillcrest LS | Rain 7.0 inches 14 melting snow with 7.0 of heavy rain. Pumped from manholes at L/S to prevent backups into homes and to stop plant from flooding. | See Report | SSO Reached Receiving Water | Montgomery Ditch
30913 | 43039 | IN0038288 | OWENSVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Gibson | 2013-12-21 11:30 | 2013-12-22 02:00 | 2013-12-23 12:38 | 150000 | gallons | Hwy 168 L/S | Rain 7.0 inches 14 melting snow with 7.0 of heavy rain. pumped from manholes at LS to prevent backups into homes and to stop plant from flooding. | See Report | SSO Reached Receiving Water | Montgomery Ditch
| 42083 | Terminated Permit | Dollar Store | Gibson | 2013-11-20 12:00 | 2013-11-21 08:30 | 2013-11-21 13:10 | 0 |  | Lift Station | Equipment Failure | See Report | SSO Affected Private Property
24896 | 35480 |  | SWEETSER TOWN | Grant | 2013-01-11 06:00 | 2013-01-11 12:00 | 2013-01-16 07:32 | 300 | gallons | 807 Maple Court | Precipitation event along with snow melt and ground water leaking into sewage system combined to cause a residential basement backup | Back up due to problems at Eagle Drive Lift Station (Incident Report 35477). The town rented a 2 pump to help the homeowner pump out basement. Called in Stanley Steemer to do the clean up.Complete repairs at the Eagle Drive Lift Station and perform maintenance on the system. | SSO Basement Backup
24896 | 35477 |  | SWEETSER TOWN | Grant | 2013-01-11 10:00 | 2013-01-12 13:30 | 2013-01-15 04:21 | 31000 | gallons | Eagle Drive Lift Station | Precipitation event and debris lodged in pump #1 caused the pump to fail. While pulling pump #2 a 4 force main was broken resulting untreated release from the lift station. Release was discharged to private property. | Replaced blown capacitor on pump #1 and replaced damaged pump. Repairs are being made to force main. Discharged into field because we have no vac truck and needed to see the bottom of the pit to seat our pumps. Maintenance on system to determine cause of ground water leakage into system and make repairs. | SSO Affected Private Property
19846 | 35638 | IN0020559 | VAN BUREN MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-01-13 | 2013-01-14 | 2013-01-16 11:05 | 0 |  | manhole east of highway 5 beside Vectren gas valves. | Precipitation event along with snow melt resulted in untreated release from manhole to storm sewer. | Attempting to reduce infiltration | SSO Reached Public Land; Storm Sewer
19846 | 35407 | IN0020559 | VAN BUREN MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-10 19:30 | 2013-04-12 11:00 | 2013-04-12 10:03 | 0 |  | Manhole on 4th Street west of highway 5 by gas valve station. Van Buren IN | Precipitation event triggered an overflow from a manhole to storm sewer. | Try to reduce I & I. | SSO Reached Public Land; Storm Sewer
19846 | 36436 | IN0020559 | VAN BUREN MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-18 20:30 | 2013-04-19 19:30 | 2013-04-22 14:02 | 0 |  | Manhole on 400 N west of highway 5 by Vectron Gas Valves Storm Sewer | Rain 4.25 inches | Try to reduce our I&I | Storm Sewer
19846 | 36614 | IN0020559 | VAN BUREN MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-24 08:00 | 2013-04-24 15:00 | 2013-04-25 11:54 | 0 |  | Manhole on 400N West of Highway 5 by Vectren gas valves. | Flow from precipitation event(s) triggered untreated release from manhole to storm sewer. | Try to reduce i & I. | SSO Reached Public Land; Storm Sewer
20175 | 36488 | IN0021105 | FAIRMOUNT MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-19 02:00 | 2013-04-19 14:30 | 2013-04-19 15:00 | 0 |  | Fairmount WWTP | Precipitation event(s) resulted in local flooding putting influent structure under water and creek flooding coming in old outfall into chlorine tank. Creek water around lab building. All streets in town flooded. Treatment Plant bypass untreated release partially treated release. | slowed flow into WWTP as not to wash solids out of plant. | SSO Occurred at Treatment Plant | Back Creek
20175 | 39906 | IN0021105 6.56 Raw from 4-10 to 4-20-13 | FAIRMOUNT MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-19 04:00 | 2013-04-19 02:00 | 2013-04-19 12:30 | 0 |  | 200 W 8th St Fairmont WWTP | Rain 3.1 inches. 4:00 hrs on 4-19 we were called out because of complaints of street flooding and residents were not able to flush toilets. The influent structure at the WWTP was under water. We shut off the sluice gate and lift only 1 raw sewage pump to run. Creek was overflowing into plant parking area and was also flooding into the chlorine contact tank. | Kept 1 raw pump running as not to wash solids from plant. As soon as water reseeded from influent structure we started flow into WWTP. | SSO Reached Receiving Water | Back Creek
11987 | 35924 | IN0025585 | Raymond H Strickland Waste Water Treatment Plant | Grant | 2013-04-10 21:30 | 2013-04-10 22:00 | 2013-04-16 14:33 | 3000 | gallons | 809 Briarwood Ln MH#17-2209 Street/Storm Sewer | Untreated Release Rain 4 inches. Surcharge out of manhole was originally reported as a storm sewer. After review of the maintenance logs it was discovered that this was actually a combined sewer. | Area was checked-there was no debris. Continue to look for sources of inflow and infiltration and possible restrictions in sewer. | SSO Affected Private Property; Storm Sewer
11987 | 36506 | IN0025585 | Raymond H Strickland Waste Water Treatment Plant | Grant | 2013-04-18 19:30 | 2013-04-19 13:00 | 2013-04-19 16:47 | 10000 | gallons | Stone Road MH 67-2628403 West 4th STreet MH 25-1658 | High flow caused by precipitation event resulted in overflow from manholes and mixing with storm water. Untreated release reached the street storm sewer and farm field. | Area was checked and cleaned. Sewers will be inspected to make sure all are free of restrictions and operating properly. | SSO Affected Private Property; Paved Surface; Storm Sewer
11987 | 37608 | IN0025585 | Raymond H Strickland Waste Water Treatment Plant | Grant | 2013-06-13 01:00 | 2013-06-13 02:00 | 2013-06-13 11:30 | 7000 | gallons | Manhole #36-2273 & 22950 | Rain 3.0 inches Manhole | The system relieved itself as rain slowed. Area was cleaned up. No problems were found with the sewers. It is believed that the installation of Tideflex Red Valves at the Home Avenue overflow (CSO #009) may be causing a restriction and not allowing the system to relieve itself fast enough causing the combined sewer to back up. | SSO Affected Private Property
13912 | 35941 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-01-11 05:45 | 2013-01-11 08:15 | 2013-01-11 16:55 | 300 | gallons | North Lift Station | Precipitation event plus snow melt triggered an untreated release from the lift station to receiving waters |  | SSO Reached Receiving Water | Swartz Ditch
13912 | 35504 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-01-11 23:30 | 2013-01-12 04:30 | 2013-01-14 03:05 | 600 | gallons | North Lift Station | Precipitation events along with snow melt exceede the capacity of a lift station resulting in an untreated release from the Lift Station to receiving waters. | No action taken | SSO Reached Receiving Water | Swartz Ditch
13912 | 35597 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-04-10 22:00 | 2013-04-11 08:00 | 2013-04-11 10:14 | 1200 | gallons | North Lift Station Schwartz Ditch | Untreated Release rain 3.0 inches |  | SSO Reached Receiving Water
13912 | 35582 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-04-11 03:00 | 2013-04-11 08:00 | 2013-04-11 10:14 | 600 | gallons | West Lift Station Jefferson Ditch | Untreated Release rain 3.0 inches Bypass of a Treatment Process |  | SSO Reached Receiving Water | Jefferson Ditch
13912 | 36470 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-04-19 04:30 | 2013-04-19 06:00 | 2013-04-19 14:22 | 410 | gallons | North Lift Station and West Lift Station. | Flow from precipitation event exceeded the capacity of lift stations resulting untreated release to receiving waters. | No action taken. Overflow lasted only 100 minutes. | SSO Reached Receiving Water | Jefferson Ditch; Swartz Ditch
13912 | 37847 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-06-13 02:00 | 2013-06-13 05:00 | 2013-06-13 11:09 | 360 | gallons | North Lift Station Schwartz Ditch | Rain 2.7 inches |  | SSO Reached Receiving Water
13912 | 37854 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-06-13 02:00 | 2013-06-13 04:00 | 2013-06-13 11:09 | 240 | gallons | West Lift Station Jefferson Ditch | Rain 2.7 inches |  | SSO Reached Receiving Water | Jefferson Ditch
13912 | 37855 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-06-13 05:00 | 2013-06-13 07:30 | 2013-06-13 11:09 | 300 | gallons | Plant site manhole Jefferson Ditch | Rain 2.7 inches |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Jefferson Ditch
13912 | 38251 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-06-30 07:30 | 2013-06-30 09:30 | 2013-07-02 09:42 | 0 |  | North Lift Station | Rain 2.25 inches | None | SSO Reached Receiving Water
13912 | 39540 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-07-10 14:30 | 2013-07-10 18:30 | 2013-07-10 23:04 | 0 |  | North Lift Station | Rain 1.2 inches 1.1 of rain in less than a hour |  | SSO Reached Receiving Water
13912 | 40061 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-09-09 20:00 | 2013-09-10 07:00 | 2013-09-10 14:18 | 0 |  | Manhole at plant site | Pump Station Failure | Repaired Pump Station | SSO Reached Receiving Water | Jefferson Ditch
13912 | 43044 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-12-21 11:15 | 2013-12-23 10:15 | 2013-12-24 | 0 |  | West Lift Station | Equipment Failure Rain 2.9 Snow Melting | Repaired Pump Station | SSO Reached Receiving Water | Jefferson Ditch
13912 | 43045 | IN0036978 | Upland Municipal Waste Water Treatment Plant | Grant | 2013-12-21 21:00 | 2013-12-22 12:00 | 2013-12-24 09:48 | 0 |  | North Lift Station | Rain 2.9 inches snow melting |  |  | Schwartz Ditch
23543 | 36027 | IN0037001 | SWAYZEE WASTE WATER TREATMENT PLANT | Grant | 2013-04-11 06:00 | 2013-04-11 09:00 | 2013-04-17 16:29 | 2700 | gallons | Outfall 002 Main Lift Station WWTP | Precipitation event triggered an untreated release from WWTP lift station to receiving waters. | Both pumps running at full capacity. Personnel on site to visually monitor the bypass pipe. Turned air off at WWTP so lift station at WWTP could pump at full capacity.Continue to search for source of I & I. Continue to water proof manholes using a company that specializes in manhole rehab. Smoke test - visually inspect manholes. | SSO Reached Receiving Water | Taylor Creek
23543 | 36527 | IN0037001 | SWAYZEE WASTE WATER TREATMENT PLANT | Grant | 2013-04-19 03:30 | 2013-04-19 12:30 | 2013-04-20 07:43 | 16000 | gallons | Outfall 002 at Main Plant Lift Station | Precipitation event exceed pumping capacity of lift station resulting in untreated release to receiving water. | All pumps running at full capacity.Personnel on sit at facility to visually monitor bypass pipe.Turned air off at WWTP so lift station can pump at full capacity.Continue to search for and eliminate sources of I & I.Continue to water proof manholes and perform smoke tests.Visually inspect manholes. | SSO Reached Receiving Water | Taylor Creek
15858 | 35851 | IN0042994 - Terminated | JONESBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-01-14 01:15 | 2013-01-14 11:45 | 2013-01-15 11:15 | 950000 | gallons | Manholes I-1 I-3 I-11 I-18 I-19 | Precipitation event snow melt and flooding resulted in non permitted and untreated release to ground and receiving waters | Cleaned in and around manholes spread lime in affected areas. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Back Creek
15858 | 36340 | IN0042994 - Terminated | JONESBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-18 18:30 | 2013-04-19 18:15 | 2013-04-22 09:29 | 2000000 | gallons | Manholes: C-1 C-8 I-1 I-3 I-11 I-18 I-19 D-37A | Precipitation event created an unpermitted untreated release from multiple locations to surrounding ground and unnamed flooding creek. | Cleaned manholes and spread lime on affected areas.Town of Jonesboro normally sends waste water to Gas City for treatment. | SSO Reached Public Land; SSO Reached Receiving Water
15858 | 36334 | IN0042994 - Terminated | JONESBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-18 18:30 | 2013-04-19 18:15 | 2013-04-22 09:29 | 2000000 | gallons | Manholes: C-1 I-1 I-3 I-11 I-18 I-19 D-37A C-8 | Precipitation event caused non permitted untreated release from multiple locations to surrounding ground and unnamed flooded creek. | Cleaned manholes spread lime. Wastewater normally sent to Gas City WWTP. | SSO Reached Public Land; SSO Reached Receiving Water
15858 | 36615 | IN0042994 - Terminated | JONESBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Grant | 2013-04-24 04:15 | 2013-04-24 19:30 | 2013-04-25 11:39 | 450000 | gallons | Manholes: I-11 I-8 I-13 | Flows from precipitation event(s) caused untreated release from multiple manholes to surrounding ground and receiving water. | Cleaned manholes spread lime on and around affected areasl | SSO Reached Public Land; SSO Reached Receiving Water | Back Creek
24896 | 38485 | IN0064165 | SWEETSER WASTE WATER TREATMENT PLANT | Grant | 2013-07-18 08:00 |  | 2013-06-13 09:24 | 0 |  | Kelly Dr. Lift Station | Rain 4 inches.. Infiltration into sanitary line. 4 inches of rain overnight. Lift Station overflowed due to rain. | Working on repairing bad lines. Repair bad line and reduce infiltration. | SSO Reached Public Land; SSO Reached Receiving Water | Pipe Creek
15858 | 35361 | No active permit | JONESBORO MUNICIPAL WASTEWATER TREATMENT PLANT | Grant | 2013-04-11 09:00 | 2013-04-12 10:00 | 2013-04-15 09:45 | 1500000 | gallons | I-1 I-3 I-11 I-18 & I-19 | Untreated Release - Precipitation 4.25 Inches. Excessive amount of rainfall within 24 hour period. | Wastewater sent to Gas City for treatment. Cleaned manholes and affected areas - spread lime. | SSO Reached Public Land; SSO Reached Receiving Water
24896 | 37697 | No- Permit | SWEETSER WASTE WATER TREATMENT PLANT | Grant | 2013-06-13 08:00 |  | 2013-06-13 09:32 | 0 |  | Kelly Dr Lift Station | Rain 4 inches. Infiltration into sanitary line 4 inches of rain overnight. | Working on repairing bad lines repair bad line and reduce infiltration. | SSO Reached Public Land; SSO Reached Receiving Water | Pipe Creek
| 43054 |  |  | Greene | 2013-12-24 |  | 2014-01-22 08:54 | 0 |  | Final Effluent Lagoon | Rain 5 inches just bring to your attention that Eel River has exceeded it s banks due to excessive rains (5 0 and has entered the final treatment lagoon of the wastewater system. | See Report | SSO Occurred at Treatment Plant | Eel River
20048 | 36025 | IN0020575 | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-04-17 06:00 |  | 2013-04-17 14:30 | 0 |  | WWTP manhole | Precipitation event caused untreated release and treatment bypass at WWTP to receiving waters. Plant manhole under water. |  | SSO Reached Receiving Water | Beehunter Ditch
20048 | 36131 | IN0020575 | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-04-19 07:00 | 2013-04-19 13:00 | 2013-04-19 13:11 | 0 |  | City of Linton WWTP | Precipitation event caused untreated release and treatment plant bypass to receiving waters. |  | SSO Reached Receiving Water | Beehunter Ditch
20048 | 36124 | IN0020575 | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-04-24 07:00 | 2013-04-24 12:30 | 2013-04-24 02:17 | 0 |  | At plant manhole Beehunt Ditch | Untreated Release Bypass of a Treatment process Rain 1.7 inches. |  | SSO Reached Receiving Water | Beehunter Ditch
20048 | 37515 | IN0020575 | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-05-31 07:30 | 2013-05-31 10:30 | 2013-05-31 13:01 | 0 |  | Manhole at WWTP | Precipitation event exceeded plant capacity resulting in a treatment bypass to receiving waterl | Pictures taken. Can submit them via email if needed. | SSO Reached Receiving Water | Beehunter Ditch
20048 | 39456 | IN0020575 | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-07-20 17:00 | 2013-07-21 11:00 | 2013-07-22 07:22 | 0 |  | At plant numerous manholes around town | 5.2 inches of rain fell within 2 hours. |  | SSO Reached Receiving Water | Beehunter Ditch
20048 | 39589 | IN0020575 | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-07-20 17:00 | 2013-07-21 11:00 | 2013-07-20 04:30 | 0 |  | At Plant/ Numerous manholes | 5.2 inch of rain fell within 2 hours |  | SSO Reached Receiving Water | Beehunter Ditch
20048 | 41583 | IN0020575 | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-10-31 15:00 | 2013-11-01 07:00 | 2013-11-01 14:27 | 0 |  | Manhole at Plant | Rain 3.25 inches. |  | SSO Reached Receiving Water | Beehunter Ditch
20048 | 39078 | IN0020575 Brehurster Ditch | LINTON MUNICIPAL WASTE WATER TREATMENT PLANT | Greene | 2013-06-26 19:30 | 2013-06-27 21:15 | 2013-06-27 09:00 | 0 |  | Plant Manhole | Rain 5.25 inches |  | SSO Reached Receiving Water
25826 | 35113 | IN0109606 | SWIFT & COMPANY | Greene | 2013-01-22 12:00 | 2013-01-28 15:00 | 2013-01-31 07:42 | 0 |  | Corn Flour Producers LLC Worthingto IN | Extreme precipitation event caused the Eel River receiving water to overflow berm and infiltrate the 2nd tertiary treatment pond. approximately 1000 fish killed. | No actions taken. Not a preventable event. Fish kill was discovered when waters finally receded on 1/29/13. | Fish Kill; SSO Reached Receiving Water | Eel River
25826 | 36359 | IN0109606 | SWIFT & COMPANY | Greene | 2013-04-22 07:00 |  | 2013-04-22 13:52 | 0 |  | Lagoon Ground | Blended with Final Effluent & Sampled Rain 9 inches Upset condition. River flooded into final lagoon. Act of nature
25826 | 39685 | IN0109606 | SWIFT & COMPANY | Greene | 2013-07-03 08:00 | 2013-08-02 14:00 | 2013-08-02 14:26 | 0 |  | Overflow Pit/ North side of western tertiary | Since we have accumulated too much rain we have to lower the level of our final tertiary pond. Water is testing good we will test. We are estimating to bypass 1.3 MGD by lowering 1 foot in our pond by the end of today or maybe less. | See Report | SSO Reached Receiving Water
25826 | 39376 | IN0109606 | SWIFT & COMPANY | Greene | 2013-07-31 08:00 | 2013-08-02 14:00 | 2013-07-31 10:00 | 0 |  | Overflow Pit/ North side of western tertiary | Rain 5 inches Since we have accumulated too much rain we have to lower the level of our final tertiary pond. Water is testing good. We are estimating to bypass 1.million gallons by lowering one foot in our pond by the end of today maybe less. | See Report | SSO Reached Receiving Water | Eel River
25826 | 39656 | IN0109606 | SWIFT & COMPANY | Greene | 2013-07-31 08:00 |  | 2013-08-26 09:12 | 0 |  | Overflow Pit/ North side of Western Teritary | Rain 5 inches Since we have accumulated to much rain we have to lower the level of our final tertiary pond. We are estimating to bypass 1.3 MGD by lowering 1 foot in our pond by the end of today or maybe less. | See Report | SSO Reached Receiving Water | Eel River
25826 | 39329 | IN0109606 | SWIFT & COMPANY | Greene | 2013-07-31 08:00 | 2013-08-02 14:00 | 2013-07-31 13:49 | 0 |  | Overflow Pit/ North side of western tertiary. | Rain 5 inches Since we have accumulated too much rain we have to lower the level of our final tertiary pond. Water is testing good we will test. We are estimating to bypass 1.3 MGD buy lowering 1 foot in our pond by the end of today cr maybe less. | See Reports | SSO Reached Receiving Water | Eel River
25826 | 39315 | IN0109606 | SWIFT & COMPANY | Greene | 2013-07-31 08:00 | 2013-08-02 14:00 | 2013-08-14 10:17 | 0 |  | Overflow Pit/North side of western tertiary | Rain 5 inches Since we have accumulated too much rain we ha to lower the level of our final tertiary pond. Water is testing good we will test. We are estimating to bypass 1.3MGD by lowering 1 foot in our pond by the end of today or maybe less. | See Report | SSO Reached Receiving Water
25826 | 39377 | IN0109606 | SWIFT & COMPANY | Greene | 2013-08-02 08:00 | 2013-08-02 14:00 | 2013-08-16 10:05 | 0 |  | Overflow Pit/north side of western tertiary | Rain 5 inches Since we have accumulated too much rain we have to lower the level of our final tertiary pond. Water is testing good. We are estimating to bypass 1.3 million gallons by lowering one foot in our pond by the end of today maybe less. | See Report | SSO Reached Receiving Water | Eel River
25826 | 43062 | IN0109606 Outfall 001 | SWIFT & COMPANY | Greene | 2013-12-24 |  | 2013-12-24 10:15 | 0 |  | Final effluent lagoon | Rain 5 inches Just bringing to your attention that Eeel River has exceeded it s banks due to excessive rains(5 ) and has entered the final treatment lagoon of the wastewater system. | See Report | SSO Occurred at Treatment Plant | Eel River
25826 | 43064 | IN0109606 Outfall 001 | SWIFT & COMPANY | Greene | 2013-12-26 | 2013-12-27 | 2013-12-30 10:55 | 0 |  | Eel River overflow | Eel River overflowed it s banks and entered the final effluent lagoon of CFPLLC wastewater plant. The water entered the final lagoon in the early morning hours of 12/26/13 and by the early morning hours of 12/27/13 the Eel river had subsided and was no longer in the final effluent lagoon. The water quality in the final effluent lagoon was of good quality. | See Report | SSO Occurred at Treatment Plant | Eel River
13756 | 34959 | IN0020168 | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-01-12 00:51 | 2013-01-13 12:30 | 2013-01-13 12:00 | 0 |  | Lift Station #1 and Lift Station #5 at 15545 Allisonville Road and 406 West Chester Boulevard respectively in Noblesville IN 46060 | Heavy rain event caused flow into the lift stations beyond peak pump capacity. Resulting in untreated release. | Samples were taken at the site and the results of the lab tests will be sent in a follow up report to IDEM | SSO Reached Receiving Water | White River
13756 | 36730 | IN0020168 | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-04-18 20:15 | 2013-04-19 09:00 | 2013-04-30 15:03 | 0 |  | Lift Station #5406 West Chester BoulevardLift Station #115545 Allisonville RoadLift Station #87208 Lands End Circle | Flow caused by precipitation event(s) exceeded pumping capacity of multiple lift stations resulting in untreated release from the lift stations to receiving water. | Samples were taken at the site and the results of the lab tests follow.City ordnance against sump pumps being tied into the City s sewers. | SSO Reached Receiving Water | White River; Morse Reservoir
13756 | 36208 | IN0020168 | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-04-18 20:15 |  | 2013-04-19 09:17 | 0 |  | Lift Station #1Lift Station #5Lift Station #8 | Precipitation event triggered untreated release from lift stations to receiving waters. | City ordnance against sump pumps being tied into the City sewer. Lab tests wer taken at the site and the results will be sent to IDEM in follow up report. | SSO Reached Receiving Water | White River; Morse Reservoir
13756 | 36210 | IN0020168 | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-04-18 21:00 |  | 2013-04-19 09:17 | 0 |  | Noblesville WWTP | High water levels and equipment failure caused treated effluent to back up and flooded the controls and boards for the UV equipment. | Making repairs asap as water recedes. Contacted manufacturer rep to seek assistance there as well. | SSO Occurred at Treatment Plant | White River
13756 | 41509 | IN0020168 | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-10-13 03:15 | 2013-10-13 15:45 | 2013-10-31 15:40 | 0 |  | Air relief valve asset #92 near our lift station at 14789 River Rd Ground | Equipment Failure Air relief valve failure caused raw sewage to belch onto the ground when lift station pumps kicked on. At time of incident it was believed to be inside of our lift station property and not on the side road ditch area unable to sample. | Valve was shut off and pulled brought back to maintenance shop for repair. Better understanding of these valves how these and far between incidences are handler with all of the operators and communicated to supervision. Air relief valve will be repaired do more preventative maintenance on the valves annually. | SSO Affected Private Property
13756 | 41752 | IN0020168 | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-11-08 14:13 | 2013-11-08 18:00 | 2013-11-08 15:16 | 0 |  | Air Relief Valve asset #SA-SWVEST-0470 near our lift station at 6649 E 161st Noblesville | Equipment Failure Air relief valve failure caused raw sewage to flow into the ground. Top 6 of soil was removed from area. | See Reports | SSO Affected Private Property; SSO Reached Receiving Water
13756 | 39745 | IN0020168 Waterbody - West Fork White River | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-08-07 16:45 | 2013-08-07 17:00 | 2013-08-08 14:36 | 0 |  | Plant outfall #001 | Our self-cleaning Trojan UV disinfection system functions with hydraulic hoses connected to the cleaning wipers. One of the hydraulic hoses failed releasing some of the hydraulic oil onto the pavement modules and effluent. It is not known how much may have gotten into the water compared to what landed on the concrete and equipment. The three gallon reservoir was approximately halve emptied. | That UV channel was shut down oil absorbent pig brand socks were lain i the UV channel equipment was pulled and wiped down as well as the grating and concrete. All of the hydraulic hoses were replaced on the entire unit. | SSO Affected Private Property; SSO Reached Receiving Water
20192 | 36509 | IN0021334 | ARCADIA WASTE WATER TREATMENT PLANT | Hamilton | 2013-04-19 05:00 |  | 2013-04-19 17:18 | 0 |  | 9099 East. 266th Street - Arcadia WWTP | Precipitation event coupled with an unsealed building allowed storm water to enter the headworks building and damage all of the raw influent pumps. The result was untreated release and bypass of the treatment plant to receiving waters. | Large portable pumps were set up immediately upon discovery of the raw influent pump failures. One pump moved sewage from the raw influent wet well to the oxidation ditch and the other was used to pump out the headworks.The building will be sealed properly as soon as the electrical contractors project is completed. This will prevent storm water entry into the headworks in the future. | SSO Reached Receiving Water | Cicero Creek
20192 | 36815 | IN0021334 | ARCADIA WASTE WATER TREATMENT PLANT | Hamilton | 2013-04-19 05:00 |  | 2013-04-19 07:00 | 0 |  | 9099 E. 266th St Arcadia IN 46030 Ground Cicero Creek | Construction Related Bypass of a Treatment Process During an exceptionally large rain event storm water entered the headworks building damaging all of the raw influent pump. The building was in a unsealed condition due an electrical contractors project. | Large portable centrifugal pumps were set up immediately after the raw pump failures were discovered. One pump was set up to pump from the raw influent wet-well to the oxidation ditch (normal flow path); another was set up to pump out the headworks. The building will be sealed properly as soon as the electrical contractors project is completed. This will prevent storm water from entering the headworks in the future. | SSO Affected Private Property; SSO Reached Receiving Water | Cicero Creek
20193 | 43066 | IN0021351 | WESTFIELD UTILITIES | Hamilton | 2013-12-21 20:00 | 2013-12-21 23:30 | 2013-12-22 08:20 | 31500 | gallons | See Report | Rain 2.5 inches Lift Station running to capacity I&I overwhelmed system. | See Report | SSO Reached Receiving Water | Cool Creek
20784 | 35682 | IN0022306 | ATLANTA WASTE WATER TREATMENT PLANT | Hamilton | 2013-01-13 13:00 | 2013-01-15 10:00 | 2013-01-15 13:19 | 750000 | gallons | Central and Main Bypass manhole #16 | Precipitation event along with snow melt caused untreated release overflows from manhole to storm sewer | New storm sewe system is restrictied by a weir that was placed by the Hamilton County Drainage Board. This was installed to restrict flow in another open ditch until the county performs additional work at an unknown date. Attempting to have the county remove the weir. The town engineers believe it is unnecessary. Removal of this weir should resolve the overflow problem. | SSO Reached Public Land; Storm Sewer
20784 | 36343 | IN0022306 | ATLANTA WASTE WATER TREATMENT PLANT | Hamilton | 2013-04-18 22:00 | 2013-04-21 11:00 | 2013-04-22 08:34 | 750000 | gallons | Central and Main Bypass manhole #16 | Precipitation event(s) and unnecessary weir in storm drain restricting water flow resulted in an untreated release to central and main storm sewer. | County is going to start the project that will allow the removal of the weir. Unknown completion date. | SSO Reached Public Land; Storm Sewer
12657 | 36502 | IN0022497 | Carmel Waste Water Treatment Plant | Hamilton | 2013-04-19 01:15 | 2013-04-19 10:30 | 2013-04-19 16:02 | 201000 | gallons | Manhole on Jeremy Drive - Foster Estates SubdivisionSmokey Knoll Lift Station - 14113 Gray Road | Flow from precipitation event exceed the capacity of manhole and lift station resulting in untreated release from manhole and lift station to surrounding ground and storm sewer. | Divert flow to EQ Basin. Flush area with jet truck. Ongoing sewer rehab project. Contracting for flow monitorintg and TV inspections. Current project to upgrade main lift station. current project to add capacity at plant. | SSO Reached Public Land; Storm Sewer
12657 | 36346 | IN0022497 | Carmel Waste Water Treatment Plant | Hamilton | 2013-04-19 09:00 | 2013-04-20 12:00 | 2013-04-22 09:10 | 28000000 | gallons | Carmel WWTP | Precipitation event necessitated treatment process bypass. UV disinfection bypassed to prevent overflow of final clarifiers aeration tanks and primary tanks. Flow was diverted to EQ Basin | Flow diverted to EQ basin. Ongoing sewer rehab project; contracting for flow monitoring and TV inspections; courrent project to upgrade main lift station; current project to add capacity at plant. | SSO Reached Receiving Water | White River
12657 | 36749 | IN0022497 | Carmel Waste Water Treatment Plant | Hamilton | 2013-04-19 09:00 | 2013-04-20 12:00 | 2013-04-22 09:12 | 28000 | gallons | Carmel Wastewater Treatment Plant White River | Rain 3.25 inches UV disinfection bypassed to prevent overflow of final clarifiers aeration tanks and primary tanks. | Divert flow to EQ Basin. Ongoing sewer rehab project; contracting for flow monitoring and TV inspections current project to upgrade main lift station; current project to add capacity at plant. | SSO Reached Receiving Water | White River
12657 | 36503 | IN0022497 | Carmel Waste Water Treatment Plant | Hamilton | 2013-04-19 09:00 | 2013-04-19 16:00 | 2013-04-19 16:02 | 750000 | gallons | EQ Basin - Outfall 002 815 North Rangeline Road. Carmel WWTP | local flooding and high flows caused by precipitation event resulted in treatement bypass and untreated release from EQ Basin at WWTP to receiving waters. | sandbag area to prevent flooded stream from entering sanitary sewer system.Ongoing sewer rehab project. Contracting for flow monitoring and TV inspections. Current project to upgrade main lift station. Current project to add capacity at WWTP. | SSO Reached Receiving Water | Cool Creek
12657 | 41045 | IN0022497 | Carmel Waste Water Treatment Plant | Hamilton | 2013-10-05 05:00 | 2013-10-05 08:30 | 2013-10-07 14:01 | 0 |  | Woodfield Dr 4879491749434959 Basement Backups | Open manhole at construction site allowed surface water into sanitary sewer system. Pump station serving that area overwhelmed. Water backed up into the basements of at least four homes 6 - 12 deep. | See Report | SSO Basement Backup
12657 | 43085 | IN0022497 | Carmel Waste Water Treatment Plant | Hamilton | 2013-12-23 14:30 | 2013-12-23 16:00 | 2013-12-26 10:26 | 0 |  | Summer Trace Forcemain near 12725 Old Meridian | Untreated Release | See Report | SSO Affected Private Property
20203 | 35471 | IN0022586 | CICERO UTILITIES OFFICE | Hamilton | 2013-01-13 | 2013-01-14 02:00 | 2013-01-15 11:39 | 2700000 | gallons | SSO #1 Plant Headworks SSO #2 Main St. Lift Station | Precipitation event and out of service equipment combined to cause SSO overflows to Storm Sewer and Public Ground. Untreated Release | #2 Raw pump is out for repair. On order since 11/15/12. Personnel on site 24x7 to ensure that all pumps are running at capacity and monitoring overflow. Engineer has finished preliminary report on proposed work to be done. To be submitted to Town Council on 1/15/13. | SSO Occurred at Treatment Plant
20203 | 36327 | IN0022586 | CICERO UTILITIES OFFICE | Hamilton | 2013-04-18 20:30 | 2013-04-20 19:48 | 2013-04-22 08:43 | 3050000 | gallons | SSO #1 Plant HeadworksSSO #2 Main Lift StationManhole #134Academy Lift StationSSO #3 Manhole #369 | Precipitation event triggered untreated release from WWTP headworks and Lift Station as well as multiple manhole locations to surrounding ground and storm sewers. | Staff on site for duration of bypass to monitor pumps. Plant running above peak capacity. Inflow and Infiltration report has been completed by engineer and submitted to the Town Council. The Town Council has instructed the engineer to proceed. | SSO Occurred at Treatment Plant; Storm Sewer
20203 | 36610 | IN0022586 | CICERO UTILITIES OFFICE | Hamilton | 2013-04-24 06:00 | 2013-04-25 06:30 | 2013-04-25 13:31 | 450000 | gallons | SSO #1 WWTP headworksManhole #134 | Precipitation event(s) and apparent I & I contribution resulted in untreated release from WWTP Outfall #1 and manhole to storm sewer and surrounding ground. | Staff on site for duration of bypass to monitor pumps. Plant running above design peak capacity. Inflow and infiltration report has been completed by the Engineer and submitted to Town Council. Town Council has instructed engineer to proceed design and has instructed fincancial consultant to proceed with financing of the project. | SSO Reached Public Land; SSO Occurred at Treatment Plant; Storm Sewer
20203 | 41637 | IN0022586 | CICERO UTILITIES OFFICE | Hamilton | 2013-10-31 22:50 | 2013-11-01 01:38 | 2013-11-01 12:30 | 0 |  | SSO #! Plant Headworks SSO #2 Main St. Lift Station | Rain 2.15 inches | See Report | SSO Affected Private Property
20203 | 43081 | IN0022586 | CICERO UTILITIES OFFICE | Hamilton | 2013-12-21 21:30 | 2013-12-21 14:30 | 2013-12-23 09:12 | 0 |  | SSO #1 Plant Headworks | Exceeded Max CapacityRain 3.36 inches | See Report | SSO Occurred at Treatment Plant | Morse Reservoir
20203 | 43082 | IN0022586 | CICERO UTILITIES OFFICE | Hamilton | 2013-12-21 21:30 | 2013-12-22 05:30 | 2013-12-23 09:12 | 0 |  | SSO #@ Main St Lift Station | Exceeded Max Capacity Rain 2.36 inches | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Morse Reservoir
13762 | 34921 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-02-11 12:10 | 2013-02-14 15:00 | 2010-02-14 16:55 | 0 |  | Sheridan Wastewater Treatment Plant Sheridan IN | End of cleaning tertiary pond in plant. Bypass of tertiary pond. | Bypass from Secondaries to contact Tank in plant. | SSO Occurred at Treatment Plant
13762 | 34969 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-02-11 12:10 |  | 2013-02-11 14:12 | 0 |  | Sheridan WWTP Sheridan IN | In Plant Bypass to clean out Tertiary Pond due to sludge in pond from excess rain. | Flow bypassed from secondaries to contact tank. Cleaning Tertiary Pond of sludge built up as a result of 3+ inches of rain. | SSO Occurred at Treatment Plant
13762 | 35419 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-03-11 21:00 | 2013-03-12 07:30 | 2013-04-12 08:42 | 500000 | gallons | Sheridan WWTP Sheridan IN | Precipitation event forced the Untreated Release from the influent Box to the receiving waters. Plant was full lines in town were full. Customers could not flush. Had to bypass plant to empty some lines in town. | No further action taken. | SSO Reached Receiving Water | Storms Ditch
13762 | 36089 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-03-18 21:30 |  | 2013-04-18 21:47 | 0 |  | Sheridan Wastewater Treatment Plant | Precipitation event exceeded capacity of treatment plant and sewer collection system resulting in a treatment plant bypass and untreated release to receiving waters. Excessive rain plant full. Lines in town full. Customers not able to flush toilets. |  | SSO Reached Receiving Water | Simonin Ditch
13762 | 35637 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-04-11 21:00 |  | 2013-04-11 22:17 | 0 |  | Influent Box Simons Ditch | Rain 3.5 inches Had to bypass plant full all lines in town full due to excess rain 3.5 inches had to bypass to keep form backing up into homes. |  | SSO Reached Receiving Water
13762 | 36528 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-04-18 21:30 | 2013-04-21 06:00 | 2013-04-20 19:56 | 0 |  | Influent box to receiving waters. Sheridan WWTP | Flow from precipitation event exceeded the capacity of the sewer collection system and the WWTP resulting plant bypass of untreated release. Plant at capacity and sewer collection system full. Some homes not able to flush toilets. Plant was bypassed to receiving waters. |  | SSO Reached Receiving Water | Simonin Ditch
13762 | 36684 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-04-28 12:00 |  | 2013-05-10 12:06 | 0 |  | WWTP | Precipitation event necessitated internal plant bypass from secondaries to contact tank. Cleaning out tertiary pond due to excess rain causing plant to overflow pushing sludge into tertiary pond. | Internal bypass only. No impact on effluent. | SSO Occurred at Treatment Plant
13762 | 36779 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-04-28 12:00 | 2013-05-02 07:30 | 2013-05-02 07:55 | 0 |  | Sheridan WWTP | Cleaning of Tertiary Pond required an in house bypass from secondaries to contact tank. |  | SSO Occurred at Treatment Plant
13762 | 37911 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-06-19 10:00 |  | 2013-06-19 10:06 | 340000 | gallons | Secondaries | Rain 4 inches Treatment Bypass. Bypass of tietary pond to clean out sludge due to in plant overflows sludge into cleaning pond. Bypass from secondaries to contact tank. |  | SSO Occurred at Treatment Plant
13762 | 38612 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-06-19 10:00 | 2013-06-21 07:30 | 2013-06-19 07:45 | 350 | gallons | Secondary to contact tank | Rain 4 inches cleaned sludge out of Tietary Pond from heavy rains.
13762 | 42070 | IN0031071 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-11-18 10:00 | 2013-11-20 14:00 | 2013-11-20 14:03 | 0 |  | Treatment Bypass at Plant | End of inplant bypass cleaning pond | See Report | SSO Occurred at Treatment Plant
13762 | 41992 | IN0031071 Outfall 001 | Sheridan Waste Water Treatment Plant | Hamilton | 2013-11-18 10:00 |  | 2013-11-18 10:51 | 0 |  | Treatment Plant Bypass | Rain 3 inches Inplant bypass cleaning out tietary pond. | See Report | SSO Occurred at Treatment Plant | Simonin Ditch
108748 | 39046 | IN0054143 - Terminated | Hamiliton Southeastern Utilities Incorporated | Hamilton | 2013-09-22 13:00 | 2013-09-23 09:50 | 2013-09-30 12:20 | 0 |  | Thorpe Creek Lift Station | Equipment Failure Identified pump 2 VFD had failed due to heat sink over temperature. Electrical interference in the form of line static from the pump 2 VFD failure caused Pump 1 VFD not to receive a run command from the PLC causing a Failed to run error on pump 1. | Repaired Pump Station See Report | SSO Affected Private Property | Grand Calumet River
23586 | 35495 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-01-13 00:30 | 2013-01-13 12:30 | 2013-01-14 12:55 | 60000 | gallons | Winding Creek Lift Station | Precipitation event combined with snow melt caused inflow and ifiltration to the lift station to exceed pumping capacity resultining in untreated release to receiving waters. | On call personnel were on site to ensure that all available pumps remained online. The town has long term plans to install parallel lift station force mains in order to increase pumping capacity. | SSO Reached Receiving Water | Shoemaker Ditch
23586 | 35492 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-01-13 07:00 | 2013-01-13 16:15 | 2013-01-14 12:54 | 24000 | gallons | Smock Creek Lift Station | Precipitation event along with snow melt caused inflow and infiltration to the lift station to exceed pumping capacity resulting in untreated release to unamed receiving water. | On call personnel were on site to ensure all available pumps remained online. The town has long tem plan to install parallel lift station force mains in order to increase pumping capacity. | SSO Reached Receiving Water
23586 | 35488 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-01-13 11:45 | 2013-01-14 01:00 | 2013-01-14 12:54 | 160000 | gallons | Allisonville Road Lift Station | Precipitation event cause I & I to the lift station to exceed pumping capacity resulting in an untreated release to receiving waters | On call personnel were on site during the event to ensure maximum pumping effort. The Town has long term plans to install parallel lift station force mains in order to increase the pumping capacity. | SSO Reached Receiving Water | Cheeney Creek
23586 | 35489 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-01-13 12:30 | 2013-01-13 22:30 | 2013-01-14 15:54 | 120000 | gallons | Hague Road Lift Station | Inflow and Infiltration to the lift station exceeded pumping capacity during a 3 day precipitation event. Untreated release to receiving waters. | On call personnel on site to ensure that all available pumps were online. The town has long term plans to install parallel lift station force mains in order to increase the pumping capacity. | SSO Reached Receiving Water | Cheeney Creek
23586 | 35683 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-04-05 23:15 | 2013-04-07 22:40 | 2013-04-08 12:08 | 160000 | gallons | Allisonville Road Lift Station Cheeney Creek | Untreated Release Equipment Failure Pressure transmitters for wet well control failed causing PLC and main duty pumps to shut down. | On-call personnel responded and re-started the pumps. Third party instrumentation and controls contractor is on site 4/8/13 making necessary repairs. | SSO Reached Receiving Water | Cheeney Creek
23586 | 36501 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-04-18 21:00 | 2013-04-19 11:00 | 2013-04-19 15:44 | 170000 | gallons | Winding Creek Lift Station | High flows during and following precipitation event exceeded the pumping capacity of lift station resulting in untreated release to receiving waters. | On-call personnel remained on site throughout the event to ensure that all pumps continued to run at 100%.The Town s Master Plan provides for additional force amin capacity and I & I remedial work. | SSO Reached Receiving Water | Shoemaker Ditch
23586 | 36499 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-04-18 23:00 | 2013-04-19 07:30 | 2013-04-19 15:44 | 150000 | gallons | smock Creek Lift Station | High flows resulting from precipitation event exceeded the pumping capacity of lift station resulting in untreated release to receiving water. | On-call personnel remained on site throughout the event to ensure that all pumps continued to run at 100%.The town s Master Plan provides for additonal force main capacity and I & I remedial work. | SSO Reached Receiving Water | Cheeney Creek
23586 | 36498 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-04-19 00:30 | 2013-04-19 12:30 | 2013-04-19 15:44 | 300000 | gallons | Allisonville Road Lift Station | High flows resulting from precipitation event exceeded pumping capacity at lift station resulting in untreated release to receiving water. | On-call personnel remained on site throughout the event to ensure that all pumpls continued to run at 100%. The town s Master Plan provides for additional force manin capacity and I & I remedial work. | SSO Reached Receiving Water | Cheeney Creek
23586 | 36496 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-04-19 09:00 | 2013-04-19 11:00 | 2013-04-19 15:44 | 25000 | gallons | Hague Road Lift Station | Flow from precipitation event exceeded capacity of lift station pumps resulting in untreated release to receiving waters. | All pumps on line during event. On-call personnel remained on site throughout the event to ensure that all pumps continued to run at 100%.The town s master plan provides fro additional force main capacity and I & I remedial work. | SSO Reached Receiving Water | Cheeney Creek
23586 | 36612 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-04-24 09:30 | 2013-04-24 13:10 | 2013-04-25 15:04 | 100000 | gallons | Allisonville Road Lift Station | High flows due to a precipitation event exceeded pumping capacity. All pumps were on line at start of event. The back up pump failed reducing pumping capacity resulting in and untreated release from the lift station to receiving waters. | On call personnel remained on site throughout the event to ensure that all pumps continued to run at 100%. The backup pump was repaired and placed back online at 12:45. The Town s Master Plan provides for additional force main capacity and I & I remedial work. | SSO Reached Receiving Water | Cheeney Creek
23586 | 42567 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-12-17 12:00 | 2013-12-17 18:00 | 2013-12-18 12:00 | 0 |  | MH1188 @ 116th St and Cumberland Rd Ditch tributary to Sand Creek | MH1188 @ 116th St and Cumberland Rd | See Report |  | Sand Creek
23586 | 43077 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-12-21 12:30 | 2014-12-22 05:30 | 2013-12-22 13:58 | 300000 | gallons | Allisonville Road Lift Station | Rain 3.5 inches High flows due to precipitation event exceeded pumping capacity. All pumps wee on line throughout the event. | See Report | SSO Reached Receiving Water | Cheeney Creek
23586 | 43079 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-12-21 20:45 | 2013-12-22 02:00 | 2013-12-22 13:58 | 100000 | gallons | Smock Creek Lift Station | Rain 3.5 inches High flows due to precipitation event exceeded pumping capacity. All pumps were on line throughout the event. | See Report | SSO Reached Receiving Water | Smock Creek
23586 | 43076 | IN0055484 | FISHERS CHEENEY CREEK WASTE WATER TREATMNT PLANT | Hamilton | 2013-12-21 21:10 | 2013-12-22 | 2013-12-22 13:58 | 75000 | gallons | Hague Road Lift Station | rain 3.5 inches High flows due to precipitation event exceeded pumping capacity. All pumps were on the line throughout the event. | See Report | SSO Reached Receiving Water | Cheeney Creek
241 | 35595 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Hamilton | 2013-01-07 08:30 |  | 2013-01-07 12:42 | 250 | gallons | Lift Station 7 | A failed fitting inth valve vault came loose resulting in an untreated release and overflow of the valve vault to the ground around the lift station. | Site cleaned up in house. New fittings installed. Continuing weekly checks. | SSO Reached Public Land
241 | 35460 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Hamilton | 2013-01-13 03:00 | 2013-01-13 07:00 | 2013-01-14 10:26 | 6000 | gallons | manhole at 96th and Keystone Ave. Tom Wood Ford dealership | Precipitation event triggered an overflow of untreated release from manhole to ground surrounding manhole. | Continue to monitor situation and lift station to prevent other overflows. Continue I & I manhole repairs. | SSO Reached Public Land
241 | 34857 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Hamilton | 2013-01-15 10:00 | 2013-01-15 10:45 | 2013-01-15 14:30 | 10000 | gallons | Lift Station 9 force Main | City of Carmel Utilities contractor TPI bored through the District s lift station number 9 s foorce main while installing a water line causing an Untreated Release. | Clean up the site before any flow reached a storm drain. District and Fluid Waste trucks were used to pump down the lift station to prevent another overflow. Continue to educate contractors to confirm the utilities that are on site and pay attention to locate flags and.or paint. | SSO Reached Public Land; Surface Soil
241 | 34936 | IN0055760 | CLAY TOWNSHIP REGIONAL WASTE DISTRICT | Hamilton | 2013-02-12 08:00 | 2013-02-12 11:30 | 2013-02-12 13:00 | 10000 | gallons | Manhole SG-065 | Manhole overflow due to contractor boring through laterals while installing a water line. Filled sanitary sewer with slurry mixed with stone and pieces of broken lateral pipe resulting in a blockage causing untreated release from manhole SG-065. | Cleaned sanitary line with jet truck and used vacuum truck to catch material washed out. Fluid Waste was also called to assist in the clean-up of the site and main. Continue to educate contractors to locate laterals along with other utilities before work begins. | SSO Reached Public Land
17382 | 35786 | IN0059544 | WESTFIELD MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-01-13 09:15 | 2013-01-13 15:00 | 2013-01-14 11:18 | 31050 | gallons | 1st manhole west of Gurly Street behind barn surcharging. 2nd and 3rd manholes behine antique store between South Union and Cherry Street | Precipitation event triggered untreated release from manholes to ground and receiving waters. | Lift station pumps worked at capacity. System overwhelmed. Working on plans to install possible new lift station to pump north to regional station to take significant amount of flow of this line.s | SSO Reached Public Land; SSO Reached Receiving Water | Cool Creek
17382 | 36122 | IN0059544 | WESTFIELD MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-04-18 23:00 | 2013-04-19 11:00 | 2013-04-19 11:26 | 108000 | gallons | 1st and 2nd manholes west of Gurley Street/ 3 manholes between South Union and Cherry Street. | Precipitation event caused untreated release from overflowing manholes to surrounding ground and receiving waters. | Lift stations running to capactiy. I & I overwhelmed system. Working on plans to install new lift station to pump north to regional station to take load off of existing station. | SSO Reached Public Land; SSO Reached Receiving Water | Cool Creek
17382 | 36118 | IN0059544 | WESTFIELD MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-04-19 00:30 | 2013-04-19 04:00 | 2013-04-29 10:18 | 4200 | gallons | Manhole in front of Tractor Supply | Precipitation event caused overflow of untreated release from manhole to surrounding ground and drainage swale. | Lift station running to capacity. I & I overwhelmed system. Manufactured home park working on I & I issues. Have done some lining and manhole repairs. | SSO Reached Public Land
17382 | 43068 | IN0059544 | WESTFIELD MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-12-22 08:00 | 2013-12-22 11:00 | 2013-12-22 11:20 | 0 |  | Manhole in front of tractor supply US 31 | Rain 2.5 inches Lift Station running to capacity. Checked amps on both pumps. I&I overwhelmed system. | See Report | SSO Affected Private Property
13756 | 43069 | IN0220168 | NOBLESVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Hamilton | 2013-12-21 21:45 | 2013-12-22 02:29 | 2013-12-22 10:28 | 0 |  | Lift Station #5 406 West Chester Bouelvard Noblesville In 46060 | Rain 3.1 inches Heavy 2 day rain with snow melt caused flow into the lift stations beyond peak pump capacity. | See Report | SSO Affected Private Property
| 39457 | Terminated Permit | Hamilton Southeastern | Hamilton | 2013-07-18 13:55 | 2013-07-18 16:00 | 2013-07-22 14:54 | 0 |  | 10435 Calbauge Dr 11217 Reflection Point Dr | Exceeded Max Capacity Pump Station Failure. Grease picked floats up | See Report | SSO Affected Private Property
12714 | 39776 | IN0002925 | Covance Laboratories Incorporated | Hancock | 2013-08-15 07:16 | 2013-08-15 07:17 | 2013-08-15 16:40 | 0 |  | 671 S Meridian Rd Greenfield IN UV Building prior to entering discharge pipe | Equipment Failure Our UV system consists of a S and N unit both of which are backed up with an Uninterrupteable Power Supply (UPS) system. This morning our facilities management staff person was attempting to verify a temperature loop calibration between 2 buildings at our WWTP. In that action power to our South UV system was inadvertently without power. At the time both the N and S units were operating so only about half of the effluent flow went without disinfection for a 30 second period. Nonetheless a few gallons of flow went without disinfection as unidentified above. | Through the quick actions of the electrician flow through the inoperable unit ceased as quickly as possible once it was realized that power to the unit was interrupted. This minimized the amount of wastewater that had not been disinfected. | SSO Reached Receiving Water | Leary Ditch
32643 | 43087 | IN0020109 | GREENFIELD MUNICIPAL WASTE WATER TREATMENT PLANT | Hancock | 2013-12-21 05:00 |  | 2013-12-21 23:38 | 0 |  | Plant headworks surrounding ground | Rain 5.66 inches Heavy precipitation started around noon on 12-20 and is still raining at the timer of this notification. all equipment is functioning well but the system is surcharged. | See Report
32643 | 43086 | IN0020109 | GREENFIELD MUNICIPAL WASTE WATER TREATMENT PLANT | Hancock | 2013-12-21 05:00 | 2013-12-22 18:30 | 2013-12-23 08:30 | 0 |  | Plant Headworks | Rain 5.78 inches | See Report | SSO Affected Private Property
34827 | 42385 | IN0036528 Outfall 001A | HEARTLAND RESORT | Hancock | 2013-12-10 10:30 | 2013-12-10 12:00 | 2013-12-11 08:46 | 0 |  | WWTP Discharge Pump Station Failure | Equipment Failure Exceeded Max Capacity. Facility s lift station pumps malfunctioned causing the level in the lift station to rise not overflow. Onsite manager tried to pump down lift station and the large amount of water hydraulically overloaded plant and caused solids to discharge. This discharge was minimal and corrected within the hour. Effluent was sampled for permit required parameters. | Repaired Pump Station See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Sugar Creek
35033 | 39837 | IN0058009 | GEM UTILITIES NORTHERN WASTE WATER TREATMENT PLANT | Hancock | 2013-08-21 08:00 | 2013-08-21 08:15 | 2013-08-21 14:00 | 0 |  | Manhole next to Outfall (20 North) | Power Failure Equipment Failure Electrical failure alarm system failure. Due to incorrect wiring of alarm system for power failures. | Repaired Pump Station See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Doe Creek
35033 | 39828 | IN0058009 | GEM UTILITIES NORTHERN WASTE WATER TREATMENT PLANT | Hancock | 2013-08-21 08:00 | 2013-08-28 08:15 | 2013-08-21 14:00 | 0 |  | Manhole next to outfall (20 North) | Power Failure Equipment Failure Electrical failure alarm system failure. Due to incorrect siring of alarm system for power failures. | Repaired Pump Station See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Doe Creek
51096 | 39536 | IN0020460 | MILLTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Harrison | 2013-07-08 09:11 | 2013-07-09 09:11 | 2013-07-08 15:30 | 0 |  | Force main on Harrison Co side of Main St | Construction Related Force main was split at bottom of 8: line repair was made with 1 stainless steel bolt down clamp leak repaired & covered with new gravel old material discarded at town site. | See Report | SSO Reached Public Land
50317 | 40983 | IN0040215 | LANESVILLE WASTE WATER TREATMENT PLANT | Harrison | 2013-10-06 13:30 | 2013-10-06 18:00 | 2013-10-07 12:04 | 0 |  | Manhole near Lift Station Creek | Manhole | Natural Occurrence
50317 | 41933 | IN0040215 | LANESVILLE WASTE WATER TREATMENT PLANT | Harrison | 2013-11-17 14:24 | 2013-11-17 02:45 | 2013-11-18 08:47 | 0 |  | Manhole Creek | Major precipitation in few hours. | Natural Occurrence
51235 | 41809 | IN0059781 Outfall 001 | CAESARS INDIANA GAMING FACILITY | Harrison | 2013-11-13 04:30 | 2013-11-13 07:30 | 2013-11-13 18:59 | 0 |  | R.A.S. Lift Station at WWTF | Equipment Failure Electrical control panel breaker serving Return Activated Sludge (R.A.S.) Lift Station tripped and disabled both pumps. alarm float switch did not activate on-site emergency telemetry. for a brief period of time the lift station over-flowed (through a drain); however spill did not leave the treatment facility premises. | Repaired Pump Station See Report | SSO Occurred at Treatment Plant
| 35008 |  | Marsh Corporation | Hendricks | 2013-02-03 | 2013-02-03 13:00 | 2013-02-04 01:30 | 0 |  | Manhole north of Marsh Lift Station Plainfield IN | Plainfield DPW found lift station in high level on 2/2/2013. DPW found the lift station in equipment failure on 2/3/2013. | gordon s plumbing contacted to make repairs at the Marsh Lift Station. Marsh Corporation has not submitted a preventive maintenance program to the Town of Plainfield | SSO Reached Receiving Water | Clarks Creek
13776 | 36576 | IN0020079 | Danville Water Pollution Control Facility | Hendricks | 2013-01-11 05:15 | 2013-01-11 10:15 | 2013-01-11 11:50 | 37500 | gallons | Manhole #93 East Broadway St Danville IN Ground | Untreated Release 1.6 inches Main sewer line plugged with debris. | Vac/Jet sewer line rinsed ground with clean water. Vac tank used root cutter. One additional personnel will be hired within the month of January 2013. Specifically to be responsible for the ongoing preventative maintenance program for the sanitary sewer system. | SSO Affected Private Property
13776 | 34855 | IN0020079 | Danville Water Pollution Control Facility | Hendricks | 2013-01-11 05:15 | 2013-01-11 10:15 | 2013-01-11 11:50 | 37500 | gallons | Manhole #93 east Broadway St. Danville IN | Main sewer line plugged with debris causing and untreated release. | Vac/Jet sewer line. Rinse ground with clean water. Vac truck used root cutter. One additional person will be hired with the month of January 2013 to be specifically responsible for the ongoing preventative manintenance program for the snaitary sewer system. | SSO Reached Public Land; Surface Soil
13776 | 34854 | IN0020079 | Danville Water Pollution Control Facility | Hendricks | 2013-01-12 23:45 | 2013-01-13 08:45 | 2013-01-13 13:15 | 54000 | gallons | Manhole #105 S. Jefferson St. Danville IN | 11 of snow runoff and 3.1 rainfall created area flooding around manhole #105 S. Jefferson St. Danville IN | The overflow occurred at a lift station designed and built to convey overflows to the treatment plant. the town of danville will investigate installing an additional small section of interceptor pipe to relieve the overflow bottleneck. | SSO Reached Public Land
13776 | 36575 | IN0020079 | Danville Water Pollution Control Facility | Hendricks | 2013-01-12 23:45 | 2013-01-13 08:45 | 2013-01-13 13:15 | 54000 | gallons | Manhole # 105 S Jefferson St Danville IN Ground | Untreated Release Rain 3.1 inches A combination of 11 of snow runoff and 1.6 of rain Friday January 112013 followed by 3.1 of rain during the release created areal flooding. | No action taken. No damage. This overflow occurred at a lift station designed and built to convey overflows to the treatment plant. The town of Danville will investigate installing and additional small section of interceptor pipe to relieve the overflow bottleneck. | SSO Affected Private Property
13776 | 36467 | IN0020079 | Danville Water Pollution Control Facility | Hendricks | 2013-04-18 21:30 | 2013-04-19 05:00 | 2013-04-19 14:00 | 0 |  | Manhole # 655 Wilson Street | Precipitation event triggered area flooding and an untreated release from manhole to surrounding ground. | Release occurred during area flooding. Residential complaint. No action taken no damage to area. Ongoindpreventive maintenance program for the sanitary sewer system. | SSO Reached Public Land
13776 | 36171 | IN0020079 | Danville Water Pollution Control Facility | Hendricks | 2013-04-18 23:30 | 2013-04-19 08:00 | 2013-04-19 09:52 | 103125 | gallons | Manhole #93 Broadway StreetManholes #39 and #145B Old North Salem Road | Precipitation event triggered untreated release from manholes to surrounding ground and storm ditch. Release occurred during area flooding. | No action taken. No damage as the creek was out of its bank. ongoing preventative maintenance program for the sanitary sewer system. Danvill is currently in the planning/survey phase of an old sewer area replacement manhole rehabilitation project for 2013 has been completed. A new pipe was installed to prevent a previous overflow. | SSO Reached Public Land; Storm Sewer
13776 | 36673 | IN0020079 | Danville Water Pollution Control Facility | Hendricks | 2013-04-26 17:20 | 2013-04-26 19:20 | 2013-04-26 20:56 | 60 | gallons | 1247 Sherwood Drive | Main sewer line clog resulted in an untreated release from manhole to surrounding ground and storm sewer. | Main sewer line blocked by broken pieces of lateral. Vac/jet sewer line.Ongoing preventative maintenance. | SSO Reached Public Land
13776 | 41133 | IN0020079 Outfall 001A | Danville Water Pollution Control Facility | Hendricks | 2013-10-20 14:59 | 2013-10-20 14:59 | 2013-10-21 13:30 | 0 |  | Manhole #677 Cook Ave | Unknown We were notified on Monday (today) about this overflow. The overflow was on the ground and did not make it to any stream. | Removed Blockage | SSO Affected Private Property
13776 | 42333 | IN0020079 Outfall 001A | Danville Water Pollution Control Facility | Hendricks | 2013-12-07 19:00 | 2013-12-07 21:30 | 2013-12-09 09:00 | 0 |  | 1014 Lincoln St Danville In | Equipment Failure This was a grease blockage. Wast water was not notified until 8:00am on 12/09/2013 the overflow was in a basement and did not make it to any stream. | Removed Blockage See Report | SSO Basement Backup
42949 | 35862 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-01-11 05:00 | 2013-01-11 | 2013-01-11 15:48 | 0 |  | WWTP clarifiers | Precipitation event and snow melt resulted in partially treated discharge from WWTP to unnamed receiving waters | No actions taken or planned due to unpredictability of precipitation events. | SSO Reached Receiving Water
42949 | 35780 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-01-12 23:00 | 2013-01-14 | 2013-01-14 15:56 | 0 |  | WWTP clarifiers and manhole at main lift. Manhole across from Brixton Lift. | Precipitation event triggered untreated release from Brixton and main lift stations. Waste went to unnamed ditch and Receiving waters. High plant flows caused solids to exit the clarifiers as a partially treated release | All areas around the manholes will be cleaned. All solids picked/raked up. Areas will be limed. No actions planned at this time as rain events cannot be predicted. Town is investigating ways to help with infiltration and illicit connection of sump pump lines to the sanitary line. Town hopes to camera and smoke the problem lines disconnecting any illicit source that is found. | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White Lick Creek
42949 | 35779 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-01-17 | 2013-01-17 12:30 | 2013-01-18 12:01 | 0 |  | 164 Brixton West Drive | Eight inch force main break resulted in sink hole and untreated release to surrounding ground and ditch. | Shut down lift station. Excavated and replaced approximately 69 inches of force main pipe. While break was being repaired pump truck transported waste from the Brixton Lift Station to the main lift station at the WWTP. Town will go in and clean any debrie and lime the area as needed andput straw over the disturbed areas. Once the weather changes the town will go in and button area up and plant grass. | SSO Reached Public Land
42949 | 34919 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-02-05 | 2013-02-05 15:00 | 2013-02-06 15:08 | 0 |  | Break occurred in 8 inch force main in Brixton subdivision. 134 Brixton Woods West Drive Pittsboro IN | Break in 8 force main in Brixton Subdivision. Caused Untreated Realease to residential swale and yard | Lift station shut down while break was repaired. Force main excavated and repaired. Pumper truck transported waste from Brixton station to main station while break was under repair. Town will go in and clean any debris and lime the area as needed. Once the weather changes the town will button up the area and plant grass. Town of Pittsboro is looking at costs of replacing a large segment of this line due to numerous breaks. | SSO Reached Public Land; SSO Affected Private Property; Surface Soil
42949 | 34952 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-02-05 08:52 | 2013-02-08 15:11 | 2013-02-08 15:11 | 0 |  | East entrance of Brixton subdivision | Break in 8 inch force main in Brixton subdivision. East entrance of Brixton | Shut down lift station excavated force main and repaired it. Pumper truck transported waste from Brixton lift station to main lift station at waste water plant during repair. Town will clean up any debris and lime the area as needed. Once weather changes the town will button up the area and plant grass. Town of Pittsboro is investigating the cost of replacing a large segment of this line due to numerous breaks. | SSO Reached Public Land; SSO Affected Private Property
42949 | 34417 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-03-13 | 2013-03-13 09:30 | 2013-03-13 02:46 | 556000 | gallons | 244 Brixton Woods West Drive Break in 8 inch force main in Brixton Subdivision. | Untreated Release Equipment Failure Eight inch forced main break. This causes a sin hole to form and wastewater to be released. Unknown time frame and unknown amount released. | First lift station was shut down then forced main was dug up and fixed. Approximately 47 inches of pipe was replaced. While the break was being fixed a pumper truck transported waste from the Brixton Lift Station to the main lift station at wastewater treatment plant. Town will go in clean any debris and lime the area as needed. Once the weather changes the town will go in a button area up and plant grass.No actions will be taken as this could not be predicted. Town of Pittsboro is getting ready to replace a large segment of this line due numerous breaks. It will be a same ditch replacement. | SSO Affected Private Property
42949 | 35127 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-03-19 15:10 | 2013-03-19 15:15 | 2013-03-20 13:27 | 0 |  | Break in 8 inch force main in Brixton subdivision 174 Brixton Woods West Drive. Grassy swale/yard | Untreated Release Equipment Failure Eight inch forced main bread due to direction bore skimming the pipe. The crew knew instantly when they hit the pipe and called for the lift to be turned off. No sewage even made it to the surface only the small amount in the hole. | First ;oft station was shut down then forced main was dug up and fixed. While the break was being fixed two pumper trucks transported waste from the brixton lift station to the main lift station at wastewater treatment plant. Town will go in clean any debris and lime the area as needed. Once the weather changes the town will go in a button area up and plat grass.No actions will be taken as this could not be predicted. Town of Pittsboro is getting ready to replace a large segment of this line due numerous breaks. It will be a same ditch replacement. | SSO Affected Private Property
42949 | 35686 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-04-16 11:45 | 2013-04-17 | 2013-04-18 02:19 | 0 |  | WWTP Clarifiers through to creek. | Partially Treated Release Blended With Effluent & Sampled Rain 3.19 inches. High rain fall caused flooding and infiltration in the wastewater system. Numerous Lift Station in town went into high alarm. High plant flows caused solids leaving from clarifier. | No actions could be taken to prevent the high flows due large rain event. No actions planned at this time as rain events cannot be predicted. Town is investigating ways to help with infiltration and illicit-connection of sump pump lines to the sanitary line. Town hopes to camera and smoke the problem lines. Disconnecting any illicit source that is found.
42949 | 36627 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-04-18 08:10 | 2013-04-19 06:00 | 2013-04-19 01:35 | 0 |  | Plant lift overflow Brixton lift & School Lift Plant Clarifier | Untreated Release Rain 3 inches High rain fall continued causing flooding. 6.34 inches of rain in 72 hours 3 lifts went into high alarm then started to overflow. High plant flow caused solids to leave from west clarifier. | No action could be taken to prevent high flow due to large rain event over numerous days. | SSO Affected Private Property
42949 | 41584 | IN0020401 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-10-31 08:30 | 2013-11-01 12:30 | 2013-11-01 10:15 | 0 |  | manhole at Main Lift Clarifer at WWTP Manhole across Brixton lift manhole at school lift | Rain The discharge form the manhole at the min lift station went down grassy hill into a field area then entered a small tributary to the West Fort of White Lick Creek. The discharge started at approxiately 8:30pm on 10/31/2013 and stopped by 12:45 am on 11/01/13. The hill area below the manhole will be cleaned up. No damages was observed to aquatic life or receiving stream. The discharge from the manhole behind the school did not appear to leave the grassy swale area. This overflow started approxiately 9:pm and had stopped by 12:30. The manhole across from Brixton lift discharged to a grassy area which was flooded by near by unnamed ditch. This overflow started a approxiately 9 pm on 10/31/13 and stopped by 1230am on 11/-1/2013. No damage was observed to aquatic life or receiving stream. | See Report | SSO Reached Receiving Water | White Lick Creek
42949 | 43142 | IN0020401 Outfall 001 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-12-21 14:00 | 2013-12-21 20:00 | 2013-12-23 08:32 | 0 |  | Rain 3 inches First event is bypass at wwtp-System was hydraulically overloaded and cause the clarifiers to loose some solids. Second event both the school & Brixtion lifts overflowed to much water in the system the pumps could not keep up with the flow. | Rain 3 inches First event is bypass at wwtp-System was hydraulically overloaded and cause the clarififiers to loose some solids. Second event0both the schools & Bristion lifts overflowed to much water in the system. the pumps could not keep up with the flow. | See Report | SSO Affected Private Property; SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White Lick Creek
42949 | 43144 | IN0020401 Outfall 001 | PITTSBORO MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-12-21 22:30 | 2013-12-22 | 2013-12-23 08:32 | 0 |  | Briston & School lifts station overflow | Rain 3 inches. first event is bypass at wwtp-System was hydraulically overloaded and cause the clarifiers to loose some solids. Second event both the school & Brixtion lifts overflowed to much water in the system the pumps could not keep up with the flow. | See Report | SSO Affected Private Property; SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White Lick Creek
40083 | 34730 | IN0021202 | PLAINFIELD WASTE WATER TREATMENT PLANT | Hendricks | 2013-02-26 13:00 | 2013-02-26 17:30 | 2013-02-27 13:00 | 0 | gallons | Deerfield Park Lift Station. 3264 E. Main Street | Precipitation Event 1.6 inches of rain caused untreated release | Rain stopped | SSO Reached Public Land; Surface Soil
40083 | 35509 | IN0021202 | PLAINFIELD WASTE WATER TREATMENT PLANT | Hendricks | 2013-04-01 | 2013-04-01 15:00 | 2013-04-02 13:54 | 100 | gallons | Easement west of 450 Picket St Ground | Untreated release Root obstruction | Root ball removed jetted line to clean Applied lime to ground Routine cleaning. | SSO Affected Private Property
40083 | 36421 | IN0021202 | PLAINFIELD WASTE WATER TREATMENT PLANT | Hendricks | 2013-04-19 | 2013-04-20 09:00 | 2013-04-20 14:35 | 0 |  | Manhole at Swinford Park | Precipitation event triggered an untreated release from manhole to surrounding ground. |  | SSO Reached Public Land
40083 | 39409 | IN0021202 | PLAINFIELD WASTE WATER TREATMENT PLANT | Hendricks | 2013-07-15 13:30 | 2013-07-15 13:50 | 2013-07-15 14:10 | 0 |  | CSO Outfall #006 | Exceeded Max Capacity Construction crew plugged sewer man for manhole installation. When plug was removed surge at the plant exceed max flow. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White Lick Creek
40083 | 40099 | IN0021202 | PLAINFIELD WASTE WATER TREATMENT PLANT | Hendricks | 2013-09-11 15:57 | 2013-09-11 16:11 | 2013-09-12 11:40 | 0 |  | Outfall #6 White Lick Creek | Equipment Failure | Started additional raw pump and shortened time delay on fine screen. Repairs to fine screen level sensor for auto stop and start. | SSO Reached Receiving Water | White Lick Creek
42744 | 35857 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-01-12 21:55 | 2013-01-13 19:18 | 2013-01-14 16:13 | 12660000 | gallons | CSO tank Outfall 005 | Precipitation events and snow melt resulted in a partially treated release from WWTP to receiving waters | System was inspected to verify theat plant maximization during the event was maintained. Stormwater separation projects continue to move forward for the community. | SSO Reached Receiving Water | White Lick Creek
42744 | 35073 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-02-02 06:00 | 2013-02-02 09:45 | 2013-02-04 16:00 | 100 | gallons | Manhole at the intersection of Maxine and Weston in Brownsburg IN | Sewer main blockage due to debris and root infiltration. Untreated release. | Blockage was cleared as quickly as possible. Preventative maintenance of the collection system including televising cleaning and root treatment programs will continue. | SSO Reached Public Land
42744 | 34995 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-02-02 06:00 | 2013-02-02 09:45 | 2013-02-02 13:10 | 100 | gallons | Manhole at intersection Maxine and Weston | Root and debris causing sewer main blockage resulting in Unteated Release to street catch basin storm sewer. | Blockage was cleared as quickly as possible. Preventative maintenance of the collection system including televising cleaning and root treatment programs will continue | SSO Reached Public Land
42744 | 34607 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-03-07 10:30 | 2013-03-07 11:15 | 2013-03-07 13:19 | 300 | gallons | Manhole at the NW corner of 1353 E Main Ground | Untreated Release Equipment Failure Force main form the creek side lift station was leaking at a air release valve pit. Pit filled with sewage and overflowed onto the ground. Repair of the force main is ongoing at this time. | Lift station was shut off and vac truck was used to pump material out of the pit. Vac truck was also used to vac up as much material from the ground as possible. Line will be dug up so that the extent of damage can be assessed and the line repaired. Tanker and portable pump set up at the lift station to keep the level at the lift station maintained. If the cause of the failure can be determined changes to installation requirements can be made to prevent future recurrences. | SSO Affected Private Property
42744 | 36001 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-04-16 18:40 | 2013-04-17 03:07 | 2013-04-17 20:36 | 150000 | gallons | CSO Overflow tank Outfall 005 | Precipitation event exceeded the capacity of the overflow storage tank resulting in a partially treated release to receiving waters. | Flows to the treatement plant were maintained at the maximum before and during the event. As flows decrease the storage tank will be emptied as much as possible in anticipation of further precipitation.The Southside Drainage separation project has been designed and the Town is in the process of obtaining easements such that the project many continue moving forward. | SSO Occurred at Treatment Plant | White Lick Creek
42744 | 36508 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-04-18 20:15 | 2013-04-19 13:35 | 2013-04-19 17:15 | 20000000 | gallons | Brownsburg WWTP CSO Tank Outfall 005 | High inflows resulting from precipitation events caused the Combined Overflow Storage Tank to fill and overflow resulting in a partially treated release to receiving waters. | Flows to treatment plant were maintained at the maximum before and during the event. The flows have been at maximum for several hours. The tank had been emptied just before this rain event began.The Soutside Drainage separation project has been designed and the Town is in the process of obtaining easements such tht the project may continue to move forward. | SSO Reached Receiving Water | White Lick Creek
42744 | 36098 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-04-19 | 2013-04-19 05:00 | 2013-04-19 20:57 | 300 | gallons | 33 East Tilden Avenue | Precipitation event cause severe flooding and resulted in an untreated release into a residential basement. | All Lift Stations and collection system operating at full capacity. Basement back up drained back into system following flooding. Continue televising of sewer system to determine sources of inflow and infiltration and eliminate when found. This location is within the area of a planned storm separation project that continues to move forward. | SSO Basement Backup
42744 | 36132 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-04-19 00:30 | 2013-04-19 09:30 | 2013-04-19 20:57 | 10000 | gallons | Manhole at 221 South Mardale Drive | Precipitation event and associated flooding triggered untreated release from manhole to surrounding ground parking lot and open ditch. | Sewer line overwhelmed due to severe flooding. Lift stations running at capacity. Personnel present during event to monito lift stations. Continue televising of sewer system to determine sources of inflow and infiltration and eliminate when found. Sewer lid inserts have already been placed in several locations to prevent possible inflow. | SSO Reached Public Land; Paved Surface
42744 | 36444 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-04-19 01:00 | 2013-04-19 05:00 | 2013-04-22 16:01 | 25 | gallons | 16 Twin Street - Basement backup Basement drain back into system. | Untreated Release Rain 3.25 inches Sewer line overwhelmed due to severe flooding throughout community. Homeowner stated that the drains has been plugged and some water seeped through the plugs and pooled around two drains. Homeowner had plugs removed this morning to eliminate the two pools of water surrounding the drain. Estimated start & stop time - homeowner unsure of the times. | All lift stations and collection system were operating at full capacity. Continue televising of sewer system to determine sources of inflow and infiltration and eliminate when found. | SSO Basement Backup
42744 | 36252 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-04-24 | 2013-04-24 00:30 | 2013-04-24 12:15 | 200 | gallons | Main pumping station 200 S Green Ground | Untreated Release Equipment Failure As a rain event began the main pumping station wet well filled. All 3 pumps plus the 4 back up pump were running; however two of the pumps were air locked and not pumping properly. The automatic sluice gate did not close enough and the influent channel overflowed. | Personnel responded to a high level alarm. Upon arrival the influent sluice gate was placed in manual and lowered just as the channel began to overflow. The pumps were inspected and two were found to be air locked and not pumping correctly. The air was cleared from the pumps and the sluice gate was placed back into the automatic mode. It is believed that air entered into the pumps during the cleaning of gravel out of the influent channel earlier in the week. Anytime personnel pump down the wet well for maintenance they are to operate each of the 4 pumps to verify they are all still working properly. | SSO Affected Private Property
42744 | 36160 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-04-24 08:28 | 2013-04-24 10:55 | 2013-04-24 21:46 | 500000 | gallons | CSO Tank Outfall 005 White Lick Creek | Partially Treated Release Rain 1.25 inches The combined overflow storage tank became full during an intense rain event and began discharging through outfall 005. There had previously been an intense rain event within the past two days. The ground was saturated and receiving streams were at an elevated level. | Flows to the treatment plant were maintained at the peak capacity or greater before and during the event. The flows have been at the maximum for several hours. Once the flows to the treatment plant decrease the CSO storage tank will be emptied and prepared for the next possible event. The Southside Drainage separation project has been designed and the Town is in the process of obtaining easements such that the project may continue to move forward. | SSO Reached Receiving Water | White Lick Creek
42744 | 38222 | IN0021245 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-07-02 20:18 | 2013-07-02 21:18 | 2013-07-02 22:10 | 0 |  | CSO 005 Partially treated overflow from CSO facility. | Rain 0.75 inches. Intense heavy rainfall occurred causing the event. | Treatment plant flows were maximized during the rain event. The south side drainage separation project has been designed and the Town is in the process of obtaining easements such that the project may continue forward. | SSO Reached Receiving Water | White Lick Creek
42744 | 41489 | IN0021245 Outfall 005 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-10-31 19:33 | 2013-10-31 23:41 | 2013-11-01 05:00 | 0 |  | CSO 005 | Rain 0.75 inches Intense heavy rainfall occurred causing the event. | See Report | SSO Reached Receiving Water | White Lick Creek
42744 | 41896 | IN0021245 Outfall 005 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-11-17 03:15 | 2013-11-17 05:30 | 2013-11-17 07:00 | 0 |  | CSO ))% | Rain 1.25 inches Intense heavy rainfall occurred causing the event. | See Report | SSO Reached Receiving Water | White Lick Creek
42744 | 42628 | IN0021245 Outfall 005 | BROWNSBURG MUNICIPAL SEWAGE TREATMENT PLANT | Hendricks | 2013-12-21 13:15 | 2013-12-22 03:30 | 2013-12-22 14:30 | 0 |  | CSO 005 | Rain .75 inches. Intense heavy rainfall occurred following a snow melt causing the event. | See Report | SSO Reached Receiving Water | White Lick Creek
43074 | 36450 | IN0040436 | NORTH SALEM MUNICIPAL WASTE WATER TREATMENT PLANT | Hendricks | 2013-04-19 04:00 | 2013-04-20 11:00 | 2013-04-21 12:08 | 100000 | gallons | 1st manhole west of lift station | Precipitation event caused flash flooding and erosion cutting buried power lines and 4 force main from lift station to sewer plant. Untreated release. | temporarily repaired 4 force main and electric until ground dries out to make permanent repairs. Redirect surface water runoff to prevent erosion. | SSO Reached Public Land
41100 | 36475 | IN0049581 | BELLEVILLE CONSERVANCY DISTRICT WASTE WATER TREATMENT PLANT | Hendricks | 2013-04-18 23:00 | 2013-04-19 07:00 | 2013-04-19 14:49 | 0 |  | Lift Station on C. R. 121 Clayton IN | Precipitation event flow exceeded capacity of lift station resulting in an untreated release to surrounding ground. | Station was monitored to ensure that pumps were running. | SSO Reached Public Land
41100 | 43145 | IN0049581 | BELLEVILLE CONSERVANCY DISTRICT WASTE WATER TREATMENT PLANT | Hendricks | 2013-12-21 08:16 | 2013-12-22 08:00 | 2013-12-22 08:57 | 0 |  | Clayton IN CR 121 Lift Station Ground | rain 3.3 rain Station was monitored to ensure that pumps were running. | See Report | SSO Affected Private Property
14678 | 36033 | IN0057614 | Hendricks County Regional Sewer District | Hendricks | 2013-04-18 10:00 | 2013-04-19 08:00 | 2013-04-22 03:29 | 0 |  | Wynbrooke Lift Station Bullard Creek | Rain 3.8 inches. All pumps opening could not keep up due to excessive flow. | Maintained surveillance over night. | SSO Affected Private Property
14678 | 37397 | IN0057614 | Hendricks County Regional Sewer District | Hendricks | 2013-04-18 10:20 | 2013-04-19 08:00 | 2013-04-19 | 0 |  | Wynbrooke Lift Station Bullard Creek | Rain 3.8 inches Wynbrooke Lift station | All pumps operating could not keep up due to excessive flow. Maintained surveillance over night. | SSO Reached Receiving Water
45450 | 36486 | IN0062456 | PLAINFIELD SOUTH WASTE WATER TREATMENT PLANT | Hendricks | 2013-04-19 | 2013-04-19 | 2013-04-19 15:03 | 0 |  | Clarks Creek Road Lift Station | Flow from precipitation event caused an untreated overflow from lift station to surrounding ground. | Lift station was checked during rain event but overflow wa not observed. | SSO Reached Public Land
| 37003 | No Permit |  | Hendricks | 2013-05-19 | 2013-05-19 12:52 | 2013-05-21 08:16 | 0 |  | Manhole at trailer park ground. | Untreated Release Equipment Failure Rain This is a private sewer line for the trailer park. The trailer park manager was notified and failed to respond in an adequate time frame. | On -call operator called in a vendor to unclog the trailer park sewer line. The trailer park manager has not submitted any preventive maintenance plan for the trailer park sewer system. | SSO Affected Private Property
42624 | 35548 | IN0023914 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-01-13 09:00 |  | 2013-01-15 14:46 | 4000000 | gallons/day | Final effluent filter at WWTP | Equipment failure at WWTP necessitates the bypass of the final filter process. 2 pumps require repair. Final discharge to unnamed receiving water. | Effluent will be recombined and sampled before discharge. All effluent will be going through flow meter. New filter pumps will be installed. | SSO Occurred at Treatment Plant
42624 | 35653 | IN0023914 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-01-17 09:13 |  | 2013-01-25 16:01 | 0 |  | End of structure #10 inside WWTP bypassing filters | Failure of the filter pumps resulted in Bypass of a treatment process and reblending and sampling of Final Effluent. | filter pumps removed for repair. Baffle from end of chlorine contact tank also removed. | SSO Reached Receiving Water | Blue River
42624 | 35774 | IN0023914 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-01-17 09:17 |  | 2013-01-11 10:11 | 0 |  | New Castle WWTP | Filter pump failure resulted in bypass of a treatment process while pumps were being repaired. | Removed filter pumps for repair. Removed baffle end of chlorine tank. Pumps being rebuilt. Bypass effluent being recombined with final effluent and sampled prior to discharge. | SSO Occurred at Treatment Plant | Blue River
42624 | 35413 | IN0023914 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-04-12 10:00 |  | 2013-04-12 09:06 | 0 |  | City of New Castle WWTP New Castle IN | Diffuser repairs for better mixing and aeration required the bypass of this operation from the Old East/Old West aeration basins. The partially treated release was remixed with final effluent and sampled before dishcarge. | Fixing diffusers to obtain better mixing and aeration. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Blue River
42624 | 39525 | IN0023914 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-07-02 08:00 | 2013-07-03 15:30 | 2013-07-01 08:03 | 0 |  | 10 Midway Dr. New Castle IN 47362 | Construction Related Equipment Failure Repairing and replacing plumbing and diffusers in our contact tank to be able to run our post DO blower system. The only affected area of our treatment plant process will be our disinfection system which will be shut down during this repair. | Repaired Pipe | SSO Reached Receiving Water | Big Blue River
42624 | 39658 | IN0023914 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-08-01 08:00 | 2013-08-02 13:00 | 2013-08-01 02:00 | 0 |  | 10 Midway Dr. New Castle IN 47362 | Repairing and replacing plumbing and diffusers in our contact tank to be able to run DO blower system. The only affected area of our treatment plant process will be our disinfection system which will be shut down during the repair. | Repaired Pipe See Report | SSO Reached Receiving Water | Big Blue River
42624 | 40031 | IN0023914 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-09-10 08:00 | 2013-09-11 08:00 | 2013-09-09 23:34 | 0 |  | 10 Midway Dr New Castle In 47362 | Repairing and replacing plumbing and diffusers in our contact tank to be able to run our post DO blower system. The only affected area of our treatment plant process will be our disinfection system which will be shut down during the repair. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Big Blue River
42624 | 42533 | IN0023914n Outfall 001 | NEW CASTLE WASTE WATER TREATMENT PLANT | Henry | 2013-12-15 11:00 | 2013-12-16 07:00 | 2013-12-16 14:00 | 0 |  | Foster Landing Lift Station Fosters Way New Castle In 47362 | Equipment Failure Float failed on lift station. Wastewater overflowed to dry weather ditch and remains contained due to ground being frozen. Location of lift station is indicated on attachment accompanying this Bypass/Overflow Incident Report.. | Repaired Pump Station See Report | SSO Reached Public Land
| 34941 | IN0023915 |  | Henry | 2013-03-19 09:23 | 2013-03-19 | 2013-03-19 20:33 | 0 |  | End of Contact Tank Blue River | End of Contact Tank Blue River |  | SSO Reached Receiving Water | Blue River
43017 | 35539 | IN0041181 | GOLDEN PEBBLE ESTATES MOBILE HOME PARK | Henry | 2013-01-12 |  | 2013-01-15 12:19 | 0 |  | Permit says Golden Pebble Estates Mobile Home Park. Incident Report indicates Blue River Schools. | New plant set up caused clarifier to float up. Resulting in Bypass of Treatment Process Untreated Release recombined with final effluent and sampled before discharge to receiving waters |  | SSO Occurred at Treatment Plant | Blue River
43003 | 39758 | IN0055131 | SOUTH HENRY REGIONAL WASTE DISTRICT | Henry | 2013-08-09 04:30 | 2013-08-09 05:15 | 2013-08-09 09:36 | 0 |  | Home owner clean out @ 105 Union St Lewisville Ground | Floats did not tip they were on a mat in the wet well and was carried up without tipping and wet well went into high alarm and did not call. Sewer did not over flow @ any manhole and ran out of home owner clean out in front yard. | Cleaned wet well so floats work properly. Wet well is cleaned weekly and had a mat floating that just happened to carry floats and did no allow to tip. Will keep a better program of cleaning wet well more often also will install backflow valve in home owner lateral line. | SSO Affected Private Property
43003 | 41127 | IN0055131 | SOUTH HENRY REGIONAL WASTE DISTRICT | Henry | 2013-10-15 14:30 |  | 2013-10-16 11:19 | 0 |  | 1228 W Fair Oaks Rd New Castle | Unknown Contractor has been called and emergency locates have been done. It appears to be a possible pipe failure next to a homeowner grinder pump station. The ground is moist but no puddling. | Repaired Pipe See Report | SSO Affected Private Property
43003 | 39173 | Jerry Libby | SOUTH HENRY REGIONAL WASTE DISTRICT | Henry | 2013-08-09 04:00 |  | 2013-08-09 05:30 | 5000 | gallons | 105 Union Street | SSO | Waste district contacting their insurance company but conducting the cleanup in-house at time of notification. Smith requested waste district fax a bypass notification form to OWQ. Incident referred to OWQ.Jerry Libby updated Smith at 9:45 AM that the revised amount of sewage released to 5000 gallons. He indicated it discharged from a clean-out on the residential home s lateral line and not from a sanitary sewer manhole. He also confirmed sewage did not impact the crawl space or the garage of the home.
43129 | 36215 | 43129 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-18 18:00 |  | 2013-04-19 08:41 | 0 |  | Greentown WWTP | Temporary levee breached by flood waters. Wet well was overtopped and pump building flooded. Pump #1 temporarily disabled. | Levee being repaired and water pumped out. Pump will be repaired. Report to follow. Plant currently undergoing reconstruction. | SSO Occurred at Treatment Plant
43129 | 35248 |  | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-01-13 00:25 | 2013-01-14 00:45 | 2013-01-14 12:14 | 0 |  | Greentown WWTP Greentown IN | Precipitation event resulted in Untreated Release from WWTP Outfall 002 to receiving waters. | Begin reconstruction of plant in March of 2013. Bypass pumped effluent to outfall 003 | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Brunk Ditch
42710 | 36437 | IN0020532 | RUSSIAVILLE WASTE WATER TREATMENT PLANT | Howard | 2013-04-18 17:00 | 2013-04-19 16:30 | 2013-04-20 17:28 | 141000 | gallons | 1st Manhole South of the WWTP | Precipitation event(s) and I & I contribution(s) exceeded the capacity of the collection system and the WWTP. Result was a partially treated release to receiving waters. | Ensured that pumps were operating correctly. Removed t-shirt clogging the 2nd backup pump. Increased flow to 650 gpm. Pumped 40000 gallons of mixed liquor from RAS wet well into digester to preserve biosolids and protect treatment. Took 2nd influent pump out of service to prevent ATs overflowing. Creek crested at 20 feet out of its banks. WWTP continued to operate even though Outfall structure was submerged.The Russiaville Wastewater utility is in the midst of a capital improvement project which includes the cleaning and televising of sewers in an area suspected of contributing extraneous water from inflow/infiltration to the wastewater collection system. The project inclueds the re-lining of up to 4000 feet of sewers to remove the I & I influence from the system as well as new influen pumps and controls. The project also inclues intallation of an emergency generator to insure a continuous power supply for the influen pumps and WWTP process units. This work is projected to be completed by the end of May 2013. | SSO Reached Receiving Water | Honey Creek
42710 | 38487 | IN0020532 | RUSSIAVILLE WASTE WATER TREATMENT PLANT | Howard | 2013-06-16 10:56 | 2013-06-16 11:30 | 2013-06-18 11:00 | 24000 | gallons | 1st MH South of WWTP Ground - honey Creek | Equipment FailurePrecipitation A lightening strike during a severe storm in Ruissiaville (at approximately 0530) destroyed a transformer in Rruissiaville interrupting electrical service i the area. The power surge when the electrical service was restored caused a loss in 1- phase of the 3- phase electrical service into the Ruissiaville WWTP when he discovered that the influent pumps were not operating and that wastewater was flowing out of the 1st MH upstream of the WWTP. A local electrician responded to an emergency call and power was restored to the influent pumps and they were put back on line immediately. | As described above. The Operator making the weekend check responded as quickly as possible and corrected the situation. The Russiaville Wastewater Utility is sin the midst of a capital improvement project which includes the installation of an emergency generator and automatic transfer switch. The generator has been installed but not connected for use. That has been scheduled as a priority item for the week of 6/17/13 | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Honey Creek
43129 | 35247 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-01-13 04:00 | 2013-01-14 14:00 | 2013-01-14 12:14 | 0 |  | Greentown Municipal WWTP Greentown IN | Precipitation event resulted in Bypass of treatment process partially treated release and blending with and sampling of final effluent. Release from Surge Basin to Polishing Ponds. | Begin reconstruction of plant in March 2013. | SSO Occurred at Treatment Plant
43129 | 34764 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-02-27 07:00 | 2013-02-28 07:00 | 2013-02-28 10:45 | 0 |  | Surge Basin at Greentown Municipal WWTP | A 1.1 inch precipitation event caused a partially treated release due to a bypass of a treatement process. Release was blended with Final Effluent and Sampled. | Follow up to report submitted on 2/27/2013. No action taken to prevent mitigate or minimize. Plant is currently undergoing reconstruction. | SSO Occurred at Treatment Plant
43129 | 35602 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-11 |  | 2013-04-11 08:59 | 0 |  | Surge Basin Polishing Ponds | Bypass of a Treatment Process Rain 3.2 inches | Plant currently undergoing reconstruction.
43129 | 35605 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-11 03:35 |  | 2013-04-11 08:59 | 0 |  | Outfall 002 Brunk Ditch | Untreated Release Rain 3.2 inches | Plant currently undergoing reconstruction. | SSO Reached Receiving Water | Brunk Ditch
43129 | 35409 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-11 03:35 | 2013-04-12 09:10 | 2013-04-12 11:16 | 0 |  | Greentown WWTP outfall 002 Greentown IN | Precipitation event triggered an Untreated Release from the Greentown WWTP Outfall 002. | No action taken. Follow up report to one filed on 4/11/13. Plant currently undergoing reconstruction. | SSO Reached Receiving Water | Brunk Ditch
43129 | 35805 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-11 06:00 | 2013-04-15 07:00 | 2013-04-15 03:47 | 0 |  | Surge Basin Polishing Ponds | Partially Treated Release Bypass of a treatment Process Blended with Final effluent & Sampled Follow up report to one filed on 4-11-13 | Plant currently undergoing reconstruction. | SSO Occurred at Treatment Plant
43129 | 36380 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-18 18:00 | 2013-04-22 06:00 | 2013-04-22 10:51 | 0 |  | Surge Basin to Polishing Ponds | Follow up report to Incident Report(s): 36213 36215 36258. | Levee repaired - water pumped out Pumps being repaired. Plant currently undergoing reconstruction. | SSO Occurred at Treatment Plant
43129 | 36379 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-18 21:20 | 2013-04-20 03:15 | 2013-04-22 10:51 | 0 |  | Greentown WWTP | Follow Up report to Incident Number(s): 36221336215 and 36258. Linked | Levee is repaired - water pumped out. Pumps being repaired. Plant currently undergoing reconstruction. | SSO Reached Receiving Water | Brunk Ditch
43129 | 36213 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-18 21:20 |  | 2013-04-19 08:41 | 0 |  | Greentown WWTP Outfall 002 | Precipitation event and resulting flooding breached a levee and flood waters overflowed the wet well and flooded the pump building. Pump #1 temporarily disabled. Untreated release to receiving waters. | Levee being repaired and water pumped out. Pump will be repaired. Plant currently undergoing reconstruction. | SSO Reached Receiving Water | Brunk Ditch
43129 | 36258 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-24 03:40 | 2013-04-24 06:15 | 2013-04-24 08:27 | 0 |  | Outfall 002 Brunk Ditch | Untreated Release Rain 1.5 inches Raw sewage pumps #1 & #2 are down. Supplementing with gas & electric pumps. | Raw sewage pumps are being repaired using gas and electric pumps. Plant is being reconstructed. | SSO Occurred at Treatment Plant | Brunk Ditch
43129 | 36591 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-24 16:00 | 2013-04-25 14:30 | 2013-04-25 14:18 | 0 |  | Greentown WWTP Surge Basin to Polishing Ponds | Precipitation event and equipment failure resulted in treatment process bypass as well as partially treated release that was blended with final effluent and sampled prior to discharge. Raw sewage pumps 1 & 2 failed. | Using gas and electric pumps to try to handle inflow while the two main pumps are out of service. Plant is currently being reconstructed. | SSO Occurred at Treatment Plant
43129 | 36662 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-24 16:00 | 2013-04-26 07:00 | 2013-04-26 09:10 | 0 |  | WWTP Surge Basin Contact Tank Polishing Ponds. | Equipment failure at the WWTP resulted ion treatment bypass and partially treated release to the polishing ponds. | Raw sewage pumps #1 and #2 were both failed. Supplemented with gas and electric pumps. Raw sewage pump #2 was repaired #1 being repaired. Overflow was blended with final effluent and sampled before discharge.Plant is currently being reconstructed. | SSO Occurred at Treatment Plant
43129 | 37778 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-06-10 13:00 | 2013-06-11 06:00 | 2013-06-11 10:32 | 75000 | gallons | Surge Basin Wildcat Creek | Exceeded Max Capacity Rain 2 inches | Plant currently undergoing reconstruction. | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water
43129 | 37763 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-06-10 13:00 |  | 2013-06-10 02:51 | 50000 | gallons | Surge Basin | Exceeded Max Capacity Rain 2 inches | Plant currently undergoing reconstruction. | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water
43129 | 37843 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-06-13 07:15 |  | 2013-06-13 11:07 | 0 |  | Surge Basin Wildcat Creek | Exceeded Max Capacity Rain 3.1 inches Surge Basin. | None Plant currently undergoing reconstruction. | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Wildcat Creek
43129 | 38621 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-06-13 13:30 |  | 2013-06-13 16:40 | 100000 | gallons | Outfall #002 | Rain 3.1 inches Exceeded Max Capacity Duckbill | Plant currently undergoing reconstruction | SSO Reached Receiving Water | Wildcat Creek; Brunk Ditch
43129 | 37913 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-06-13 13:30 | 2013-06-13 18:10 | 2013-06-14 08:35 | 150000 | gallons | Outfall 002 Wildcat Creek Brunk Ditch | Exceeding Max Capacity Rain 3.1 inches | None Plant currently undergoing reconstruction. | SSO Reached Public Land; SSO Reached Receiving Water | Wildcat Creek; Brunk Ditch
43129 | 39489 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-07-02 22:40 | 2013-07-03 13:50 | 2013-07-03 01:44 | 0 |  | Outfall #002 Treatment Bypass Other- Duckbill | Rain 2.7 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Brunk Ditch
43129 | 39492 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-07-02 22:40 |  | 2013-07-03 10:13 | 0 |  | Outfall #002 Treatment Bypassed Duckbill | Rain 2.7 inches Exceeded Max Capacity | See Report | SSO Reached Public Land; SSO Occurred at Treatment Plant; SSO Reached Receiving Water
43129 | 39491 | IN0021091 | GREENTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-07-03 06:30 |  | 2013-07-03 08:55 | 0 |  | Surge Basin | Surge Basin Treatment Bypassed | See Report | SSO Reached Receiving Water | Wildcat Creek
40050 | 35600 | IN0032875 | KOKOMO MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-11 08:42 |  | 2013-04-11 10:08 | 0 |  | Manhole 987B001 Hylas Morris Ditch | 2.39 inches of Rain the City of Kokomo received 2.39 of rainfall between 7:15am (4/10/13) and 10:15pm (4/11/13). The sewer system for this area is running full causing manhole #987A001 to overflow. | The WWTP has been processing 40.0 MGD since 10:00pm on 4/10/13 | SSO Reached Receiving Water
40050 | 35624 | IN0032875 | KOKOMO MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-04-11 08:42 | 2013-04-11 15:30 | 2013-04-12 07:15 | 0 |  | Manhole 987B001 Hylas Morris Ditch | Rain 2.39 inches Maximum rain intensity during this event was 6.03 in/hr | The City of Kokomo received 2.39 inches of rainfall between 7:15am (4/10/13) and 10:15pm (4/11/13). The sewer system for this area running full causing manhole #987ao overflow. | SSO Affected Private Property
40050 | 39774 | IN0032875 | KOKOMO MUNICIPAL WASTE WATER TREATMENT PLANT | Howard | 2013-08-13 12:30 | 2013-08-13 12:30 | 2013-08-14 05:33 | 0 |  | CSO 041 Outfall Line | Atlas Construction was bypass pumping the combination sewer and the flow exceeded the capacity of their 6 trash pump causing combined sewage to overflow their temporary dam. The sewage entered their work area in which Atlas had a ground water dewatering pump. This pump was set up to pump to the storm line which CSO 041 is attached. | Atlas Construction brought an additional 6 trash pump and began bypassing pumping. This ceased the overflow of the temporary dam. They then shut off the ground water pump and routed all flow to the sanitary sewer. | SSO Reached Receiving Water | Wildcat Creek
45634 | 36547 | IN0058173 | NEW LONDON CONSERVANCY DISTRICT | Howard | 2013-04-18 21:00 | 2013-04-19 14:00 | 2013-04-20 09:59 | 51000 | gallons | Manhole at Lift Station nearest WWTP | Flow resulting from precipitation event(s) exceeded the capacity of the Main Lift Station resulting in partially treated release to surrounding ground. | The pumps in the pump station were operating at maximum capacity. The WWTTP and pump station wer monitored during the event ot insure that they remained in operation. Maximizing flow to and through the WWTP. A review of the area will be completed to detect down spouts and/or sump pumps that may be connected to the sewers and could be sources of extraneous water. | SSO Reached Public Land
32779 | 36296 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-18 19:00 |  | 2013-04-19 10:00 | 0 |  | Manhole at Intersection of Vine Street and Canal Street. SSO #002 | Precipitation event(s) causing river to back up into WWTP preventing discharge. Result is untreated release from manhole to receiving water. |  | SSO Reached Receiving Water | Cow Creek
32779 | 36786 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-18 19:00 | 2013-04-20 00:30 | 2013-05-03 15:36 | 24900 | gallons | Manhole at High and First Streets SSO #003 | Cow Creek out of banks in the area and flooding SSO #002 may have helped to flood system in this area causing overflow. |  | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Cow Creek
32779 | 36785 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-18 19:00 | 2013-04-21 14:00 | 2013-05-03 15:36 | 60300 | gallons | Manhole at intersection of Vine and Canal Streets - SSO# 002 | River backing into WWTP. Could not discharge. Cow Creek out of its banks flooding intersection. Not sure if flow was in or out of the manhole during flooding. |  | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Cow Creek
32779 | 36293 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-18 19:00 |  | 2013-04-19 10:11 | 0 |  | Manhole at intersection of High Street and First Street. SSO #003 | Precipitation event(s) caused river flooding which backed up into WWTP and did not allow discharge. Backup caused untreated release from manhole to receiving water. |  | SSO Reached Public Land; SSO Reached Receiving Water | Cow Creek
32779 | 36297 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-19 05:00 | 2013-04-20 01:00 | 2013-04-20 10:11 | 18000 | gallons | Manhole at intersection of High Street and Vine Street. SSO #005 | Flooding river backing up into WWTP preventing discharge. Result is an untreated release from manhole to receiving water. | follow up report to previous Incident Report #36293 | SSO Reached Receiving Water | Cow Creek
32779 | 36298 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-19 05:00 |  | 2013-04-20 10:11 | 0 |  | Manhole at Intersection of Vine Street and Canal Street. SSO #002 | River flooding backed up into WWTP preventing discharge and resulting in untreated release from manhole to receiving water. Creek has intersection flooded and may be infiltrating sanitary sewer. | Monitoring continues | SSO Reached Receiving Water | Cow Creek
32779 | 36294 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-19 05:00 | 2013-04-20 00:30 | 2013-04-20 00:30 | 17550 | gallons | Manhole at intersection of High Street and First Street. SSO #003 | River backing into WWTP. Not allowing discharge. Result is untreated release from manhole to receiving water. Follow up report. Previous Incident number 36293. |  | SSO Reached Receiving Water | Cow Creek
32779 | 36783 | IN0021440 | Roanoke Municipal Waste Water Treatment Plant | Huntington | 2013-04-19 05:00 | 2013-04-20 01:00 | 2013-05-03 15:36 | 18000 | gallons | Manhole at High and Vine Streets SSO #005 | Precipitation event(s) and flooding resulted in untreated release from manhole to receiving water. Cow Creek out of banks at SSO#2 may have helped to flood system in this area causing overflow. Over 6.5 inches of rain between 4/9 and 4/19. |  | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Cow Creek
29840 | 39958 | IN0023132 | HUNTINGTON WASTE WATER TREATMENT PLANT | Huntington | 2013-08-14 10:36 | 2013-08-14 10:36 | 2013-08-14 13:43 | 0 |  | Facility Bypass | Dry weather bypass construction related an anticipated bypass. Shut down flow to repair line in plant took longer than thought and bypass occurred. | 8-14-2013 1.5 hrs 10:45am - 12:15pm12:15 Plant back on line. | SSO Occurred at Treatment Plant
32974 | 36485 | IN0023736 | MARKLE SEWAGE UTILITY | Huntington | 2013-04-19 00:45 |  | 2013-04-19 14:58 | 0 |  | Equalization Basins at WWTP | Precipitation event(s) and ground water infiltration resulted in untreated overflow from Equalization Basins to receiving waters. | Utilized collection system for storage of excess wastwater as much as possible. On going program to line manholes and sewers. | SSO Reached Receiving Water | Wabash River
32974 | 36441 | IN0023736 | MARKLE SEWAGE UTILITY | Huntington | 2013-04-19 00:46 | 2013-04-21 18:00 | 2013-04-22 15:13 | 582000 | gallons | Equalization Basins Wabash River | Untreated Release Rain 4.20 inches. 4.2 inches of rainfall from 1:00pm 4/28/13 - 7:00 am 4/19/13 resulted in ground water infiltrating sewer lines causing the Equalization Basins to fill to capacity and subsequently bypass untreated wastewater into the Wabash River. Total rainfall event of 7.65 - inches in last 10 days. | Utilized the collection system for storage of excess wastewater as much as possible. On-going program to line manholes and sewers. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Wabash River
35484 | 36389 | IN0061310 | BIPPUS REGIONAL SEWER DISTRICT | Huntington | 2013-04-18 20:00 | 2013-04-19 07:00 | 2013-04-22 00:57 | 0 |  | Effluent Lift Station at WWTP | Precipitation event cause partially treated release from Effluent Lift Station to Receiving waters. No visible release but just by looking at erosion and flow it appears that some sort of washout occurred. UV system was under water. | Shut blowers off at 7:00 PM to prevent solids from leaving plant. Shut off and removed UV system until 4:00 PM on 4/20. Levels and operations back to manageable by that time. Plant operations were closely monitored during the wet weather event. | SSO Reached Receiving Water | Carrol Creek
10781 | 37602 | IN0024473 | EMC SEYMOUR WASTE WATER TREATMENT PLANT | Jackson | 2013-06-03 14:20 | 2013-06-03 14:30 | 2013-06-03 18:11 | 80 | gallons | Force Main Ground Ditch | Untreated Release Equipment Failure | Dug area where discharge was coming from. There was a hole in 6 ductile iron pipe about 3 inch round. When lift station turned on a small amount discharged at hole. Shut off Lift Station while digging and repair. Installed 6 inch light max stainless steel band tested by turning on Lift Station. No leaks. | SSO Affected Private Property
10781 | 39518 | IN0024473 The Higlands Subdivision | EMC SEYMOUR WASTE WATER TREATMENT PLANT | Jackson | 2013-07-01 14:14 | 2013-07-01 14:09 | 2013-07-03 15:00 | 0 |  | Lift Station at Highland Subdivision Ground | Untreated Release | See Report | SSO Affected Private Property
39702 | 40459 | IN0039101 | WATER SERVICES COMPANY OF INDIANA | Jasper | 2013-09-28 12:10 | 2013-09-28 12:10 | 2013-09-28 16:40 | 0 |  | Lake Holiday Camp Ground Lot 195 Manhole | Equipment Failure Plugged Sewer Main Pipe Failure | Remove Blockage See Report | SSO Affected Private Property
39702 | 41140 | IN0039101 | WATER SERVICES COMPANY OF INDIANA | Jasper | 2013-10-21 15:00 | 2013-10-21 18:00 | 2013-10-21 18:30 | 0 |  | 11948 Port Au Price (LOT 196) | Equipment Failure Grease in sewer main | Removed Blockage See Report | SSO Affected Private Property
15861 | 42626 | IN0024406 | Redkey Waste Water Treatment Plant | Jay | 2013-12-21 21:00 | 2013-12-22 10:00 | 2013-12-22 14:00 | 0 |  | Numerous Manholes Throughout Town | Rain >3.0 inches. Severe flooding throughout Redkey Jay County and the state due to large amount of snow melt 6 on the ground that began on 12/19/13. had .390 of rainfall on 12/20/2013 then had a total of 2.97 of rain on 12/21/13 with 1.74 of that total coming after 7:00pm which was the last time I checked various problem areas throughout town. The system was surcharged but not spilling at any manholes and the plant was not spilling over at the time. At 9:00pm receiving stream was out of it s banks. See Attached Page | See Report | SSO Reached Public Land; SSO Affected Private Property; SSO Occurred at Treatment Plant | Redkey Run
15861 | 42627 | IN0024406 | Redkey Waste Water Treatment Plant | Jay | 2013-12-21 21:00 | 2013-12-22 11:00 | 2013-12-22 14:00 | 0 |  | Plant Bypass | Rain >3.0 inches Severe flooding throughout Redkey Jay County and the State due to large amount of snow melt 6 on the ground that began on 12/19/13. Had .390 of rainfall on 12/20/13 then had a total of 2.97 of rain on 12/21/13 with 1.74 of that total corning after 7:00pm which was the last time I checked various problem areas throughout town. The system was surcharged but not spilling at any manholes an the plant was not spilling over at that time. At 9:00pm receiving stream was out of it s bank. See Attachment | See Report |  | Redkey Run
11954 | 39501 | 25666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-02 10:00 | 2013-07-02 10:30 | 2013-07-02 15:30 | 0 |  | 1440 Crozier Ave MH 6-F3-18 | Rain 1.43 inches Manhole blocked caused sanitary sewer to back up into basement. Sump pump in basement pump sewage into the yard. | See Report | SSO Reached Receiving Water | Ohio River
41641 | 36529 |  | HANOVER COLLEGE | Jefferson | 2013-04-14 | 2013-04-14 06:00 | 2013-04-14 17:07 | 5000 | gallons | 413 Ball Drive Hanover IN 47243 Ground Storm Sewer | Untreated Release Equipment Failure Sewer line blockage caused a backup and overflow at manhole. Four buildings housing 150 students feed into line. Approximately 5300 square feet of ground and asphalt surface were affected by the overflow. The flow reached a storm drain in the parking area located approximately 230 feet from the manhole. A public safety employee noticed the parking lot was wet around midnight and then checked around 2:30AM to find a steady flow from the manhole. Our on call maintenance personnel was not contacted until 5:42AM. once on site the Maintenance Supervisor reported the flow had stopped and the manhole was full. The town of hanover was contacted to utilize their power jet to clear the blockage. | About half of the contaminated area was a grassy section and 80 pounds of pulverized lime was dispersed to neutralize the spill. the rest covered and asphalt parking lot which was sprayed with a 10% bleach solution to disinfect the area. The locate health department was contacted around 9AM and we received verbal recommendations: not further action was required as not food service areas or inhabited buildings were impacted. Review emergency Spill Plan Procedures with pertinent employees. | SSO Affected Private Property; Storm Sewer
41641 | 42098 |  | HANOVER COLLEGE | Jefferson | 2013-11-21 | 2013-11-21 16:35 | 2013-11-19 15:20 | 0 |  | ClassicHall 608 Caollege Ave Hanover IN 47243 | Equipment Failure Sewer line blockage/pipe collapse caused a backup and overflow into the crawl space of Classic Hall. The flow was contained in the crawl space but given the amount of sewage the ground beneath the building was completely saturated. Approximately 1500 square feet of ground surface beneath the building was affected by the overflow. | Repaired Pipe See Report | SSO Basement Backup
41085 | 35793 | IN0020702 | HANOVER WASTE WATER TREATMENT PLANT | Jefferson | 2013-04-12 | 2013-04-12 | 2013-04-15 06:53 | 20 | gallons | 2419 Lohege Hills Hanover In 47353 Down very steep hill and yard | Untreated Release Equipment Failure Small hole in coupling/firm co. Had to pump out hole to fix coupling/firm co | Dug up and fixes on site 50 pounds of lime spread on ground. | SSO Affected Private Property
11954 | 35938 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-01-11 07:00 | 2013-01-11 11:45 | 2013-01-11 15:33 | 230000 | gallons | City of Madison - WPCF | Precipitation event triggered an overflow in the WWTP resulting in recombining and sampling of effluent before release to receiving waters. |  | SSO Occurred at Treatment Plant | Ohio River
11954 | 35865 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-01-13 04:55 | 2013-01-14 00:45 | 2013-01-14 12:03 | 2280000 | gallons | Wastewater Treatment Plant | Precipitation and saturated ground combined to trigger a blended release from the WWTP to receiving waters | LTCP | SSO Reached Receiving Water | White River
11954 | 35859 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-01-13 16:30 | 2013-01-13 20:30 | 2013-01-14 15:00 | 1000 | gallons | several manholes | Precipitation event and saturated ground resulted in untreated release from manholes to surrounding ground. | Cleaned up area around manhole. LTCP | SSO Reached Public Land
11954 | 35038 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-01-30 05:30 | 2013-01-30 21:30 | 2013-01-31 13:40 | 1293570 | gallons | City of Madison WPCF Madison IN | Heavy rain fall with already saturated ground caused an overflow at the WWTP that was blended with the final effluent and sampled. | None | SSO Occurred at Treatment Plant | Ohio River
11954 | 35211 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-01-30 08:00 | 2013-01-30 10:30 | 2013-01-30 15:11 | 1000 | gallons | Madison IN | Precipitation event caused untreaded release from several manholes in Madison IN. | Cleaned up area around manholes. LTCP | SSO Reached Public Land
11954 | 34860 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-02-22 07:30 | 2013-02-22 15:00 | 2013-02-23 08:30 | 2000 | gallons | Water Pollution Control Facility Madison IN | Precipitation caused an overflow that was blended with final effluents and sampled. | None | SSO Occurred at Treatment Plant | Ohio River
11954 | 34743 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-02-26 15:00 | 2013-02-26 21:25 | 2013-02-27 10:00 | 430000 | gallons | City of Madison WPCF | Precipitation event casued an overflow that was blended with the final effluent and tested. .75 inch rainfall | Overflow was blended with final Effluent and tested. | SSO Reached Receiving Water | Ohio River
11954 | 34617 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-03-05 17:50 | 2013-03-05 21:45 | 2013-03-06 | 130000 | gallons | City of Madison WPCF Ohio River | Blended with final effluent & sampled rain 0.57 Rain and snow melt with already saturated ground. |  | SSO Reached Receiving Water | Ohio River
11954 | 34481 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-03-11 04:55 | 2013-03-11 23:05 | 2013-03-11 23:05 | 1910 | gallons | Wastewater Treatment Plant Ohio River | Blended with final effluent & sampled Rain 1.41 inches. Overflow due to heavy rains & heavily saturated ground. | Nothing done LTCP | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Ohio River
11954 | 34462 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-03-11 08:30 | 2013-03-11 15:00 | 2013-03-12 15:00 | 10000 | gallons | Several Manholes Ground | Untreated Release Precipitation 1.41 inches. heavy rainfall with already saturated ground. | Cleaned up around manholes LTCP | SSO Affected Private Property
11954 | 34779 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-03-12 10:25 | 2013-03-12 10:30 | 2013-03-13 | 360 | gallons | Wastewater Treatment Plant | Blended with Final Effluent & Sample and already heavy saturated system. | No damage LTCP | SSO Reached Receiving Water | Ohio River
11954 | 34909 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-03-18 00:05 | 2013-03-18 18:50 | 2013-03-19 08:45 | 2020000 | gallons | City of Madison WPCF | Blended with final effluent & sampled Rain 1.74 inches Heavy rain fall of 1.76 inches over long period of time with already saturated ground. |  | SSO Reached Receiving Water | Ohio River
11954 | 34907 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-03-18 07:30 | 2013-03-18 14:30 | 2013-03-19 09:30 | 75000 | gallons | Several Manholes Ground | Untreated Release Rain 1.76 inches Heavy rainfall with already saturated ground. | Cleaned up around manholes LTCP | SSO Affected Private Property
11954 | 35359 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-11 08:30 | 2013-04-11 22:50 | 2013-04-12 09:00 | 230000 | gallons | City of Madison W.P.C.F | Blended with Final Effluent & Sampled - Precipitation 1.06 Inches | None | SSO Reached Receiving Water | Ohio River
11954 | 35360 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-12 00:30 | 2013-04-12 07:30 | 2013-04-12 09:00 | 260000 | gallons | City of Madison W.P.C.F. | Blended with Final Effluent & Sampled - Precipitation 0.24 Inches | Heavy rain overnight of 0.24 inches with 1.06 inches the day before and already saturated ground. | SSO Reached Receiving Water | Ohio River
11954 | 36043 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-16 19:00 | 2013-04-17 13:15 | 2013-04-18 10:10 | 1470000 | gallons | City of Madison WPCF | Precipitation event along with already saturated ground resulted in a release of Blended and sampled final effluent to receiving waters. |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Ohio River
11954 | 36530 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-19 03:20 | 2013-04-19 15:40 | 2013-04-20 08:20 | 850000 | gallons | City of Madison WPCF Ohio River | Blended with Final effluent & Sampled Rain 1.1 inches Heavy rain fall of 1.1 inches with already saturated ground. |  | SSO Reached Receiving Water | Ohio River
11954 | 36490 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-19 03:20 | 2013-04-19 15:40 | 2013-04-20 08:20 | 0 |  | City of Madison WPCF Ohio River | Blended with Final Effluent & Sampled Heavy rain fall of 1.1 inches with already saturated ground. |  | SSO Reached Receiving Water | Ohio River
11954 | 36489 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-19 07:00 | 2013-04-19 08:30 | 2013-04-19 15:07 | 1000 | gallons | Manhole at 1440 Cragmont Street MH5-F5-98A | Precipitation event along with saturated ground resulted in SSO and untreated release to surrounding ground. | Cleaned up around manhole. Sedam Contrators to replace the manhole with a larger diameter manhole with bolt down watertight lid. | SSO Reached Public Land
11954 | 36492 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-19 07:00 | 2013-04-19 08:30 | 2013-04-19 15:07 | 1000 | gallons | 1524 Cragmont Street MH5-F5-97 | Precipitation event coupled with saturated ground resulted in untreated release from manhole to surrounding ground. | Cleaned up around manhole.Sedam Contractors to replace the manhole with a larger diameter manhole with bolt down water tight lid. LTCP | SSO Reached Public Land
11954 | 36623 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-04-24 07:25 | 2013-04-24 16:05 | 2013-04-25 10:00 | 500000 | gallons | City of Madison WPCF | High flow due to precipitation event(s) resulted in release that was blended with final effluent and sampled before discharge to receiving water. |  | SSO Reached Receiving Water | Ohio River
11954 | 36788 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-05-05 09:25 | 2013-05-06 14:50 | 2013-05-06 15:40 | 1820000 | gallons | City of Madison WPCF | Flow from precipitation event exceeded capacity of WWTP and resulted in treatment bypass and partially treated blended release to receiving water. | bypass effluent was recombined with final effluent and sampled prior to discharge to receiving water. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Ohio River
11954 | 36789 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-05-05 17:00 | 2013-05-05 18:00 | 2013-05-06 14:00 | 500 | gallons | 142 Irish Hollow Lane - MH5-F7-24A | Flow from precipitation event resulted in an untreated release from a manhole to surrounding ground. | Cleaned up around manhole and have Sedam Contractions seal around the concrete manhole and casting.LTCP | SSO Reached Public Land
11954 | 36854 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-05-10 12:55 | 2013-05-11 11:35 | 2013-05-11 13:00 | 1650000 | gallons | City of Madison WPCF Ohio River | Blended with Final Effluent & Sampled Rain 1.10 inches Steady rain fall of 1.10 inches starting at 10:30am |  | SSO Reached Receiving Water | Ohio River
11954 | 36842 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-05-10 14:30 | 2013-05-10 18:30 | 2013-05-11 13:30 | 7000 | gallons | 1524 Cragmont St MH5-F5-97 Ground | Untreated Release Rain 1.10 inches Steady rain fall of 1.10 inches starting at 10:30am with already saturated ground. | Cleaned up around manhole and Sedam Contraction is going to replace the manhole with a larger diameter manhole with a bolt down waletight lid asap. LTCP | SSO Affected Private Property
11954 | 36841 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-05-10 14:30 | 2013-05-10 18:30 | 2013-05-11 13:30 | 7000 | gallons | 1440 Cragmont St MH5-F5-98A Ground | Untreated Release Rain 1.10 inches Steady rain fall of 1.10 inches starting at 10:30am with already saturated ground. | Cleaned up around manhole and Sedam Contraction is going to replace the manhole with a larger diameter manhole with a bolt down watertight lid asap. LTCP | SSO Affected Private Property
11954 | 36849 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-05-10 14:30 | 2013-05-10 15:00 | 2013-05-11 14:00 | 200 | gallons | 112 S Grange Hall Rd MH# 001 Ground | Untreated Release Rain 1.10 inches Pump failure at the pump station got the pump back on line. | Cleaned up around the manhole going to call Xylem on Monday to look at the pump and to see what repairs are needed. | SSO Affected Private Property
11954 | 37090 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-05-22 18:40 | 2013-05-22 19:45 | 2013-05-23 10:00 | 3000 | gallons | City of Madison WPCF Ohio River | Blended with Final Effluent & Sampled Rain 0.5 inches Heavy rain fall of 0.5 in a very short time. | Long Term Control Plan | SSO Reached Receiving Water | Ohio River
11954 | 37751 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-05 14:30 | 2013-06-05 15:00 | 2013-06-05 16:30 | 200 | gallons | 1932 Falls Blvd. MH#2-F4-8 | Equipment Failure Pipe Failure Blockage in gravity line. | Cleaned up area around the M.H. and put lime down on both sides of the street. Going to look at repairing the pipes in this area. | SSO Reached Public Land
11954 | 38898 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-26 06:15 | 2013-06-26 07:00 | 2013-06-26 08:40 | 0 |  | WPCF | Bypass/O is blended with final effluent at disinfection point. | See Report LTCP | SSO Reached Receiving Water
11954 | 38379 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-26 17:30 | 2013-06-27 01:10 | 2013-06-27 11:40 | 307000 | gallons | WPCF Secondary Treatment Bypassed. | Rain 1.74 inches Bypass /Overflow is blended with final effluent at disinfection point. | None LTCP | SSO Reached Receiving Water | Ohio River
11954 | 38360 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-29 17:00 | 2013-06-29 22:30 | 2013-06-30 11:00 | 318000 | gallons | WPCF | Rain 1.06 inches. Bypass/overflow is blended with final effluent disinfected and sampled. Overflow was due to heavy rain with already saturated ground. | None LTCP | SSO Reached Receiving Water | Ohio River
11954 | 38272 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-29 17:30 | 2013-06-29 18:00 | 2013-06-30 14:30 | 0 |  | 1526 Cragmont St MH5-F5-96A | Rain 1.06 inches Manhole Overflow was due to heavy rain with already saturated ground. | Cleaned up area around the M.H. and put lime down. Sedam Contraction video the line. Found a blockage in the line after they put in the new manholes. They are going to open the line up this week and take out the blockage. | SSO Reached Public Land
11954 | 38362 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-29 17:30 | 2013-06-29 18:00 | 2013-06-30 14:30 | 0 |  | 1440 Cragmont St MH5-F5-98A | Rain 1.06 inches Overflow was due to heavy rain with already saturated ground. | Cleaned up area around the M.H. and put lime down. Sedam Contraction video the line. Found a blockage in the line after they put in the new manholes in. They are going to open the line up this week and take out the blockage. | SSO Reached Public Land
11954 | 38364 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-30 19:40 | 2013-07-01 01:30 | 2013-07-01 08:45 | 453000 | gallons | Treatment Plant | Rain 1.56 inches Bypass/overflow is blended with final effluent disinfected and sampled. | None LTCP | SSO Reached Receiving Water | Ohio River
11954 | 38365 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-30 20:30 | 2013-06-30 21:30 | 2013-07-01 14:30 | 0 |  | 1526 Cragmont St MH5-F5-96A | Rain 1.56 inches Overflow was due to heavy rain with already saturated ground. | Cleaned up area round the MH and put lime down. Sedam Contraction video the line. Found blockage in the line after they put in the new manholes in. They are going to open the line up this week and take out the blockage. | SSO Reached Public Land
11954 | 38366 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-06-30 20:30 | 2013-06-30 21:30 | 2013-07-01 13:30 | 0 |  | 1440 Cragmont St MH5-F5-98A | Rain 1.56 rain Overflow was due to heavy rain with already saturated ground. | Cleaned up area around the MH and put lime down. Sedam Contraction video the line. Found a blockage in the line after they put in the new manholes in. They are going to open the line up this week and take out the blockage. | SSO Reached Public Land
11954 | 39500 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-01 21:00 | 2013-07-02 09:50 | 2013-07-02 15:00 | 0 |  | WPCF Secondary Treatment Bypassed | Rain 1.43 inches Exceeded max Capacity Bypass/Overflow is blended with final effluent disinfected and sampled. Heave rain fall of 1.43 in a short time already saturated ground with a total rain fall of 4.08 in the last four days | See Report | SSO Reached Receiving Water | Ohio River
11954 | 39507 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-02 02:30 | 2013-07-02 03:30 | 2013-07-02 15:30 | 0 |  | 1526 Craigmount MH 5-F5-96A | Rain 143 inches Overflow due to heavy rain of 1.43 in a short time already saturated ground with a total rain fall of 4.08 in the last four days. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 39502 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-02 02:30 | 2013-07-02 03:30 | 2013-07-02 15:30 | 0 |  | 1440 Craigmount St MH 5-F5-98A | Rain 1.43 inches Overflow due to heavy rain of 1.43 in a short time already saturated ground with a total rain fall of 4.08 in the last four days. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 39496 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-06 06:30 | 2013-07-06 16:40 | 2013-07-07 11:00 | 0 |  | WPCF Secondary Treatment Bypassed | Exceeded Max Capacity Bypass/Overflow is blended with final effluent disinfected and sampled. Heavy rain fall with already saturated ground. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 39547 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-09 09:30 | 2013-07-09 11:00 | 2013-07-11 08:07 | 0 |  | 603 Green Rd MH #5-F5-51 | Equipment Failure Blockage in gravity line. | Removed Blockage | SSO Reached Public Land
11954 | 39549 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-09 09:30 | 2013-07-09 11:00 | 2013-07-11 08:08 | 0 |  | 603 Green Rd MH #5-F5-51 | Equipment Failure Blockage in gravity line Pipe failure | Removed Blockage | SSO Reached Public Land
11954 | 39552 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-07-10 15:15 | 2013-07-10 17:15 | 2013-07-11 15:45 | 0 |  | WPCF | Rain 0.28 inches Bypass/Overflow is blended with final effluent disinfected and sampled. Heavy rain in a short time with already saturated ground. | See Report |  | Ohio River
11954 | 39762 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-08-09 12:23 | 2013-08-09 02:35 | 2013-08-09 15:20 | 0 |  | City of Madison WPCF | Rain 1.01 inches Exceeded Max Capacity Bypass/Overflow is blended with final effluent disinfected and sampled. Heavy rain fall of 1 of rain. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 39933 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-08-31 18:00 | 2013-08-31 22:55 | 2013-09-01 13:00 | 0 |  | WPCF | Rain 1.65 inches Bypass/overflow is blended with final effluent disinfected and sampled. Heavy amount of rain in a short time. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 40316 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-09-21 10:58 | 2013-09-21 01:40 | 2013-09-23 08:32 | 0 |  | WPCF | Bypass/Overflow is blended with final effluent disinfected and sampled. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 40839 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-10-06 09:00 | 2013-10-06 11:00 | 2013-10-07 14:45 | 0 |  | 1510 Washington Ave | Construction Related Rain 4.46 inches The sewer line at Terrace Drive is undergoing construction to prevent future SSO s. The Contractor had busted the 12 sewer and had made a temporary repair. During the heavy volume of rain that fell late Saturday night through Sunday the repair failed to hold releasing approximately 100000 gallons of sewage. | Repaired Pipe See Report | SSO Reached Public Land
11954 | 41375 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-10-27 12:30 | 2013-10-27 13:00 | 2013-10-28 12:30 | 0 |  | 2520 Franks Dr. | The M-7 lift station at franks dr. Both pumps failed because they both had wads of rags in the impellers. Pulled both pumps resat back on line. | Cleaned up area around the lift station. Going to put in a OminiSite Viper to call us out when a pump fails. | SSO Reached Public Land
11954 | 41373 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-10-28 09:00 | 2013-10-28 09:30 | 2013-10-28 13:15 | 0 |  | 1013 W 1st MH 1-3-801 | Equipment Failure the sewer line at 1013 w 1st had a blockage. The city flush and cleaned the line. | Repaired Pipe See Report | SSO Reached Public Land
11954 | 41642 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-10-31 20:40 | 2013-11-01 14:40 | 2013-11-01 13:46 | 0 |  | Water pollution Control Facility | Exceeded Max Capacity Rain 0.9 inches Bypass/Overflow is blended with final effluent and disinfected. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 38661 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-11-17 07:20 | 2013-11-18 10:59 | 2013-11-18 15:37 | 56 | gallons | Water Pollution Control Facility | Rain 2.1 inches Bypass/Overflow is blended with final effluent at disinfection point. Due to heavy rain fall of 2.1 inches. | See Report. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Ohio River
11954 | 43285 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-21 11:49 | 2013-12-21 15:30 | 2013-12-21 19:03 | 100000 | gallons | 1510 Washington Ave | Rain 1.34 inches The sewer line at Terrace Drive is undergoing construction to prevent future SSOs. The contractor could not repair line due to a Cease to Work Order by Court. Because property owner filled saying we had no utility easement for work. During the heavy volume of rain that fell Saturday. Releasing approximately 10000 gallons of sewage. | Repaired Pipe | SSO Reached Public Land
11954 | 43258 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-21 23:30 | 2013-12-21 13:30 | 2013-12-21 18:00 | 0 |  | 142 Irish Hollow In MH%-F7 24A | Exceeded Max Capacity Rain 1.34 inches Heavy rainfall with already saturated ground. | See Report | SSO Affected Private Property
11954 | 43283 | IN0025666 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-21 23:30 | 2013-12-21 13:30 | 2013-12-21 19:03 | 1000 | gallons | 112 S Grange Rd MH #001 | Exceeded Max Capacity Rain 1.34 inches Heavy rainfall with already saturated ground. | See Reports | SSO Affected Private Property
11954 | 41078 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-10-05 22:02 |  | 2013-10-06 12:30 | 0 |  | Secondary Treatment Bypassed | Rain Bypass/Overflow is blended with final effluent at disinfection point. Note: Complete report to follow. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 41079 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-10-05 22:02 | 2013-10-06 21:20 | 2013-10-07 14:15 | 0 |  | Water pollution Control Facility | Bypass?overflow is blended with final effluent at disinfection point. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 41941 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-11-17 07:25 |  | 2013-11-17 12:15 | 0 |  | Water Pollution Control facility | Rain Bypass/Overflow is blended with final effluent disinfected and sampled. Bypass started at 7:25 am 11-17-13. Follow-up report to bypass will be filed after event. | See Report |  | Ohio River
11954 | 42550 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-14 11:00 | 2013-12-14 23:03 | 2013-12-15 10:45 | 0 |  | Water Pollution Control Facility | Bypass/Overflow is blended with final effluent at disenfection point. The overflow was due to rain fall and heavy snow melt. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 43252 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-21 08:15 |  | 2013-12-21 19:04 | 0 |  | Water Pollution Control Facility | Exceeded Max Capacity Rain 1.34 bypass?Overflow is blended with final effluent at disinfection point. The overflow started at 8:15am . There will be a follow-up report at a later date. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 43259 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-21 10:00 | 2013-12-21 12:30 | 2013-01-21 17:45 | 5000 | gallons | Flint St MH 6-F2-111A | Euipment Failure Rain 1.34 inches MH 6-F2-111 overflowed due to down stream lift station Failure. Manhole over flowed into store water ditch which leand to Cliffty Creek | See Report | SSO Reached Receiving Water
11954 | 43250 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-22 07:30 | 2013-12-22 11:30 | 2013-12-22 18:45 | 100000 | gallons | 1510 Washington Ave. | Rain 2.52 inches Contractor could not repair pipe due to cease to Work Order from Court Property owner filled saying there was no utility easement. Water flowed into a storm water ditch that leads to crooked creek. | Repaired Pump Station | SSO Affected Private Property; SSO Reached Receiving Water
11954 | 43162 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-22 15:00 | 2013-12-22 15:30 | 2014-12-22 13:06 | 0 |  | Hanna Dr L/S #M-07 | Equipment Failure Rain 2:52 Inches Lift Station overflowed due to a pump tripped out and the other pump could not keep up with flow. | Repaired Pump Station | SSO Affected Private Property
11954 | 43149 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-26 07:00 | 2013-12-26 10:00 | 2013-12-26 14:04 | 0 |  | L/S # M-07 Hanna Dr. | Equipment Failure while checking Hanna Drive Lift Station I noticed it overflowing and when I opened the control panel I found pump number one in the off position I turned pump one back on and pumped the station down. | Repaired Pump Station | SSO Affected Private Property
11954 | 43148 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-29 | 2013-12-29 13:25 | 2013-12-30 11:00 | 138 | gallons | Water Pollution Control Facility | Exceeded Max Capacity Rain 0.35 inches. Bypass /Overflow is blended with final effluent at disinfection point. Rain fall of .35 with already saturated ground. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 43147 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-21 08:10 | 2013-12-23 01:00 | 2013-12-24 15:00 | 3 | gallons | Water Pollution Control Facility | Rain 2.72 inches Exceeded max Capacity Bypass/Overflow is blended with final effluent at disinfection point. Heavy rain fall of 2.72 over a long period with snot melt and saturated ground. | See Report | SSO Reached Receiving Water | Ohio River
11954 | 43150 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-22 07:45 | 2013-12-22 08:30 | 2013-12-22 13:06 | 2000 | gallons | Flint St MH 06-F11A | Equipment Failure Rain 2.52 inches Flint St MH 06-F2-11A | Repaired Pump Station | SSO Reached Receiving Water | Clifty Creek
11954 | 43161 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-22 10:30 | 2013-12-22 01:00 | 2013-12-22 18:45 | 2000 | gallons | Hanna Dr L/S #M-07 | Equipment Failure Rain 2.52 inches Lift Station overflowed due to a pump tripped out and the other pump could not keep up with flow. | Repaired Pipe | SSO Affected Private Property
11954 | 43287 | IN0025666 Outfall 001 | Madison Waste Water Treatment Plant | Jefferson | 2013-12-25 10:00 | 2013-12-25 10:30 | 2013-12-25 19:09 | 1000 | gallons | L?S # M-07 Hanna Dr. | Equipment Failure Pumps tripped out. We reset pumps and they started. We are calling Xylem to have them trouble shoot the pumps and controls 12/26/13 | Repaired Pump Station | SSO Affected Private Property
11954 | 43146 | IN0025666 Outfall 001 LAT/LONG ARE INVALID | Madison Waste Water Treatment Plant | Jefferson | 2013-12-24 10:00 | 2013-12-24 10:30 | 2013-12-24 15:00 | 1000 | gallons | Hanna Dr Lift Station | Equipment failure pumps tripped out due to debris in pump. Removed debris and reset pumps. LS#M-07 | See Report | SSO Affected Private Property
16146 | 35165 | IN0020451 | NORTH VERNON WASTE WATER TREATMENT PLANT | Jennings | 2013-01-31 05:00 | 2013-01-31 07:30 | 2013-01-31 16:20 | 0 |  | North Vernon Wastewater Treatment Plant North Vernon IN | Power outage spike caused 110 volt transformer to fail. Power was for the pumps on the aeration tanks. Result was an Untreated Release to the Muscatatuck River | Ran power to the pump controller to get pumps running and stop overflow. Replaced transformer. | SSO Reached Receiving Water | Muscatatuck River
16146 | 34947 | IN0020451 | NORTH VERNON WASTE WATER TREATMENT PLANT | Jennings | 2013-03-18 06:00 | 2013-03-18 09:00 | 2013-03-18 04:21 | 0 |  | Northwest Lift Station Unnamed drainage swale | Untreated Release Rain 1.3 inches. The sewer drainage basin received a total of 1.3 inches of rain in a hour period. The rainfall created flows that exceeded the pump station s capacity. The Muscatatuck River flow increased from the dry weather flow of 80 CFS to a wet weather flow of 9000 CFS due to the rainfall event. Overflows had a negligible impact on the Muscatatuck River. | This pump station is in LTCP to stop these over flows. | SSO Reached Receiving Water | Muscatatuck River
16146 | 43290 | IN0020451 | NORTH VERNON WASTE WATER TREATMENT PLANT | Jennings | 2013-12-22 | 2013-12-22 09:30 | 2013-12-22 15:15 | 0 |  | North east Lift Station | Power Failure Rain 3.20 inches Sewer Drainage basin received over 3.20 inch of rain in 7 hour period. And also lost power to the lift station. The Muscatatuck River increased from a dry weather flow of 100cfs to a wet weather flow of 12500 cfs during this event. We hook up our Generator and the overflow stop with in 15 min. | See Report | SSO Reached Receiving Water | Muscatatuck River
16146 | 38899 | IN0020451 Unnamed drainage swale to Muscatatuck River | NORTH VERNON WASTE WATER TREATMENT PLANT | Jennings | 2013-06-26 11:49 | 2013-06-26 11:49 | 2013-06-27 09:15 | 0 |  | Southwest Lift Station 1695 Quaker Hill Subdivision North Vernon | Sewer Drainage basin received over 1.5 inch of rain in 1 hour period. The rainfall created flow that exceeded the pump station s capacity. The Muscatatuck River increased from a dry weather flow of 100cts to a wet weather flow of 8000 cfs during this event | The lift station is in LTCP to take of these overflow | SSO Reached Receiving Water | Muscatatuck River
13759 | 42630 | 0022314 Outfall 001 | Bargersville Water Utilities | Johnson | 2013-12-21 21:45 | 2013-12-22 03:00 | 2013-12-22 14:19 | 0 |  | Manhole #1-20 | Rain 3.0 inches We had put in place the measures that had proved adequate in the past rain event. This was a unusual rain event. | See Report
13906 | 43304 | IN0020966 | NEW WHITELAND WASTE WATER TREATMENT PLANT | Johnson | 2013-12-21 08:30 | 2013-12-22 02:00 | 2013-12-22 04:06 | 1500000 | gallons | 324 W 500 N New Whilteland In 46184 Sanitation Station Retention Pond | Rain 5.16 inches Plants did not bulk do solids lost from plant. | See Report | SSO Affected Private Property
13906 | 43295 | IN0020966 | NEW WHITELAND WASTE WATER TREATMENT PLANT | Johnson | 2013-12-30 10:00 | 2013-12-20 10:15 | 2013-12-30 23:50 | 50 | gallons | Manhole between 845-851 Middle Dr Storm Sewer | Blockage in main sewer. | See Report
13906 | 36799 | IN0021415 | NEW WHITELAND WASTE WATER TREATMENT PLANT | Johnson | 2013-05-09 | 2013-05-09 12:00 | 2013-05-09 12:13 | 0 |  | Lift Station Ground around Lift Station | Equipment Failure We had outside contractor working at Lift Station and left main power off. | Spray down area and lime it. Talk with contractor to make sure it don t happen again. | SSO Affected Private Property
13906 | 43299 | IN0021415 | NEW WHITELAND WASTE WATER TREATMENT PLANT | Johnson | 2013-12-21 13:00 |  | 2013-12-21 18:36 | 0 |  | Manhole at treatment plant Brewer Ditch | Rain 2.87 inches Too uch flow in system for plant to keep up. | See Report | SSO Reached Receiving Water | Brewer Ditch
13759 | 35769 | IN0022314 | Bargersville Water Utilities | Johnson | 2013-01-13 00:30 | 2013-01-13 06:46 | 2013-01-14 19:47 | 4000 | gallons | Manhole #1-20 | Untreated release leaking from pick hole on mh cover to storm sewer inlet. | Used emergency pump in plant main lift station to reduce surcharge in sewer collection main. Pumped to EQ pond. Start emergency pump before surcharge progresses to this degree | SSO Reached Public Land; Storm Sewer
13759 | 41563 | IN0022314 Outfall 001 | Bargersville Water Utilities | Johnson | 2013-11-02 08:00 | 2013-11-03 07:00 | 2013-11-03 18:30 | 0 |  | Gravel parking lot Air bleed off valve | A 3/4 inch bleed off value was left on. When the level in the sludge storage tank got above it it began to leak. very low volume but being on the weekend was not caught till weekend rounds was made. | See Report | SSO Occurred at Treatment Plant
32782 | 40801 | IN0024970 Outfall 001 | OAK MEADOWS MOBILE HOME COMMUNITY | Johnson | 2013-08-12 14:00 |  | 2013-10-07 14:30 | 0 |  | Treatment Facility Clarifier through Polishing pond Bypass to Outfall 001 | On Monday August 12th the polishing pond of the wastewater treatment system serving the Oak Meadows MHP was taken out of service for cleaning. The pond has had issues with algae contaminating final effluent samples and causing erroneous final effluent Total Suspended Solids (TSS) violations. | There is no damage to mitigate. Secondary effluent samples collected have confirmed that water leaving the treatment facility clarifier is well below permit levels. Water from the clarifier then goes through Chlorine disinfection tablet feeders; to tablet feeders that remove excessive Chlorine residual; and finally to the polishing pond. The polishing pond is the only treatment unit being bypassed; as such water leaving the treatment facility is fully treated and below permit limits. Once the polishing pond is free of algae the bypass will cease; IDEM will be notified; and the plant will return to normal operation. | SSO Reached Receiving Water | Travis Creek
33012 | 43292 | IN0040681 | Trafalgar Waste Water Treatment Plant | Johnson | 2013-12-21 19:05 | 2013-12-22 23:30 | 2013-12-23 10:00 | 3000 | gallons | Manhole #136 | Equipment Failure Manhole #136 started overflowing due to VFD failure in the pump station the pumps were switched into bypass mode to allow them to run at maximum capacity. | Repaired Pump Station | SSO Affected Private Property
29633 | 35589 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-01-07 | 2013-01-07 12:30 | 2013-01-07 14:54 | 0 |  | 121 Marlin Drive | Grease blockage in main line resulted in untreated release from manhole to ground surrounding manhole. Unpermitted. | Jetted lin open and vacuumed up water around manhole. | SSO Reached Public Land
29633 | 35630 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-01-13 05:30 | 2013-01-13 18:45 | 2013-01-14 16:46 | 0 |  | manholes located on Valley Lane Bomar Lane Fairview Road and Leisure Lane. | Precipitation event caused untreated non permitted release from multiple manholes to receiving waters. | Areas affected have been cleaned. SSES planned to begin in 2013 | SSO Reached Receiving Water | Pleasant Run Creek
29633 | 35883 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-01-13 09:06 | 2013-01-13 10:00 | 2013-01-14 15:46 | 0 |  | 4070 Serenity Way Court | Precipitation event filled sewer lines which resulted in an untreated non permitted release to a residential basement. | Homeowner cleaned up spill in basement. | SSO Basement Backup
29633 | 35663 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-04-02 | 2013-04-02 16:00 | 2013-04-09 12:08 | 0 |  | 543 N SR135 Fomp sump pump basement | Untreated Release Sewer backed up through sump pump in basement. | Found broken sewer line replace 70ft of sewer line from MH W-26-78 to MH W-26-79 | SSO Basement Backup
29633 | 36063 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-04-16 | 2013-04-16 23:45 | 2013-04-18 09:03 | 10 | gallons | 250 Main Street and SR 135 | Main sewer blockage resulted in untreated non permitted release from manhole to surrounding ground. | Cleaned up around manhole with vac truck. | SSO Reached Public Land
29633 | 36062 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-04-17 20:50 | 2013-04-17 21:15 | 2013-04-18 09:02 | 5 | gallons | 326 Gooseberry Lane | Main sewer blockage caused an untreated non permitted release to the sidewalk. | Used root saw on line. TV the line and looking at replacing the line. | SSO Reached Public Land
29633 | 37366 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-06-03 | 2013-06-03 15:15 | 2013-06-04 09:08 | 0 |  | Manhole W-36-127 ran across the ground 50 ft. Main St and Stoney Brook Dr to small ditch into Brookstone detention pond. | Untreated Release Blocked maid sewer line 8 sewer water seeping out around lid. | Reported it to Johnson county Health Dept put sign s up around detention pond vac and clean up around manhole. Posted warning signs around Pond. Clean and TV the system check for manhole lid off or broken pipe. | SSO Affected Private Property
29633 | 40441 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-09-25 11:00 | 2013-09-25 17:30 | 2013-09-26 10:56 | 0 |  | 1280 US 31 N Manhole | Contain sewage in storm pipe 100ft | See Report | SSO Affected Private Property
29633 | 41403 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-10-28 22:00 | 2013-10-28 22:50 | 2013-10-30 09:23 | 0 |  | 355 Fry Road Clean Out | Construction Related Poindexter Construction broke lateral doing construction on new Good Will Store | Removed Blockage Repaired Pipe | SSO Basement Backup
29633 | 43293 | IN0046370 - Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-12-27 23:00 | 2013-12-29 04:00 | 2013-12-27 08:26 | 0 |  | MH P-32-162 | Exceeded Max Capacity Rain 5 inches Overflow do to five inch major rain event overloading sanitary system. | See Report | SSO Reached Receiving Water | Pleasant Run Creek
29633 | 36790 | IN0046370 -Terminated | GREENWOOD SANITATION DEPARTMENT | Johnson | 2013-05-07 | 2013-05-07 15:58 | 2013-05-08 09:20 | 0 |  | 1873 Drexal Court Manhole | Blockage in sewer line resulted in an untreated release to surrounding ground. | Found test ball in line from new construction. Cleaned up around manhole. Removed test ball.Inspector is going to note manholes that have test balls in them and before we accept lines the test ball must be removed and checked off on test sheet. | SSO Reached Public Land
38902 | 34612 | IN0002780 | Duke Energy IGCC | Knox | 2013-03-05 20:20 | 2013-03-06 10:00 | 2013-03-07 09:44 | 5000000 | gallons | 15424 E SR 358 Edwardsport IN Raw water treatment to SE pond to final pond to outfall 002. Outfall 002 to the West Fork White River | Partially Treated Release Bypass of a Treatment Process. At 10:AM on 3/06/2013 and unintentional release of partially treated coal pile runoff water was discovered and investigated. Storm water was being routinely pumped from the coal pile runoff collection pond to raw water treatment for iron removal and reuse. The forwarding pumps in raw water treatment did not keep up with the amount of storm water leads to the station s southeast pond an eventually to out 002. After the bypass/overflow event samples were collected from the coal pile storm water collection pond and tested for iron. Based on the iron results of 172 mg/L the treatment process bypass/overflow may cause an exceedance of the 002 outfall s iron limit of 1.0 mg/L | Coal pile storm water runoff collection pond forwarding pumps forwarding pumps were turned off stopping the bypass/overflow. The sequence of events leading up to the unintended diversion of the coal pile storm water into the pond system are being investigated. Based on the results of the investigation countermeasures will be put into place to prevent recurrence. An outfall 002 24 hour composite sample was being collected at the time of the incident and will be analyzed for iron and reported. Normally planned 002 sampling events are scheduled for March 1113and 15. Routine testing will include iron analysis each day. Quarterly whole effluent toxicity testing will be done on March 1113 and 15 on outfall 002 | SSO Reached Receiving Water | White River
11456 | 42633 | IN0030276 Outfall 011A | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-12-21 15:30 | 2013-12-22 02:00 | 2013-12-22 09:00 | 0 |  | 723 Maryland St Bicknell | Rain 4 inches Over flow results from lift station #3 being unable to keep up with amount of rain fall. | See Report
11456 | 42612 | IN0030276 Outfall 001 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-12-21 08:45 |  | 2013-12-21 08:45 | 0 |  | Liftstation#1 | See Report | See Report | SSO Affected Private Property
35086 | 36839 | IN0031020 | VINCENNES WASTE WATER TREATMENT PLANT | Knox | 2013-04-27 | 2013-05-09 14:00 | 2013-05-13 09:56 | 936000 | gallons | Chicago Ave Lift Station 11 Chicago Ave West Vincennes IN 47591 Storm Sewer to Wabash River | Equipment Failure River reached 27.68 inches on April 27 2013- the record level since the modern levee was built in 1960. Heavy rains north along the Wabash caused the river to climb to record levels. With the high ground water table the sandy soils saturated and nowhere for the water to drain we received a lot of infiltration. The two lift station pumps were unable to keep up with the demand. A third pump was setup to bypass to keep the sewer from backing up into homes and flooding the area. This pump was a 3 trash pump operated once per day for 4 hours each day to help the sewer system maintain adequate levels. There is no reasonable access to the sanitary sewer to relief this problem during this extraordinary conditions. | Setup Bypass pumps as mentioned above. This area has never had problems until 2011 during a near record flood with heavy rain. The 2013 flood was the highest recorded level on the modern levee system and the station was once again unable to keep up with the infiltration. We will continue to video the sewer mains to look for I&I problems. | SSO Reached Receiving Water; Storm Sewer | Wabash River
35086 | 38507 | IN0031020 | VINCENNES WASTE WATER TREATMENT PLANT | Knox | 2013-06-17 13:00 |  | 2013-06-17 13:00 | 0 |  | Behind Residence 420 Dalewood Dr Vincennes In 47591 | Equipment failure. IDEM was notified in writing via fax of sanitary sewage on the ground at the above location from a unanomous person. IDEM inspector Keith Condra called my cell phone at 10:30am June 17 2013 to have me meet him on sight. The unanomous letter sent to IDEM states the person had reported the situation to our department. We have no record of any call reported. The only call we received for this area was a standard sewer call May 17 2013 at 9:45am for slow sewer. Ann with Jack Dale Rental made the initial call The line and the exact manhole was cleaned and inspected at that time and no debris was present at this time. A service call report was completed and put on file. IDEM S call was the first call we have received for this location concerning sewage on the ground. We do not know how when or what caused the overflow. There are only a few homes on this line. | We will be investigating the area. We will camera the sewers remove the paper debris and reseal the manholes in the area. We do not know the cause of the problem at this time. We will continue to video the sewer mains to look for any problems. | SSO Affected Private Property
35086 | 39486 | IN0031020 | VINCENNES WASTE WATER TREATMENT PLANT | Knox | 2013-07-01 09:38 | 2013-07-01 09:38 | 2013-07-03 07:00 | 0 |  | 220 Meadowlark Lane (Meadowlark Lift Station) Ground | Rain 2.5 inches. During this period we received 2.5 of rain in one hour. A local resident notified us of sewage on the ground. Out employee went on sight and found no water on the ground but did notice a couple small pieces of sewage debris on the ground. The Meadowlark Lift Station was pumping at 100%. No homes were affected by the issue. The sewage backed up at the lift station for very brief period. No other sewage related issues were reported in Vincennes during this time. | See Report | SSO Affected Private Property
11456 | 35237 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-01-11 03:50 | 2013-01-11 05:20 | 2013-01-11 12:52 | 50000 | gallons | Lift Station #3 Bicknell IN | Precipitation event coupled with snow melt triggered an Untreated Release to ground around Lift Station | Area will be cleaned and limed. Plans to repair I & I problems. | SSO Reached Public Land
11456 | 35960 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-01-13 00:45 | 2013-01-13 08:50 | 2013-01-14 10:08 | 50000 | gallons | Lift Station #3 | Precipitation event exceeded capacity of system resulting in an untreated release from lift station to surrounding ground. | Area will be cleaned and limed. Plans to repair I & I problems. | SSO Affected Private Property
11456 | 34794 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-02-26 18:00 | 2013-02-26 18:15 | 2013-02-27 10:22 | 75 | gallons | Lift Station #1 in manhole on Hodge Boulevard | Untreated Release from Manhole. Lift Station #1 level transducer failure caused overflow. | Pumps were placed on hand to begin pumping down the wet well. Transducer was removed for cleaning in hopes that this would sove the issues. Upon replacement of the level transducer it had in fact failed. Back-up float system seems to be inoperable at this time. Pumps are flow pacing manually via VFD controls and were monitored throughout the night and continue to be monitored at this time. Wet well level is holding steady at approximately 5 feet of liquid. We have ordered a new level transducer from BL Anderson and a repair crew is enroute for our float system. The area where the overflow occurred was cleared of debris all liquid remaining was then washed into the originating manhole and the area was disinfected with a bleach sprayer. Back up float switches are being placed in the wet well on a new bracket so that when needed they can be submerged and while not needed they can be pulled from service to prevent fouling of the switches. | SSO Reached Public Land; Paved Surface
11456 | 36151 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-04-19 03:00 |  | 2013-04-19 08:07 | 100000 | gallons | Manholes 242-243 on White River Avenue | Precipitation event overwhelmed sewer line resulting in untreated release from manhole to White River Avenue Ditch | Area to be cleaned and limed. Currently biddng project to replace lines. | SSO Reached Receiving Water
11456 | 36095 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-04-19 03:00 | 2013-04-19 10:00 | 2013-04-19 12:43 | 100000 | gallons | 729 Maryland Street | Precipitation event exceeded capacity of lift station resulting in untreated release to surrounding ground. | Area to be limed and cleaned. Currently bidding project to rehab and replace lines. | SSO Reached Public Land
11456 | 36094 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-04-19 03:00 | 2013-04-19 10:00 | 2013-04-19 12:43 | 100000 | gallons | White River Avenue Manhole #242-243 | Precipitation event exceeded capacity of sewer collection line resulting in an untreated release from manhole to surrounding ground and ditch | Area to be cleaned and limed. Currently bidding project to replace lines. | SSO Reached Public Land; SSO Reached Receiving Water
11456 | 37647 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-06-01 04:30 | 2013-06-01 12:00 | 2013-06-01 14:26 | 50000 | gallons | Lift Station #3 | Flow from precipitation event and I & I overwhelmed lift staion resulting in overflow to surrounding ground. | Areas to be cleaned and limed once weather permits.Plans are in place to replace main sewer line suffering major I & I problems.
11456 | 39073 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-06-26 20:15 | 2013-06-27 03:00 | 2013-06-27 08:30 | 0 |  | Manhole 243 along White River Ave | Rain 2.75 inches Exceeded Max Capacity. With and already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed by 2.75 inches of rain in less than 2 hours. Rains came in two sessions of torrential downpours. | See Report | SSO Affected Private Property
11456 | 39074 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-06-26 20:15 | 2013-06-27 05:30 | 2013-06-27 08:30 | 0 |  | Lift Station #3 @ Maryland and Coal. With and already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed by 2.75 inches of rain in less than 2 hours. Rains came to two sessions of torrential downpours. | Rain 2.75 inches Exceeded Max Capacity. With and already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed by 2.75 inches of rain in less than 2 hours. Rains came in two sessions of torrential downpours. | See Report | SSO Affected Private Property
11456 | 39066 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-06-26 20:45 | 2013-06-26 22:00 | 2013-06-27 07:45 | 0 |  | Manhole 9 along Mary Street | Rain 2.75 inches Exceeded Max Capacity. With and already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed came in two sessions of torrential downpours. | See Report | SSO Affected Private Property
11456 | 39067 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-06-26 21:00 | 2013-06-26 23:30 | 2013-06-27 08:03 | 0 |  | Rain 2.75 inches Exceeded Max Capacity. With and already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed by 2.75 inches of rain in less than 2 hours. Rains came in two sessions of torrential downpours. | Rain 2.75 inches Exceeded Max Capacity. With and already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed by 2.75 inches of rain in less than 2 hours. Rains came in two sessions of torrential downpours. |  | SSO Affected Private Property
11456 | 39071 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-06-26 21:00 | 2013-06-26 23:30 | 2013-06-27 08:30 | 0 |  | Lift Station #1 at Hodge Blvd | Rain 2.75 inches Exceeded Max Capacity. With an already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed by 2.75 inches of rain in less than 2 hours. Rains came in two sessions of torrential downpours. | See Report | SSO Affected Private Property
11456 | 39061 | IN0039276 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-06-26 23:00 | 2013-06-27 07:20 | 2013-06-27 08:30 | 0 |  | Lift Station 2 along 12th St | Rain 2.75 inches Equipment Failure Exceeded Max Capacity With and already saturated ground and a previously stressed system due to the I/I from previous rains our collection system was completely overwhelmed by 2.75 inches of rain in less than 2 hours. Rains came in two sessions of torrential downpours. Then came in two sessions of torrential downpours. On top of this rain both chopper pumps had tipped out. | See Report | SSO Affected Private Property
11456 | 41081 | IN0039276 Outfall 001 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-10-06 05:30 | 2013-10-06 08:00 | 2013-10-08 09:30 | 0 |  | Private lateral at 723 Maryland Street | Rain 5.75 inches 5.75 of rain overwhelmed wastewater pumping station downstream from this home. The lift station was high but did not overflow. The WRA Sewer project seemed to have lessened the impact but not entirely corrected this issue. Home owner did not contact the wastewater department until Tuesday October 8th at 9:02am | See Report | SSO Affected Private Property
11456 | 42611 | IN0039276- Is the correct Permit Number Outfall 001 | BICKNELL MUNICIPAL WASTE WATER TREATMENT PLANT | Knox | 2013-12-21 06:30 |  | 2013-12-21 07:30 | 0 |  | Liftstation #3 | See Report | See Report | SSO Affected Private Property
42969 | 42402 | IN0030881 | HIDE AWAY HILLS MOBILE HOME PARK | Kosciusko | 2013-12-10 09:00 | 2013-12-10 12:00 | 2013-12-10 12:00 | 0 |  | Pump Station Failure | New pumps failed to turn on | Repaired Pump Station See Report | SSO Occurred at Treatment Plant
43073 | 37369 | IN0040347 | MENTONE MUNICIPAL WASTE WATER TREATMENT PLANT | Kosciusko | 2013-06-01 09:00 | 2013-06-01 10:30 | 2013-06-01 13:30 | 5000 | gallons | 507 S Franklin St Mentone IN | Rain 6 inches | Had the lift station pumped by a waste hauler (Weed s). Unsure of what other actions to take. The overflow was due to us receiving a large amount of rainfall in a 12 hour period. | SSO Affected Private Property; SSO Reached Receiving Water | Yellow Creek
43075 | 35010 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-01-28 17:00 | 2013-02-01 11:00 | 2013-02-01 15:15 | 346 | gallons | 1st trail on Epworth Forest Road North Webster IN | Lateral plugged up and sanitary sewer line was plugged causing untreated release | The lateral was cleaned by the jetter machine. Plug released and flow returned to normal. Will check the manhole more frequently during the week. | SSO Reached Public Land; Surface Soil
43075 | 36541 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-04-19 02:00 | 2013-04-19 15:00 | 2013-04-20 10:07 | 7000 | gallons | Town of North Webster WWTP | Influent flow to WWTP caused by precipitation event filled and overflowed the polishing pond to surrounding grass area. Resulting effluent was a partially treated release. | Befoe the rain event we lowered the finishing pond to try to handle the potential influent. Maintain the plant to run at peak flows. | SSO Occurred at Treatment Plant
43075 | 36542 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-04-19 03:00 | 2013-04-19 14:00 | 2013-04-20 10:07 | 5000 | gallons | North Shore Main (Epworth Forest) Lift Station | Flow from precipitation event and infiltration exceeded capacity of lift station resulting in a bypass (pumping out lift station manhole) of untreated release to surrounding ground. | Pumped out manhole to prevent lift station from going under water. Currently hunting for source of infiltration. | SSO Reached Public Land
43075 | 37626 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-06-01 03:00 | 2013-06-01 14:30 | 2013-06-02 13:19 | 4500 | gallons | North Shore main in Epworth Forest | Flow from precipitation event coupled with infiltration exceeded capacity of a main and lift station resulting in necessity of pumping manhole to surrounding ground to keep lift station from being sumerged. | Currently trying to find source of infiltration whether it is from the lake of sewer lines.
43075 | 37629 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-06-01 04:00 | 2013-06-02 08:00 | 2013-06-02 13:19 | 7000 | gallons | North Webster WWTP | Flow from preciptiation event to the WWTP exceeded the capacity of the finishing pond causing it to overflow to WWTP grounds. | Before the rain event pond level was lowered in anticipation of potential influent increase. Maintain the plant to run at peak flows. | SSO Occurred at Treatment Plant
43075 | 37753 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-06-05 10:15 | 2013-06-05 12:15 | 2013-06-05 12:44 | 500 | gallons | Manhole at East St and North St. Storm Sewer. | Equipment Failure Collection system experienced a plug that resulted in a back-up at the manhole. | Personnel responded to call out and jetted the line. We were able to unplug without further damage to the system or surrounding property. We put this manhole on the list of manholes we check every Friday to ensure proper operation. | Storm Sewer
43075 | 39680 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-08-02 23:00 | 2013-08-04 07:00 | 2013-08-05 12:26 | 0 |  | Polshing Pond WWTP | The flow that was coming into the plant was so much that it filled the polishing ponds capacity causing the finishing pond to over flow. | Before the rain event we tried to lower the polishing pond level to help handle the flow coming in. maintain the plant to be able to run at peak flows. | SSO Affected Private Property
43075 | 42551 | IN0040444 | NORTH WEBSTER WASTE WATER TREATMENT PLANT | Kosciusko | 2013-12-17 12:30 | 2013-12-17 12:30 | 2013-12-17 13:45 | 0 |  | Lift Station #9 | Lift Station #9 control panel blew a fuse and did not let the alarm sound. The fuse also did not allow the pumps to pump. | See Report | SSO Affected Private Property
45343 | 39779 | IN0045802 | TURKEY CREEK REGIONAL SEWER DISTRICT | Kosciusko | 2013-08-14 13:00 | 2013-08-14 13:23 | 2013-08-14 02:48 | 0 |  | Air Release Valve Failure | Equipment failure air release fast on force main some sewage out of manhole. | Repaired Pipe See Report | SSO Affected Private Property
45343 | 37672 | IN0054802 | TURKEY CREEK REGIONAL SEWER DISTRICT | Kosciusko | 2013-06-05 | 2013-06-05 | 2013-06-05 09:39 | 100 | gallons | Lot 842 Lot 841 | Construction Relegated house Lateral. Sewer full of roots cleaned out vactor truck jetted line on home owners property. | Line replaced and lime put down. Line replaced roots taken-out. | SSO Affected Private Property
45220 | 35075 | IN0060917 | WARSAW WASTE WATER TREATMENT PLANT 2 | Kosciusko | 2013-02-02 15:07 | 2013-02-02 16:04 | 2013-02-02 16:56 | 100 | gallons | 705 North West Street Warsaw IN | Sewer Line blocked causing untreated release. | Sewer truck used to remove blockage. The area and storm catch basin were cleaned. The sewer line will be cleaned and a root saw run through the line. We will then video inspect the sewer line. | SSO Reached Public Land
45220 | 34716 | IN0060917 | WARSAW WASTE WATER TREATMENT PLANT 2 | Kosciusko | 2013-02-26 15:50 | 2013-02-26 16:45 | 2013-02-27 08:15 | 500 | gallons | Jaylnn Street manhole by Lowes and Walmart | Blocked sewer line caused Untreated Release | Sewer truck used to remove blockage. The area and storm catch basin were cleaned. The sewer line in question will be cleaned and inspected. | SSO Reached Public Land
45220 | 37624 | IN0060917 | WARSAW WASTE WATER TREATMENT PLANT 2 | Kosciusko | 2013-06-01 02:25 | 2013-06-01 07:00 | 2013-06-01 12:13 | 628589 | gallons | CSO Outfall Warsaw Wastewater Treatment Plant #2 | Flow from multiple precipitation events exceeded capacity of treatment plant resulting in treatment bypass to receiving water. | Maintained maximum pumping and treatment at the plant. We continue to maintain our combined sewers and pump stations. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Tippecanoe River; Walnut Creek
105922 | 36668 | INP000622 | Organic Systems & Solutions LLC dba Bio-Waste Processing LLC | Kosciusko | 2013-04-23 11:50 | 2013-04-23 12:00 | 2013-04-26 12:14 | 1000 | gallons | Bio Waste Processing 1099 W 1250N | Rock Trap Overflow Cap came loose. | Immediately stopped septic hauler from pumping into the facility. Once the spill was contained the lift station was pumped down to prevent any further flow of the raw septic being discharged into the WWTP.Always make sure that the overflow cap is secured. | SSO Occurred at Treatment Plant
| 36507 | Non permitted | Town of Winona Lake | Kosciusko | 2013-04-19 13:30 | 2013-04-19 14:30 | 2013-04-19 16:53 | 1000 | gallons | Unknown location. | Precipitation event and clogged line resulted in an unpermitted untreated release from manhole to unnamed area. | Line cleaned out | SSO Reached Public Land
| 42691 |  |  | La Porte | 2013-12-27 | 2013-12-27 16:00 | 2013-12-30 12:44 | 0 |  | 5885 N 800 E New Carlise INl | Norfolk Southern RR special investigator observed septic waste hauler discharge waste into an open ditch.also noted strong septic odor emitted from the site. | Investigated this incident under Tempo #43030/Cheryl Satkus.
12070 | 35615 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-01-09 16:30 | 2013-01-09 16:55 | 2013-01-10 15:49 | 1 | gallons | 206 White Oak Drive | Routine cleaning of sewer main pushed an air bubble through a lateral resulting in a small untreated release into a residential basement. | Sanitary District forman checked upstream and downstream from residence. Homeowner had cleaned up spill before Sanitary District arrived. This line will be scheduled for re-check. | SSO Basement Backup
12070 | 35188 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-01-28 13:30 | 2013-01-28 14:27 | 2013-01-29 11:51 | 0 |  | 601 East 11th Street Michigan City IN | Employee reported sewage coming out of ground between curb and sidewalk. Untreated release to ground and storm catch basin. | Fownd sewage coming out of privat e clean out. District vacuumed up sewage on ground and catch basin. Advised homeowner to call a sewer contractor and to not use water until repair is completed. Line will be scheduled for re-check. | SSO Reached Public Land; Storm Sewer
12070 | 35185 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-01-28 17:22 | 2013-01-28 18:45 | 2013-01-29 13:25 | 1 | gallons | 100 Anchor Road Michigan City IN | Bathroom backup | Cleaned private lateral at manhole. Removed debris and restored flow. Discovered that lateral runs through a ditch and the lateral was damaged and leaking into the ditch. District crew vacuumed up the sewage in the ditch notified the customer and turned off the water until lateral was repaired. Rechecked on 1/29/13. Lateral had been repaired and no sewage was leaking into ditch. | SSO Affected Private Property
12070 | 34964 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-06 01:01 | 2013-02-06 15:00 | 2013-02-07 08:30 | 50 | gallons | 312 W. US Highway 20 fotune House restaurant. Michigan City IN | Drains not working at Fortune House restaurant. | Found several manholes holding water. The crew removed the obstruction and line was down and running. Crew investigating site found that the outside cleanout cap was missing. Sewage and grease ran out of clean out onto ground. Crew vacuumed up and cleaned parking lot of sewage and grease. This line will be scheduled for re-check adn video within 30 days. | SSO Basement Backup; SSO Reached Public Land
12070 | 35314 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-06 16:15 | 2013-02-06 17:10 | 2013-02-07 15:15 | 25 | gallons | 120 N Ashland Ave Basement Floor | Untreated Release Sanitary District Received call from homeowner at 4:15PM on 2/6/2013 stating they were experiencing backup in basement. | Sanitary District crew responded to this address at 5:00pm on 2/6/2013. Found main sewer line down and running. Crew jetted main line and did not hit a blockage. Crew went to residence to inform them that the line was down and running and no blockage was found. Homeowner said backup in basement went down. This line will be scheduled for re-check and video within 30 days.
12070 | 34879 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-06 16:15 | 2013-02-06 17:10 | 2013-02-07 15:15 | 25 | gallons | 120 N. Ashland Avenue Michigan City IN | Back up in basement at 120 N. Ashland Avenue Michigan City | Sanitary District crew founnd main line down and running. Crew jetted main line and did not encounter any obstruction/blockage. Crew informed homeownew who said that the backup in the basement had gone down. Lis will be scheduled for re-check and video within 30 days. | SSO Basement Backup
12070 | 34344 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-06 16:15 | 2013-02-06 17:10 | 2013-02-07 15:15 | 25 | gallons | 120 North Ashland Avenue | Untreated Release - Call from homeowner at 4:15 pm on 2/6/13 stating they were experiencing a backup in the basement. | Sanitary District crew responded to this address at 5:00 pm on 2/6/2013. Crew notified the residents that the line was down and running and no blockage was found. Homeowner said the backup in the basement went down. The line will be scheduled for recheck and video within 30 days. | SSO Basement Backup
12070 | 34877 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-15 20:26 | 2013-02-15 22:21 | 2013-02-16 09:45 | 500 | gallons | Parking lot at Walgreen Pharmacy 421 Franklin Street and US Highway 20 Michigan City IN | Sanitary district received a call from the manager at Walgreens Pharmacy 421 Franklin Street and US Highway 20 indicating that sewage was coming out of a manhole and onto the parking lot. | Sanitary crew responded to this address. Found sewage coming out of a private cleanout in parking lot. district crew jetted private sewer line. The plug which was grease was alleviated. District crew cleaned parking lot and catch basin with help from private contractor D&M excavating. the line will be scheduled for re-check. | SSO Reached Public Land; Paved Surface
12070 | 35309 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-15 20:26 | 2013-02-15 22:21 | 2013-02-16 09:45 | 500 | gallons | 421 US Highway 20 Walgreens Pharmacy Ground/ Storm Catch Basin | Untreated Release Sanitary District received call from manager at Walgreens pharmacy at 8:26PM 421 Franklin St. and US Highway 20. Sewage is coming out onto parking lot form manhole. | Sanitary district crew responded to this address at 9PM on 2/15/2013. Found sewage coming out of a private cleanout in parking lot. District crew jetted private sewer line. The plug which was grease was alleviated. Line was down and running by 10:21 PM. District crew cleaned parking lot and catch basin with help form private contractor D&M excavating. This line will be scheduled for re-check. | Storm Sewer
12070 | 35311 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-16 10:01 | 2013-02-06 15:00 | 2013-04-01 08:30 | 50 | gallons | 312 W US Highway 20 Ground & Catch Basin | Untreated Release Sanitary District received call from employees at Fortune House Restaurant at 312 W us Highway 20 on 2/06/2013 at 10:01AM stating water will not drain inside business. | Sanitary District crew responded to this address at 10:48AM on 2/6/2013 found multiple-manholes holding water. The crew alleviated the plug and line was down and running. Crew investigating the site found Fortune House outside clean out was missing cap. Sewage and grease ran out of clean out onto the ground. Crew vacuumed up and cleaned parking lot of sewage and grease. This line will be scheduled for re-check and video within 30 days. | Storm Sewer
12070 | 35307 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-22 10:32 | 2013-02-22 11:00 | 2013-04-01 15:22 | 2 | gallons | 2421 Wabash Street Basement Floor | Untreated Release Sanitary District crew responded to this address at 11:00am on 2/22/2013. Stating they have a backup in basement. Sewer contractor Gene s Sewer Service told homeowner to call Sanitary District to have main line checked. | Sanitary District crew responded to this address at 11:00AM on 2/22/2013. Crew jetted main line in alley. Didn t hit any blockage but brought back some rags. homeowner said water in basement went down. This line will be scheduled for a re-check & video with in 30 days | SSO Basement Backup
12070 | 34809 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-02-22 10:32 | 2013-02-22 11:00 | 2013-02-22 15:22 | 2 | gallons | 2421 Wabash Street Michigan City IN | Sanitary district received a call from homeowner at 10:32 AM on 2/22/2013 stating they have backup in basement. | Crew responded to 2421 Wabash St. Jetted main line in alley. Did not hit any blockage but brought back some rags. Homeowner said water in basement went down. The line will be re-checked and videoed in 30 days. | SSO Basement Backup
12070 | 34719 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-03-16 19:25 | 2013-03-16 20:30 | 2013-03-17 19:55 | 10 | gallons | 105 Sherman Ave Ground | Untreated Release Sanitary District received call from Michigan City Police Department at 7:25pm on 3/16/2013 stating 105 Sherman Ave. sewage coming out of the cleanout onto ground. | Sanitary District crew responded to this address at 8pm on 3/16/13 found sewage coming out of the private cleanout. District crew vacuumed sewage up from ground. Spoke to residents at 105 Sherman Ave explain to them they need to call a sewer contractor and not to run anymore water until sewer contractor can unplugged line. Sanitary District assistant superintendent will resident at 105 Sherman Ave. to see if they hired a sewer contractor to open plug. | SSO Affected Private Property
12070 | 35435 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-03-25 07:58 | 2013-03-25 07:58 | 2013-03-25 14:37 | 15521 | gallons | Snitary District of Michigan City WWTP | A power failure and 3 minute switching time to back up power resulted in the bypass of the Sand Filtration Process. No release. Just treatment bypass which was recombined with final effluent and sampled before discharge. | Immediate steps were taken to return the filtration system to service with the result of limiting the event to 3 minutes.MCSD Agreed Order Case No. 2010-19414-W requires that a Sand Filtration Bypass Elimination Plan be implemented by June 30 2013. The MCSD recently contracted with Haas and Associates to evaluate considerations for eliminating sand filtration bypassing by untilizing in-plant storage. | SSO Occurred at Treatment Plant
12070 | 35467 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-03-25 07:58 | 2013-03-25 07:58 | 2013-03-25 | 15521 | gallons | Sand Filtration Process | Blended with final Effluent and Sampled Power Failure | Immediate steps were taken to return the filtration system to service and these efforts were successful in limiting the event to three (3) minutes. MCSD Agreed Order Case NO 2010-19414-W requires that a Sand Filtration Bypass elimination Plan be implemented by June 30th 2013. The MCSD recently contracted with Haas and Associates to evaluate Considerations for Eliminating Sand Filtration Bypassing by utilizing in-plant storage. A draft copy of the report is also attached This report should be finalized soon and all implementation steps should be completed by June 30th2013 | SSO Reached Receiving Water | Trail Creek
12070 | 36072 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-04-18 02:00 | 2013-04-18 05:45 | 2013-04-18 16:53 | 2340000 | gallons | Sanitary District of Michigan City WWTF | Lightning strike at WWTP caused a power loss and resultant bypss of the tertiary sand filtration building. Also final effluent flow meter was rendered inoperable which caused a failure of automated chlorination/dechlorination feed system as well at the final effluent auto sampler. Partially treated release to receiving waters. | Auto systems were out of service for 3.75 hours. System back online in manual mode. Samples were not taken during outage but samples taken following restoration indicated that effective disinfection was completed. Outside technical contractor called to the WWTF after which the final effluent flow meter and disinfection auto feed systems were successfully reactivated at 10:45 am. An investigation of the circumstances as well as staff response will be conducted and procedures may be modified with a plan of action to prevent/mitigat any future reoccurrence. | SSO Reached Receiving Water | Trail Creek
12070 | 37199 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-04-18 02:00 | 2013-04-18 05:45 | 2013-05-29 11:32 | 2340000 | gallons | Sand Filtration Process Outfall #001 Trail Creek | Partially Treated Release Bypass of a Treatment Process Power Failure At approximately 2:00am on 4/18/2013 a lightening strike caused two problems at the JB Gifford WWTF;1) Power was interrupted to the tertiary sand filtration building which resulted in a bypass of secondary effluent around the filtration process for approximately 15 minutes; and 2) The current final effluent flow meter was rendered inoperable causing our automated chlorination/dechlorination feed system as well as the final effluent auto-sampler to fail. This lasted for approximately 3.75 hours until such time the disinfection system was re-established albeit in manual mode. Samples were not taken during outage however samples taken subsequent to the disinfection system restoration confirmed effective disinfection. Additionally E. Coli samples were taken as normal. | An outside technical contractor was called to the WWTF after which the final effluent flow meter was restored to its normal function and the disinfection auto-feed system was successfully reactivated at 10:45am | SSO Reached Receiving Water | Trail Creek
12070 | 38837 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-26 05:55 | 2013-06-26 06:40 | 2013-06-26 07:21 | 0 |  | WWTF Sand Filtration Process 1100 E Eighth Street Michigan City Indiana. Outfall 001 to Trail Creek | See Attached. | Power was restored as soon as possible. MCSD is implementing improvements for additional storage when power is interrupted.
12070 | 38846 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-26 05:55 | 2013-06-26 10:30 | 2013-06-26 07:21 | 0 |  | Manholes at the WWTF 72 inch Sewer Influent line 1100 E Eighth Street Michigan City Indiana. Manholes on the 54 inch sewer along Trail Creek Michigan City Indiana | See Attached | Treated and stored flow was maximized and Vacuum Sewer Cleaning Trucks where dispatched to the overflowing areas to vacuum sewers in an effort to minimize the overflowing amount. All areas affected were cleaned up soon after this incident. All storm event operating protocols will be examined revised as necessary and additional training will be given to all operators. | SSO Reached Receiving Water | Trail Creek
12070 | 39927 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-26 11:18 | 2013-06-26 11:18 | 2013-08-30 11:53 | 0 |  | B&E Marine 31 Lakeshore Drive Sewer backup in buildings | Rain 5.3 inches. Sanitary District was made aware of this incident on July 17th 2013 by a third party. The owner experienced a sanitary sewer backup in the bath house of approximately 1300 gallons. The owner cleaned and sanitized the affected area. | Sewers in the proximity of B&E Marine will be cleaned and inspected. It is unlikely that any reasonable efforts could prevent a backup under such extreme circumstances precipitation of over 5.3 inches in 3.5 hour time frame. | SSO Basement Backup
12070 | 39439 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-26 11:37 | 2013-06-26 11:38 | 2013-07-18 18:20 | 0 |  | B&E Marine 31 Lakeshore Dr Sewer backup in buildings | Rain 5.3 inches. Sanitary District was made aware of this incident of on July 17 2013 by a third party. The owner experienced a sanitary sewer backup in the bath of approximately 1.3000 gallons. The owner cleaned and sanitized the affected area. | See Report | SSO Basement Backup
12070 | 38852 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-27 10:22 | 2013-06-27 21:58 | 2013-06-28 14:38 | 0 |  | WWTF Sand Filtration Process 1100 E Eighth Street Michigan City Indiana | See Attached | The incidents were intermittent but the treated flow was reduced to prevent recurrence. The MCSD is currently implementing facility improvements to provide for additional storage when power is interrupted in accordance with Compliance Plan and the Agreed Order. These improvements may help to prevent recurrence. | SSO Reached Receiving Water | Trail Creek
12070 | 38848 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-27 10:22 | 2013-06-27 21:58 | 2013-07-30 09:51 | 0 |  | WWTF Sand Filtration Process 1100 E. English Street Michigan City Indiana. WWFT Sand Filtration Process 1100 Eighth Street Michigan City Indiana. | See Attached | The incidents were intermittent but the treated flow was reduced to prevent recurrence. The MSCD is currently implementing facility improvements to provide for additional storage when power is interrupted in accordance with the Compliance Plan and the Agreed Order. These improvements may help to prevent recurrence. |  | Trail Creek
12070 | 38856 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-27 10:30 | 2013-06-27 21:58 | 2013-06-28 14:38 | 0 |  | WWTF De-Chlorination Process Bypass 1100 E Eighth Street Michigan City Indiana | See Attached | The incidents were intermittent but the treated flow was reduced to prevent recurrence. The MCSD is currently implementing facility improvements to provide for additional storage when power is interrupted in accordance with the Compliance Plan and the Agreed Order. These improvements may also help to prevent recurrence. | SSO Affected Private Property; SSO Reached Receiving Water | Trail Creek
12070 | 38858 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-28 15:50 | 2013-06-28 16:08 | 2013-06-28 19:07 | 0 |  | WWTF Sand Filtration Process 1100 E eighth Street Michigan City Indiana | See Attached | The incident was brief and the treated flow was reduced to prevent recurrence. The MCSD is currently implementing facility improvements to provide for additional storage when power is interrupted in accordance with the Compliance Plan and the Agree Order. these improvements should also help to prevent recurrence. | SSO Reached Receiving Water | Trail Creek
12070 | 39193 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-06-28 15:58 | 2013-06-28 16:01 | 2013-06-28 19:07 | 0 |  | WWTF De-Chlorination Process Bypass 1100 E Eight Street Michigan City IN | See Attachment | See Report | SSO Affected Private Property; SSO Reached Receiving Water
12070 | 39554 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-07-08 09:28 | 2013-07-08 09:33 | 2013-07-12 03:19 | 0 |  | WTF Sand Filtrartion Bypass Structure | Power Failure 07-08-13 District staff initiated a test of a newly constructed secondary flow system designed to mitigate if not eliminate tertiary system bypassing. The new system functioned as intended with the exception of approximately 75 gallons of leakage. 07-09-13 a storm event caused a power interruption engaging the aformentioned retainment system that again served its intended purpose but did leak approximately 50 gallons of secondary effluent. | See Report | SSO Reached Receiving Water | Trail Creek
12070 | 39555 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-07-09 13:02 | 2013-07-09 13:08 | 2013-07-12 03:19 | 0 |  | WTF Sand Filtration Bypass Structure | Construction Related 07-08-13 District staff initiated a test of a newly constructed secondary flow retainment system designed to mitigate if not eliminate tertiary system bypassing. The new system functioned as intended with the exception of approximately 75 gallons of leakage. 07-09-13 A storm event caused a power interruption engaging the aforementioned retainment system tat again served it s intended purpose but did leak approximately 50 gallons of secondary effluent. | See Repoprt | SSO Reached Receiving Water | Trail Creek
12070 | 39568 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-07-17 13:33 | 2013-07-17 13:35 | 2013-07-17 04:26 | 0 |  | Manhole by the Filter Building | Construction Related District personnel were testing the Sand Filter Bypass Elimination Plan (Secondary Effluent Detention Scheme) when approximately 100 gallons of secondary effluent overflowed from a manhole on to the ground of which approximately 20 gallons flowed into a storm sewer. The secondary effluent bypassed sand filtration and disinfection. | See Report | SSO Reached Receiving Water | Trail Creek
12070 | 39733 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-03 09:30 | 2013-08-03 10:30 | 2013-08-03 12:13 | 0 |  | South Porter Street | Basement backups were experienced on South porter Street. This area is served by a combined sewer system. The intense rain of 8/3/13 overwhelmed the system and caused backups into the basement several homes on South Porter Street including 231 232 234241304306311 and 312 South Porter Street. |  | SSO Basement Backup
12070 | 39371 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-07 16:08 | 2013-08-07 16:53 | 2013-08-08 13:55 | 0 |  | Bypass of sand filter process | Rain 2.46 inches Power Failure Electrical power interruption caused the bypassing of sand filtration process. However the secondary effluent was subjected to disinfection and the sampling of the final effluent was uninterrupted throughout this event. | See Report | SSO Occurred at Treatment Plant | Trail Creek
12070 | 39370 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-07 16:15 | 2013-08-07 16:23 | 2013-08-08 13:55 | 0 |  | Overflow from manhole upstream of sand filter process. | Rain 2.46 inches Power Failure. Electrical power interruption caused the bypassing of sand filtration process. Additional the excessive flow resulted in intense hydraulic pressure which damages the above-referenced manhole and an overflow of approximately 300 gallons of secondary effluent of which approximately 60 gallons flowed into the storm sewer bypassing sand filtration and disinfection. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Trail Creek
12070 | 39740 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-07 16:29 | 2013-08-07 17:30 | 2013-08-08 13:01 | 0 |  | 31 Lakeshore Dr Manhole | Rain 2.46 inches Sanitary District received call from mission control of a high level alarm at 4:29 on 8/7/13 at 31 Lakeshore Drive. | See Report | SSO Reached Receiving Water | Trail Creek
12070 | 39792 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-14 11:24 | 2013-08-14 15:51 | 2013-08-16 11:04 | 0 |  | 1006 Ohio Street | Sanitary District received call from homeowner at 11:24am on 8-14-13 stating they are experiencing back up in their basement. | Sanitary District dispatch crew at 3:14pm found manhole was holding water. Crew jetted and cleaned city main and open plug which was found to be plugged with grease. This line will be scheduled to be cleaned and video inspection. | SSO Basement Backup
12070 | 39773 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-14 11:24 | 2013-08-14 15:51 | 2013-08-15 14:10 | 0 |  | 1106 Ohio Street | Sanitary District received call from homeowner at 11:24am on 8/14/13 stating they are experiencing back up in their basement. | Sanitary district dispatch crew at 3:14pm found manhole was holding water crew jetted and cleaned city main and open plug which was found to be plugged with grease. This line will be scheduled to be cleaned and video inspection. | SSO Basement Backup
12070 | 39790 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-15 13:30 | 2013-08-15 16:00 | 2013-08-16 11:43 | 0 |  | 204 Marquette Trail | Sanitary District received call from resident at 204 Marquette Trail at 1:30pm on 8/15/13 stating water coming out of ground close to lift station. | Sanitary district crew was dispatched at 1:30pm found clean out on force main. Leaking due to Cap On clean out broken sanitary district crew expose leak repaired and fixed. Repair Cap brought down underneath surface.
12070 | 40280 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-09-21 02:55 | 2013-09-21 03:30 | 2013-09-21 15:52 | 0 |  | Manhole at treatment facility | Power Failure Equipment Failure Secondary effluent overflowed at manhole between #7 and #8 final clarifiers on to ground and into Trail Creek. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Trail Creek
12070 | 41401 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-10-29 13:15 | 2013-10-29 13:30 | 2013-10-30 09:25 | 0 |  | 117 Benton Street 121 Benton Street Bathroon/Ground | Sanitary district received notice from homeowners on site at 1:15 pm on 10/29/2013 that their toilet overflowed on to ground in bathroom | See Report
12070 | 41511 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-10-31 06:53 | 2013-10-31 07:52 | 2013-10-31 16:16 | 0 |  | 512 Vail Street Floor/Basement | Sanitary District received call from homeowner at 6:53am on 10/31/2013 stating they were experiencing backup in basement. | Sanitary District crew responded to 512 Vail Street at 7:25am on 10/31/13 found sewer main holding water. The crew alleviated the plug and line was down and running. This line will be scheduled for re-check and video within 30 days. | SSO Basement Backup
12070 | 43311 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-12-14 20:05 | 2013-12-15 22:50 | 2013-12-15 11:27 | 5000 | gallons | 4128 S Franklin Street Ground/Ditch | Sanitary District received call from private business Baymont Hotel at 8:05pm on 12-14-2013 experiencing sewage back-up. | See Report
12070 | 42458 | IN0023752 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-12-14 20:05 | 2013-12-15 22:50 | 2013-12-15 12:16 | 0 |  | 4128 S Franklin Street/ Ground Ditch | Sanitary District received call from private business Baymont hotel at 8:05pm on 12-14-2013 experiencing sewage back-up. | See Report | SSO Affected Private Property
12070 | 41248 | IN0023752 Bathroom Backup | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-10-22 13:00 | 2013-10-22 14:30 | 2013-10-23 16:57 | 0 |  | 1923 Manhattan Street | Sanitary District received call from home owner on 10-23-2013 at 2:15pm stating yesterday that on 10/22/2013 toilet in bathroom overflowed onto floor. | See Report
12070 | 41154 | IN0023752 Outfall 001 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-08-07 16:08 | 2013-08-07 16:53 | 2013-08-08 13:55 | 0 |  | Bypass of Sand Filter Process | Rain 2.46 inches Electrical power interruption caused the bypassing of sand filtration process. However the secondary effluent was subjected to disinfection and the sampling of the final effluent was uninterrupted throughout the event. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Trail Creek
12070 | 39919 | IN0023752 Outfall 001 | JAMES B GIFFORD WASTE WATER TREATMENT PLANT | La Porte | 2013-09-21 02:55 | 2013-09-21 03:30 | 2013-10-29 15:32 | 0 |  | Manhole at treatment facility | Power Failure Equipment Failure Secondary effluent overflowed at manhole between #7 and #8 final clarifiers on the ground and into Trail Creek. | Removed Blockage See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Trail Creek
11905 | 39129 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-26 10:40 | 2013-06-26 10:40 | 2013-06-26 17:00 | 0 |  | Combined sewer manhole at the intersection of 14th and D Street | Manhole cover was found in street after a 3.82 inch rain in 2 hours. It is unknown how long a release occurred or the volume released. | See Report | SSO Affected Private Property
11905 | 39132 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-26 10:49 | 2013-06-26 10:49 | 2013-06-26 17:00 | 0 |  | Combined sewer storm drains at the intersection of Lawrence Street and East Jefferson Ave. | The intersection flooded during a 3.82 inch rain in 2 hours. Combined sewage and storm water pond in the street and lawns and then drain into the combined sewer system. | See Reports | SSO Affected Private Property
11905 | 39134 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-26 10:56 | 2013-06-26 10:56 | 2013-06-26 17:00 | 0 |  | Combined sewer manhole at the intersection of Central ave and First Street. | Combined sewer manhole at the intersection of Central Ave and First Street | See Report | SSO Affected Private Property
11905 | 39138 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-26 11:34 | 2013-06-26 11:34 | 2013-06-26 17:30 | 0 |  | Combined sewage was released from a clean out into the yard of 1210 Pennsylvania St. | The address is located well below the upstream manhole on the combined sewer system allowing combined sewage to be released through the address s cleanout on sewer surcharge. LaPorte has engaged a contractor to isolate the home with a sewage grinder pump. | See Report | SSO Affected Private Property
11905 | 39139 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-26 11:42 | 2013-06-26 11:42 | 2013-06-26 17:30 | 0 |  | Combined sewage was released into the basement of 310 Clement Street | Combined sewage backed into the sink and onto the floor as a result of sewer surcharge during the 3.82 inch 2 hour storm. The address has an isolation valve which the owner failed to close. | See Report | SSO Basement Backup
11905 | 39144 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-26 11:52 | 2013-06-26 11:49 | 2013-06-26 17:30 | 0 |  | Combined sewage was released into the basement of 714 Kentucky Street. | Rain 3.82 Combined sewage backed into the basement through a floor drain. The floor drain was plugged but combined sewage leaked around the plug. | See Report | SSO Basement Backup
11905 | 39146 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-26 12:01 | 2013-06-26 12:01 | 2013-06-26 17:30 | 0 |  | Combined sewer manhole at the intersection of Willow Street and Weller Ave. | Rain 3.82 inches Combined sewage and debris were noted around a manhole cover after a 3.82 inch rain in 2 hours. | See Report | SSO Reached Receiving Water
11905 | 39122 | IN0025577 | La Porte Sewage Department | La Porte | 2013-06-27 10:20 | 2013-06-27 17:30 | 2013-06-28 10:11 | 0 |  | WWTP CSO 2101 Boyd Blvd outfall 002 | LaPorte received 1.2 inches of rain on 5.25 storing 7.6MG of combined wastewater by 12/30am on 5.26.2013. LaPorte received and additional 3.82 inches of rain in 2 hours (5:00am to 7:00am) on 5/26/2013 and stored and additional 23.5 MG. At that point the CSO Lagoon wa full and overflowed 0.63 MG to Travis Ditch. | See Report | SSO Affected Private Property | Travis Ditch
| 43309 | No NPDES Permit | Baymont Inn | La Porte | 2013-12-14 20:05 | 2013-12-14 22:50 | 2013-01-28 02:21 | 5000 | gallons | 4128 S Franklin Street Ground/Swale | This revised report is being submitted to provide additional clarification. The Michigan City Sanitary District received a call fro a private business the Baymont Inn 4128 S. Franklin Street at approximately 8:05 PM stating that they were having a sewage backup. Upon arrival at 9:15 PM it became apparent that the problem was 100% the fault of the Baymont Inn as thier private sewer lateral line was clogged and the Michigan City Sanitary District Sewer line was flowing freely and unimpeded. | District staff directly notified hotel management/maintenance concerning the urgent situation recommending immediate attention by an appropriate contractor. Additionally District staff in an effort to help the Baymont Inn vacuumed overflowing manhole thus eliminating overflow until such times as a contractor was retained by owner. The MCSD also checked the manhole on serveral occasions on 12-15-13 to ensure that overflows were not reoccurring. A letter will be sent to the Baymont Inn explaining the need for proper operation and maintenance of their lateral line and explaining the need to notify IDEM in the future of such incidents.
45234 | 37033 |  | SHIPSHEWANA MUNICIPAL SEWAGE TREATMENT PLANT | Lagrange | 2013-05-20 11:00 | 2013-05-20 | 2013-05-20 | 0 |  | Grinder Pump shutoff adjacent area. | Untreated Release Homeowner didn t call in for inspector and connected without an inspector. Pump was shut off. | Pulled pump and repaired and charged homeowner Fined customer | SSO Occurred at Treatment Plant
45233 | 37689 |  | LAGRANGE COUNTY REGIONAL SEWER DISTRICT REGION B | Lagrange | 2013-06-08 12:00 | 2013-06-08 14:00 | 2013-06-10 13:17 | 0 |  | Pump breaker blown adjacent ground. | Untreated Release Power Failure Blown breaker for pump. | Checked pump and line double check pump breaker. | SSO Affected Private Property
45234 | 49507 | IN0040622 | SHIPSHEWANA MUNICIPAL SEWAGE TREATMENT PLANT | Lagrange | 2013-05-06 07:00 | 2013-05-06 23:59 | 2013-05-05 22:28 | 7000 | gallons | County Road 982 | a 45 degree elbow in a 7 inch SRR line developed a leak. After further research it was discovered that there was no leak | Erosion control installed to contain drainage. Inpect lines on a routine basis. | SSO Affected Private Property
45233 | 39961 | IN0060097 | LAGRANGE COUNTY REGIONAL SEWER DISTRICT REGION B | Lagrange | 2013-08-03 11:21 | 2013-08-04 11:21 | 2013-09-04 09:20 | 0 |  | Broken Discharge (Sewer Grinder) | The pressure discharge for the grinder of the homeowner broke. | Early and quick response. See Report
45233 | 39416 | IN0060097 (Region B) | LAGRANGE COUNTY REGIONAL SEWER DISTRICT REGION B | Lagrange | 2013-07-16 14:50 | 2013-07-16 03:50 | 2013-07-16 16:00 | 0 |  | 7185 E / 6505 Ground | Equipment failure. The end of a flushing connection broke off. The staff was able to shut off the shut off valve and stop the discharge. | Immediate response. Quick response. | SSO Affected Private Property
45235 | 37063 | IN0062014 | LAGRANGE COUNTY SEWER REGION A | Lagrange | 2013-05-21 01:30 | 2013-05-21 02:00 | 2013-05-22 13:38 | 120 | gallons | Grinder Pump 9250 E/430 S Ground adjacent to pump. | Untreated Release Equipment Failure Broken discharge on the grinder pump. | Preventative Maintenance Program Check Pumps | SSO Affected Private Property
45235 | 39801 | IN0062014 | LAGRANGE COUNTY SEWER REGION A | Lagrange | 2013-08-23 21:00 | 2013-08-23 13:00 | 2013-08-23 12:57 | 0 |  | 0515 E 0485S Ground | Cooper Trenching hit LCRUD s $ inch sewer line when boring a line. | Quick response and containment of leakage | SSO Affected Private Property
| 35841 |  |  | Lake | 2013-04-15 23:25 | 2013-04-16 10:15 | 2013-04-16 13:51 | 0 |  | 3rd and Wisconsin MH #505-018 Lake George. | Untreated Release Rain | All pumps 100% at Lift Station flow monitoring south mondel storm and sanitary rehab project underway. | SSO Affected Private Property | Lake George
25891 | 41554 | 0023060 Outfall 001 | HAMMOND SEWAGE TREATMENT | Lake | 2013-10-31 05:55 | 2013-10-31 13:50 | 2013-11-01 14:59 | 0 |  | Tertiary Filter Bypass Valve | Rain 2.94 inches Exceeded Max Capacity High secondary effluent flow and turbidity resulted in a high influent channel level at the Tertiary filter building necessitating the partial bypass of the process. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
11557 | 35052 | IN0000094 | ArcelorMittal USA Incorporated | Lake | 2013-02-06 | 2013-02-06 | 2013-02-08 14:36 | 0 |  | Pump House #6 at ArcelorMittal USA LLC Indiana Harbor East 3001 Dickey Road East Chicago IN 46312 | Overflow at #6 Pumphouse. Water overflowed the pumphouse surge well which is separated from the main water intake for the plant by a sheet pile wall and was immediately drawn back in to the main intake for use in the plant. Some of the water drawn into the plant would have bypassed Outfall 014 and instead discharged ou Outfall 011. | Continuing investigation to determine root cause of the overflow.
24442 | 36172 | IN0022829 | EAST CHICAGO SANITARY DISTRICT | Lake | 2013-04-18 | 2013-04-19 | 2013-04-19 08:55 | 0 |  | Multiple basements | Precipitation event resulted in multiple untreated releases into residential areas. | Received 4.7 of rain. Crews from East Chicago Sanitary District sent out to homes to help with water overflow in basements. | SSO Basement Backup
24442 | 38241 | IN0022829 | EAST CHICAGO SANITARY DISTRICT | Lake | 2013-06-27 18:50 | 2013-06-29 00:30 | 2013-07-02 09:31 | 0 |  | Plant Effluent Grand Calumet River | Power Failure Power outage NIPSCO switch from one power line to another but the line from the switch to the plant was down also. NIPSCO crews worked to repair line. Power was out for 30 hrs. | NIPSCO crews worked to repair line. Sanitary District maintenance crews set up generator at sand filters and plan pump station. The sanitary district has two power lines or feeds into plant when one feed is down another feed is switch on. Maintenance crews are advised and aware of what generators can be used and were to place them. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
24442 | 38242 | IN0022829 | EAST CHICAGO SANITARY DISTRICT | Lake | 2013-06-27 18:50 | 2013-06-29 00:30 | 2013-07-02 09:33 | 0 |  | OPlant Effluent | Power Failure power outage. NIPSCO switch from one power line to another but the line from the switch to the plant was down also. NIPSCO crews worked to repair line. Power was out for 30 hrs. | NIPSCO crews worked to repair line. Sanitary District maintenance crews set up generator at sand filters and plant pump station. The sanitary district has two power lines or feeds into plant when one feed is down another feed is switch on. maintenance crews are advised and aware of what generators can be used and where to place them. | SSO Occurred at Treatment Plant
24442 | 40241 | IN0022829 | EAST CHICAGO SANITARY DISTRICT | Lake | 2013-09-18 22:00 | 2013-09-19 13:00 | 2013-09-19 15:25 | 0 |  | See Report | Basement backups due to hydraulic overloads. (See Attachments) received over 3.7 of rain in 3 hours. | See Report | SSO Basement Backup
13872 | 35236 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-01-11 03:05 | 2013-01-11 04:35 | 2013-01-11 11:44 | 35 | gallons | Basement 1923 Tyler Court Gary IN | Main sewer line obstruction resulted in a basement backup and untreated release | Vactored main sewer line and removed heavy greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup; SSO Affected Private Property
13872 | 35483 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-01-16 11:30 | 2013-01-16 14:30 | 2013-01-17 06:55 | 100 | gallons | 3501 Georgia Street | Main sewer line obstructed by a heavy greasy substance caused an untreated release in a residential basement. | Vactored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup
13872 | 35665 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-01-22 10:35 | 2013-01-22 12:15 | 2013-01-22 13:48 | 15 | gallons | 1943 Main Street manhole | Main sewer line blockage with a greasy substance resulted in an untreated release from a manhole to surrounding ground. | Vactored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Reached Public Land
13872 | 35096 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-01-29 | 2013-01-29 23:05 | 2013-01-30 04:27 | 80 | gallons | 1216 East 41st Avenue Gary IN | Basement backup as a result of a precipitation event. | Line was serviced to correct the discharge. Line was serviced. | SSO Basement Backup
13872 | 35093 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-01-29 04:10 | 2013-01-29 05:15 | 2013-01-30 01:36 | 1300000 | gallons | Gary Sanitary District Gary IN | Possible precipitation event caused an otherwise unknown reason for bypass of treatment process | Flow was reduced through the plant to eliminate the overflow. An evaluation is necessary to determine cause and to prevent future recurrence. Relase was contained in the grounds and contact tanks. Recombined with final effluent and sampled.
13872 | 35191 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-01-29 04:10 | 2013-01-29 05:15 | 2013-01-30 04:27 | 800000 | gallons | Gary Sanitary District Gary IN | Treatment Process bypass due to high river level that reverted to the plant via trapezoid adn coupled with high plant flows. Update. Release recalculated and determined to be approximately 800000 gallons based on calculations used to determine bypass/overflow rates in the past. | Flow was reduced through the plant to eliminate the overflow. An evaluation is necessary to determine cause and find a solution to prevent future recurrence. | SSO Occurred at Treatment Plant
13872 | 35111 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-01-30 08:13 | 2013-01-30 10:30 | 2013-01-30 14:59 | 1000 | gallons | 1038 East 49th Avenue Gary IN | Basement back up released untreated waste into residential basement. | Vactored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restor capacity and reduce the potential for blockages. | SSO Basement Backup
13872 | 34847 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-02-16 | 2013-02-16 05:00 | 2013-02-16 07:11 | 100 | gallons | Issue occurred at the Treatment Plant located at 3600 West 3rd Avenue Gary IN | Found pressate well foaming over. Found one of 2 pumps tripped out. Placed the working pump in hand and turned of 1 of 3 belt filter presses due to too much poly in the return wanter and foaming up in the well. | Shoveled up foam. Having failed pump checked out and up and running ASAP. | SSO Occurred at Treatment Plant
13872 | 34862 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-02-20 12:30 | 2013-02-20 15:00 | 2013-02-20 15:30 | 150 | gallons | 7834 Indian Boundary | Main Sewer Line clogged with greasy substance and trash caused an untreated overflow. | Vactored main sewer line and removed greasy substance and trash. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup
13872 | 34815 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-02-27 16:20 | 2013-02-27 16:40 | 2013-02-27 19:45 | 25 | gallons | Gary Sanitary District Treatment Plant | Digester overflow at treatment plant | Transferred sludge from Primary Digester to Secondary digester to lower level to stop overflow. Continue to monitor digester level and check valve alignments. | SSO Occurred at Treatment Plant; Surface Soil
13872 | 35378 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-10 05:15 | 2013-03-10 06:20 | 2013-03-11 00:17 | 351000 | gallons | 3000 W. 3rd Ave | Bypass at treatment process. Due to snow melt and a rain event we had to open he 84 inch bypass gate to lower the water in the final clarifiers. |  | SSO Reached Receiving Water | Grand Calumet River
13872 | 34669 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-10 05:45 | 2013-03-10 06:20 | 2013-03-11 00:17 | 351000 | gallons | 3600 West 3rd Ave | Bypass of a Treatment Process Equipment Failure Due to snow melt and rain event we had to open the 84 bypass gate 5% to lower the weirs in the final clarifiers. The gate was opened at 5:45am and closed ant 620am the estimated amount released was 351000 gallons. |  | SSO Reached Receiving Water | Grand Calumet River
13872 | 34565 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-10 05:45 | 2013-03-10 06:20 | 2013-03-11 10:20 | 351000 | gallons | 3600 West 3rd St | Bypass of Treatment Process Equipment Failure. Due t Snow melt and a rain event we had to open the 84 bypass gate 5% to lower the weirs in the final clarifiers. The gate was opened at 5:45am and closed at 6:20am the estimated amount released was 351000 gallons. |  | SSO Reached Receiving Water | Grand Calumet River
13872 | 34518 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-10 05:45 | 2013-03-10 06:20 | 2013-03-11 10:20 | 351000 | gallons | 3600 West 3rd Ave Gary IN Grand Calumet River | Bypass of a Treatment Process Rain. Original document didn t go through to confirm the opening of the 84 Bypass Gate during the recent rain event and meltdown that occurred during the time and date mentioned above. | Follow up report submitted due to error in delivery of document sent previously. Closer monitoring response time streamlined to correlate with the increase in Plant Q during rain event. | SSO Reached Receiving Water | Grand Calumet River
13872 | 34627 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-10 19:00 | 2013-03-10 20:50 | 2013-03-10 22:45 | 10 | gallons | 5123 Indiana Place Gary IN Basement | Untreated Release Rain Sewer Back up into basement due to clogged sewer main. | The Collections Personnel were dispatched out to site. Jetted sewer main and restored flow. We will continue our program of cleaning televising and rehabilitate deteriorated sewers to remove sediment restore capacity minimize infiltration and reduce the potential blockages. | SSO Basement Backup
13872 | 34505 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-11 11:15 | 2013-03-11 14:30 | 2013-03-19 11:44 | 0 |  | 5345 & 5373 Delaware Street | Untreated Release Main sewer line contained a heavy greasy substance and roots | Vactored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup
13872 | 34671 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-12 11:30 | 2013-03-12 13:00 | 2013-03-12 13:39 | 0 |  | 244 East 21st Avenue Ground | Main sewer line contained a heavy greasy substance. | Vactored main sewer line and removed greasy substance Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Affected Private Property
13872 | 34728 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-16 13:30 | 2013-03-16 14:30 | 2013-03-16 14:37 | 250 | gallons | 6620 Hemlock Ave Residence basement | Untreated Release Rain Sewer backed up into basement due to clogged sewer main. | The collections personnel were dispatched out to site jetted sewer main and restored flow. We will continue our program of cleaning televising and rehabilitate deteriorated sewers to remove sediment restore capacity minimize infiltration and reduce potential blockage. | SSO Basement Backup
13872 | 35277 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-03-28 20:01 | 2013-03-28 21:50 | 2013-03-28 22:40 | 20 | gallons | 9220 Oak Ave Gary Indiana Basement Apartment | Untreated Release Plugged Sewer Line | Jetted out sewer line to free up the drain. Continue to monitor sewer lines and jet out sewers. | SSO Basement Backup
13872 | 35634 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-11 02:55 | 2013-04-11 08:00 | 2013-04-11 23:06 | 40 | gallons | 4080 Ohio St. Gary IN Basement. | Untreated Release Rain .48 inches Overflow was confined to the basement level of the residence. | Main sewer line was vactored and the blockage was cleared to correct the discharge. Line was serviced and will be monitored. | SSO Basement Backup
13872 | 35431 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-11 18:45 | 2013-04-11 23:00 | 2013-04-12 07:27 | 0 |  | 5233 Carolina Gary IN | Precipitation event triggered an Untreated Releae into the basement of a residence | Main sewer was rodded out and the blockage cleared. Line was serviced. | SSO Basement Backup
13872 | 35978 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-16 11:00 | 2013-04-16 16:15 | 2013-04-17 10:47 | 240000 | gallons | 2698 Calhoun Street Manhole | Lift station pumps malfunctioned causing sewer levels to rise in the area resulting in untreated release to the surrounding ground. | Pulled pumps for inspection. Removed debris lodged in the intake line. Increase frequency of monitoring and servicing of unit. | SSO Reached Public Land
13872 | 36146 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-18 14:00 | 2013-04-18 15:00 | 2013-04-19 12:19 | 0 |  | 720 East 20th Avenue | Main sewer line blockage and precipitation resulted in residential back up. | Vactored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup
13872 | 36504 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-19 13:00 | 2013-04-19 14:30 | 2013-04-19 14:57 | 0 |  | 6508 and 6516 East 3rd Place | Greasy substance blocking main sewer resulted in untreated release into residential basement. | Vactored main sewer line and removed greasy substance.Continue program to clean and remove sediment to restore capacity and reduce potential for blockages. | SSO Basement Backup
13872 | 36110 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-22 09:40 | 2013-04-22 11:20 | 2013-04-23 08:26 | 0 |  | 1228 Decatur Street Manhole Ground | Untreated Release Main sewer line contained a heavy greasy substance. | Vectored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Affected Private Property
13872 | 36108 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-22 12:15 | 2013-04-22 15:25 | 2013-04-23 08:25 | 0 |  | 1549 Pierce Street Basement | Untreated Release Main sewer line contained a heavy greasy substance. | Vactored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup
13872 | 36096 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-22 14:18 | 2013-04-22 16:30 | 2013-04-23 09:15 | 0 |  | 2725 Central Avenue House floor | Untreated Release Main sewer line blockage due to a heavy greasy substance in the main sewer line. | Vactored main sewer line and removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Affected Private Property
13872 | 36780 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-29 11:15 | 2013-04-30 09:20 | 2013-04-30 14:40 | 500 | gallons | 6932 East 1st Ave Gary IN Basement Floor | Main sewer line contained a heavy greasy substance and a cave-in at the site. | Removed Blockage Vactored main sewer line and removed greasy substance barricaded area. Schedule to service cave-in and repair pipe. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup; SSO Affected Private Property
13872 | 36733 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-04-29 23:15 | 2013-04-30 09:20 | 2013-04-30 14:36 | 500 | gallons | 6932 East 1st Avenue | Main sewer blockage and cave in resulted in runtreated release into residential basement. | Vactored main sewer and removed greasy substance barricaded area. Schedule to service cave-in and repair pipe. continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Basement Backup; SSO Affected Private Property
13872 | 36796 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-09 09:00 | 2013-05-09 11:00 | 2013-05-10 08:47 | 150 | gallons | 1213 Decatur Street Main Floor | Main sewer line contained a heavy greasy substance. | Removed blockage vactored and cleaned main sewer line removed greasy substance. Continue program to clean and remove sediment to restore capacity and reduce the potential for blockages. | SSO Affected Private Property
13872 | 37766 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-10 05:04 | 2013-05-10 06:30 | 2013-06-11 00:40 | 954063 | gallons | 84 Bypass gate to contact tanks | Rain Due to rain event we lost the weir over flow to the final clarifiers and the trapezoid area connected to the contact zone. We had to open the 84 bypass gate to 15% to lower the levels of the finals and the trapezoid are. After the flow slowed down the gate was closed back to 1000% closed amount bypassed is estimated to be around 954063 gallons. |  | SSO Occurred at Treatment Plant
13872 | 36814 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-10 05:35 | 2013-05-10 05:45 | 2013-05-10 23:36 | 58000 | gallons | Wiesman screen to contact tanks. | Equipment Failure Du to the wiesman filter screen tripping out the water backed up in the final clarifiers causing the weirs to be submerged we had to open the 84 bypass gala 10% to release the pressure on the wiesman screen belt before we were able to restart the screen. After the wiesman was restarted the 84 gate was closed 100% |  | SSO Occurred at Treatment Plant
13872 | 37014 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-14 09:20 | 2013-05-16 18:10 | 2013-05-17 11:26 | 0 |  | East & West Main Sluice Gates were reopened 100% and security seals installed. | Treatment Bypassed Equipment Failure Repair work has been completed on the Trash rack and the Gales has been reunited to there original position. The Bypass Gate has been closed and the East and West main Sluice Gates has been reopened 100% | Remove Blockage Debris build-up on the Trash Rack was removed. | SSO Occurred at Treatment Plant
13872 | 37043 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-14 09:20 | 2013-05-16 18:10 | 2013-05-17 11:20 | 0 |  | East & West Main Sluice Gates were reopened100% and security seals installed. | Treatment Bypass Equipment Failure Repair work has been completed on the Trash Rack and the Gates has been returned to their original position. The Bypass Gates has been closed and the East and West main Sluice Gates has been reopened 100%. | Debris build-up on the Trash Rack was removed. New support brackets were installed to the Trash Rack and the bars were straightened out. | SSO Occurred at Treatment Plant
13872 | 36865 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-15 09:20 |  | 2013-05-15 09:41 | 0 |  | E & W Main Sluice Gate Closed | Equipment Failure The reason for the Bypass Reports being issued is that we are in the process of repairing the support bracket to the bars to the Trash Rack. Damages to the bow is causing a build-up of trash and debris on the rack. | We are presently in the process of repairing support brackets that had caused a bow in the bar rack area to the Trash Rack. As a result of the damages to the rack debris is building up. Once the Trash Rack support brackets has been repaired we will resume our original set up prior to the work being done. That being Plant Q will travel thru the 96th interceptor via the East Main Slulce Gate and the West main slucie Gale at the Headworks. | SSO Occurred at Treatment Plant
13872 | 37154 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-25 06:09 | 2013-05-25 07:55 | 2013-05-25 21:42 | 40 | gallons | 1118 North County Line Road Gary Indiana Residential Basement | Untreated Release Plugged Sewer Line. Resident estimated amount of release in the home. | Jetted out sewer line to free up the drain. Continue to monitor sewer lines and jet out sewers. | SSO Basement Backup
13872 | 37198 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-05-28 22:40 | 2013-05-29 12:30 | 2013-05-29 22:46 | 9045833 | gallons | Effluent Bypass Gate closed 100% | Treatment Bypass Exceeded Max Capacity Precipitation 1.13 inches. Excessive rain conditions. Plant exceeded maximum capacity of treatment process. | Continue to follow the wet weather plan. | SSO Occurred at Treatment Plant
13872 | 37786 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-10 13:45 | 2013-06-10 15:30 | 2013-06-11 15:34 | 500 | gallons | 2040 Pennsylvania Street Basement Backup House Lateral | House Lateral Basement Backup | Vactored main sewer line and removed greasy substance. Continue to clean and remove sediment to restore capacity and reduce the potential for blockage. | SSO Basement Backup
13872 | 38861 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-21 12:15 | 2013-06-21 14:40 | 2013-06-21 15:25 | 0 |  | 2118 Wisconsin St Ground | Manhole main sewer line contained a heavy greasy substance. | Removed Blockage Vactored and cleaned main sewer line removed greasy substance | SSO Affected Private Property
13872 | 39082 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-26 09:10 | 2013-06-26 12:15 | 2013-08-07 10:17 | 0 |  | 84 Bypass Gate | Equipment Failure Heavy rainfall and weisman screen presently out of service. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water
13872 | 39085 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-27 10:37 | 2013-06-27 13:30 | 2013-06-27 14:34 | 0 |  | 1109 East 45th Ave Basement Floor | Main sewer line contained a heavy greasy substance. | See Report | SSO Basement Backup; SSO Affected Private Property
13872 | 39179 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-28 21:30 | 2013-06-29 02:18 | 2013-06-29 06:32 | 0 |  | 84 bypass gate to contact tanks | Due to rain event we lost the welr over flow to the final clarifiers. We had to open the 84 bypass gate to 15% to lower the levels of the finals. After the flow slowed down the gate was closed back to 100% closed amount bypassed is estimated to be around 3711000gal | See Report | SSO Occurred at Treatment Plant
13872 | 39619 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-30 10:00 | 2013-06-30 12:00 | 2013-07-30 15:06 | 0 |  | 7820 Indian Boundary Basement Floor | Main sewer line contained sand infiltration | Removed Blockage See Report | SSO Basement Backup; SSO Affected Private Property
13872 | 39618 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-30 10:00 | 2013-06-30 12:00 | 2013-08-22 14:44 | 0 |  | 7820 Indian Bondary Basement Floor | Main sewer line contained sand infiltration. | Removed Blockage See Report | SSO Basement Backup; SSO Affected Private Property
13872 | 39617 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-30 10:00 | 2013-06-30 12:00 | 2013-07-30 16:01 | 0 |  | 7820 Indian Boundary Basement Floor | Main sewer line contained sand infiltration. | Removed Blockage See Report | SSO Basement Backup; SSO Affected Private Property
13872 | 39534 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-07-08 13:25 | 2013-07-09 01:15 | 2013-07-09 07:32 | 0 |  | 84 bypass gate to contact tanks | Rain .95 inches Due to rain event we lost the weir over flow to the final clarifiers we had to open the 84 bypass gate to 20% to lower the levels of the finals. After the flow slowed down the gate was closed back to 100% closed amount bypassed is estimated to be around 9100.000 gal. |  | SSO Occurred at Treatment Plant
13872 | 39735 | IN0022977 | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-08-02 18:01 | 2013-08-02 09:58 | 2013-08-03 14:23 | 0 |  | 84 bypass gate to contact tanks. | Rain Due to rain event we lost the weir over flow to the final clarifiers. We had to open the 84 bypass gate to 25% to lower the levels of the finale. after the flow slowed down the date was closed back to 100% closed amount bypassed is estimated to be around 5500.00 gal. |  | SSO Occurred at Treatment Plant
13872 | 41065 | IN0022977 Outfall 001A | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-10-08 14:40 | 2013-10-08 08:37 | 2013-10-08 16:20 | 0 |  | 1134 Floyd St Ground | Blockage | Removed Blockage See Report
13872 | 42584 | IN0022977 Outfall 001A | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-12-19 14:06 | 2013-12-19 14:06 | 2013-12-19 09:30 | 0 |  | 4065 East 15th Place Force Main Ground | Pipe Failure | See Report
13872 | 41084 | IN0022977 Outfall 001A 001B | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-10-14 20:13 | 2013-10-14 21:30 | 2013-10-15 22:30 | 0 |  | 1017 Chase St Stopped | Unknown Excessive grease build up in the line. | Removed Blockage See Report | SSO Basement Backup
13872 | 42214 | IN0022977 Outfall 001A & 001B | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-11-29 09:30 | 2013-11-29 09:45 | 2013-11-27 12:19 | 0 |  | 1237 N Wayne Street | Electrical had tripped out. | Repaired Pump Station See Report
13872 | 42217 | IN0022977 Outfall 001A & 001B | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-11-29 13:40 | 2013-11-29 14:20 | 2013-11-29 17:06 | 0 |  | Lake Shore Dr East | Lake Shore Dr East | Repaired Pump Station See Report.
13872 | 42102 | IN0022977 Outfalls 001A & 001B | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-11-22 15:30 | 2013-11-22 17:30 | 2013-11-23 12:31 | 0 |  | 1975 West Ridge Road | Unknown excessive grease buildup in line | Removed Blockage See Report
13872 | 42212 | IN0022977 Outfall 001A 001B | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-11-27 09:30 | 2013-11-27 09:45 | 2013-11-27 13:16 | 0 |  | 1237 N Wayne Street | Electrical had tripped out Manhole. | Repaired Pump Station See Report
25891 | 35505 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-01-11 03:44 | 2013-01-11 12:00 | 2013-01-14 08:37 | 14300000 | gallons | Tertiary Bypass Valve WWTP | Precipitation event resulted in bypass of a treatment process which was blended with final effluent and sampled. Discharge was partially treated before release into receiving water. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with Tertiary filter efflunt prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 35088 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-01-29 03:20 | 2013-01-29 23:59 | 2013-02-01 13:23 | 9540000 | gallons | Hammond Sanitary District Hammond IN | High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitationg the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximaize flows during wet weather events in order to ninimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with Tertiary filter efflunt prior to the contact tank. The final efflunt for HSD is sampled after the flows are recombined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 35089 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-01-30 | 2013-01-30 19:45 | 2013-02-01 13:22 | 14170000 | gallons | Hammond Sanitary District plant Hammond IN | High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow not action planned. HSD is required to maximize flows during we weather events in order to minimize CSO dischare events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. ar recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are recombined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 34865 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-02-18 23:40 | 2013-02-18 | 2013-02-20 09:22 | 56000 | gallons | Tertiary Bypass valve at Hammond Sanitary District Treatment Plant | High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. Partially Treated Release | filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with Tertiary filter effluent prior to the contact tank. the final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 34868 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-02-19 | 2013-02-19 06:00 | 2013-02-20 09:22 | 10890000 | gallons | Hammond Sanitary District WWTP Hammond IN | High secondary effluent flow and turbidity resulted ina high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a reault hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 34475 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-03-10 06:40 | 2013-03-10 | 2013-03-10 | 318600 | gallons | Tertiary Bypass Valvue | Partially Treated Release Bypass of the Treatment Process Blended with final Effluent & Sampled Rain 0.83 inches. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 34476 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-03-11 | 2013-03-11 | 2013-03-11 | 34450000 | gallons | Tertiary Bypass Valve | Partially Treated Release Bypass of Treatment Process Blended with final Effluent & Sampled Rain 0.08 High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary Bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 34436 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-03-12 | 2013-03-12 09:20 | 2013-03-13 13:16 | 640000 | gallons | Teriary bypass valve. | Partially Treated Release Bypass of a Treatment Process Blended with Final effluent & Sampled. High secondary effluent flow and turbidity resulted in a high alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to maximize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 35572 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-11 02:30 | 2013-04-11 08:18 | 2013-04-11 11:16 | 12040000 | gallons | Tertiary Bypass valve Grand Calumet River | Partially Treated Releases Bypass of a Treatment Process blended with Final Effluent & SampledHigh secondary effluent flow an turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Teriary bldg. are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 35402 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-11 13:00 | 2013-04-11 23:59 | 2013-04-12 11:25 | 20133000 | gallons | Hammond Sanitary District Treatment Plant Hammond IN | A precipitation event resulted in high secondary effluent flow and turbidity causing a high level alarm for the influent channel forcing a partial bypass of the Tertiary Filter Building. Effluent was recombined with Final Effluent and sampled before discharge. | Filter backwash frequency increased. For flow no action planned. HSD is required tomaximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 35818 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-12 | 2013-04-12 04:00 | 2013-04-15 11:36 | 66000000 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Bypass of Treatment Process Blended with Final effluent & Sampled Rain 0.03 inches. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary Treatment Stage. All partial bypasses of the Tertiary Bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant | Grand Calumet River
25891 | 35875 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-15 22:10 | 2013-04-16 | 2013-04-16 12:55 | 0 |  | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Bypass of a Treatment Process Rain 0.88 inches. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary Bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 35842 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-15 22:10 | 2013-04-16 12:00 | 2013-04-16 13:55 | 0 |  | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Blended with Final Effluent & Sampled Rain 0.88 inches. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased/ For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary Bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 36038 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-16 | 2013-04-16 06:00 | 2013-04-17 13:13 | 12300000 | gallons | Tertiary Bypass Valve - WWTP | Precipitation event. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Building. Result is a partially treated release from the WWTP to receiving waters. | Filter backwash frequency increased. For flow no action is planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a resut hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 35685 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-17 20:15 | 2013-04-18 | 2013-04-18 12:11 | 0 |  | Tertiary Bypass valve Grand Calumet River | Partially Treated Release Rain 1.58 inches High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. |  | Grand Calumet River
25891 | 35689 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-17 20:15 | 2013-04-18 | 2013-04-18 12:14 | 4000000 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Rain 1.58 inches High secondary effluent flow and turgidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary Bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 36183 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-18 04:30 | 2013-04-18 07:30 | 2013-04-24 11:45 | 8800000 | gallons | Secondary Bypass Grand Calumet River | Rain 3.65 inches Tertiary filter building influent pumps failed in the opening of the secondary bypass valve. | Tertiary influent pumps returned to service. | SSO Reached Receiving Water | Grand Calumet River
25891 | 36422 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-20 | 2013-04-20 23:59 | 2013-04-22 13:13 | 18050 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Bypass of the Treatment Process Blended with Final Effluent & Sampled High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the tertiary treatment stage. All partial bypass of the Tertiary Bldg. are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant | Grand Calumet River
25891 | 36188 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-21 | 2013-04-21 21:45 | 2013-04-24 11:45 | 18240 | gallons | Columbia Ave Outfall #002 Grand Calumet River | Untreated Release Rain 6.17 inches Continuation of rain event. |  | SSO Reached Receiving Water | Grand Calumet River
25891 | 36419 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-21 | 2013-04-21 23:59 | 2013-04-22 13:41 | 18700 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Blended with Final effluent & Sampled High secondary effluent flow and turbidity resulted in a high alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant | Grand Calumet River
25891 | 36205 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-21 00:01 | 2013-04-21 23:59 | 2013-04-24 11:46 | 890000 | gallons | Forest Ave - Outfall #011 Little Calumet River | Untreated Release Rain 6.17 inches. Continuation of rain event. |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36190 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-21 00:22 | 2013-04-21 23:10 | 2013-04-24 11:46 | 2240000 | gallons | Sohl Ave-Outfall #004 Continuation of rain event. | Untreated Release Rain 6.17 inches Continuation of rain event. |  | SSO Reached Receiving Water | Grand Calumet River
25891 | 36194 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-21 00:36 | 2013-04-21 11:39 | 2013-04-24 11:46 | 2310000 | gallons | Kennedy Ave - Outfall #005 Grand Calumet River | Untreated Release Rain 6.17 inches Continuation of rain event. |  | SSO Reached Receiving Water | Grand Calumet River
25891 | 36209 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-21 10:15 | 2013-04-21 10:17 | 2013-04-24 11:47 | 420000 | gallons | Calumet -Munster Outfall #014 Little Calumet River | Untreated Release Rain 6.17 inches |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36203 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-21 12:27 | 2013-04-21 18:55 | 2013-04-24 11:46 | 540000 | gallons | Jackson Ave - Outfall #010 Little Calumet River | Untreated Release Rain 6.17 inches. Continuation of rain event. |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36189 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-22 | 2013-04-22 11:45 | 2013-04-24 11:45 | 1620000 | gallons | Columbia Ave- Outfall #002 Grand Calumet River | Untreated Release Rain 6.17 inches Continuation of rain event. |  | SSO Reached Receiving Water | Grand Calumet River
25891 | 36185 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-22 | 2013-04-22 | 2013-04-24 11:45 | 15800000 | gallons | Tertiary Filter Bypass Grand Calumet River | Partially Treated Release Bypass of a Treatment Process Blended with final Effluent & Sampled Replacing filter media in #7 filter. Bypass in auto set to open at 20 influent channel level. | Maximizing flow through remaining 7 filters. All partial bypasses of the Tertiary filter building are recombined with Tertiary filter effluent prior to the contact tank. The final effluent is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 36207 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-22 00:03 | 2013-04-22 23:59 | 2013-04-24 11:47 | 770000 | gallons | Forest Ave - Outfall #011 Little Calumet River | Untreated Release Rain 6/17 inches Continuation of rain event. |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36197 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-22 00:14 | 2013-04-22 23:15 | 2013-04-24 11:46 | 3710000 | gallons | Kennedy Ave- Outfall #005 Grand Calumet River | Untreated Release Rain 6.17 inches Continuation of rain event. |  | SSO Reached Receiving Water | Grand Calumet River
25891 | 36191 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-22 00:14 | 2013-04-22 23:30 | 2013-04-24 11:16 | 1950000 | gallons | Sohl Ave - Outfall #004 Grand Calumet River | Untreated Release rain 6.17 inches. Continuation of rain event. |  | SSO Reached Receiving Water | Grand Calumet River
25891 | 36199 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-22 11:12 | 2013-04-22 22:50 | 2013-04-24 11:46 | 1520000 | gallons | Walnut Ave - Outfall #008 Little Calumet River | Untreated Release Rain 6.17 inches Continuation of rain event. |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36211 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-22 11:35 | 2013-04-22 19:55 | 2013-04-24 11:47 | 1140000 | gallons | Calumet-Munster Outfall #014 Little Calumet River | Untreated Release Rain 6.17 inches Little Calumet River |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36186 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-23 | 2013-04-23 | 2013-04-24 11:45 | 1008000 | gallons | Tertiary Filter Bypass Grand Calumet River | Partially Treated Release Bypass of a Treatment Process Blended with Final Effluent & Sampled Equipment Failure. Replacing filter media in #7 filer. Bypass in auto set to open at 20 influent channel level. | Maximinizing flow through remaining 7 filters. All partial bypasses of the Tertiary filter building are recombined with Tertiary filter effluent prior to the contact tank. The final effluent is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 36701 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-24 | 2013-04-27 | 2013-04-29 13:17 | 41410000 | gallons | #7 Tertiary Filter In WWTP | Tertiary Filter bypass while replacing the filter media resulted in a treatement process bypass and a partially treated release to receiving water. | Maximizing flow through remaining 7 filters. Replacing filter media in #7 filter. Bypass in auto and set to open at a 20 influent channel level. All partial bypasses of the Tertiary filter building are recombined with the filter efflent prior to the contact tank. The final effluent is sampled after the flows are recombined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 36700 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-27 14:12 | 2013-04-27 14:30 | 2013-04-29 13:16 | 1000 | gallons | Forest Avenue Pump Station Outfall #011 | Flow from precipitation event(s) exceeded capacity of a Pump Station resulting in an untreated release to receiving water. |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36744 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-30 04:08 | 2013-04-30 04:20 | 2013-05-01 09:41 | 170000 | gallons | Walnut Avenue Pump Station - Outfall 008 | Construction of force main required pumping station to be shut down resulting in an untreated release from the pumping station to receiving water. |  | SSO Reached Receiving Water | Little Calumet River
25891 | 36840 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-05-10 01:18 | 2013-05-10 09:00 | 2013-05-13 11:08 | 1810000 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Bypass of a treatment Process Blended with final effluent & sampled Rain 0.87 inches. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wert weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary Bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 37140 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-05-21 01:30 | 2013-05-21 09:00 | 2013-05-24 08:50 | 5240000 | gallons | Tertiary Bypass valve Grand Calumet River | Partially Treated Release Bypass of a Treatment Process Blended with Final Effluent & Sampled #5 Tertiary filter is out of service for media replacement. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the tertiary bldg. are recombined with Tertiary filter prior to the contact tank. The final effluent for HSD sis sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 37201 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-05-28 04:05 | 2013-05-28 08:35 | 2013-05-28 11:21 | 2600000 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treatment Release Bypass of a Treatment Process Blended with final effluent & sampled. #5 Tertiary filter is out of service for media replacement. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to believe hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 37512 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-05-29 02:10 | 2013-05-29 08:05 | 2013-05-29 13:05 | 4500000 | gallons | Tertiary Bypass Valve at Hammond Sanitary District WWTP | Precipitation event triggered high secondary effluent flow and turbidity resulting in high level alarm for the influent channel level necessitating a partial bypass of the Tertiary Filter Building #5 Tertiary filter is out of service for media replacement. Partially treated release to receiving water. | Filter backwash frequency increased. No action planned for flow. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of tertiary building are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 37585 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-05-30 22:50 | 2013-05-30 23:59 | 2013-06-03 13:22 | 2417000 | gallons | Hammond Sanitary District WWTP | Precipitation event caused high secondary effluent flow resulting in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Building. Combined effluent reached receiving waters. | Filter backwash frequency increased. For flow no action planned. HSD is reuired to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with the Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 37584 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-05-31 | 2013-05-31 07:35 | 2013-06-03 13:20 | 14620000 | gallons | Hammond Sanitary District WWTP | Precipitation event flow caused high secondary effluent flow resulting in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Building. Combined effluent reached receiving waters. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary Building are recombined with the Tertiary filter effluent prior to the contact tank. The final effluen for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 37620 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-06-02 00:02 | 2013-06-02 08:45 | 2013-06-03 13:23 | 3671000 | gallons | Hammond Sanitary District WWTP | High secondary effluent flow triggered by a precipitation event resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Building to receiving water. | Filter backwash frequency is increased.For flow no action planned. HSD is required to maximized flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg. are recombined with the Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 37759 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-06-06 11:59 | 2013-06-06 13:31 | 2013-06-10 09:36 | 3500000 | gallons | Secondary Bypass Valve | Power failure Exceeded Max Capacity. Secondary effluent bypass open due to plant wide power outage. |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 37961 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-06-13 02:30 | 2013-06-13 08:00 | 2013-06-17 09:55 | 13700000 | gallons | Secondary Bypass Grand Calumet River | Rain 0.99 inches Equipment Failure | Scheduled repair of Tertiary bypass valve. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 39483 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-07-01 08:36 | 2013-07-01 08:48 | 2013-07-02 13:26 | 0 |  | Outfall #008 Walnut Pump Station | Rain 0.99 inches Equipment Failure Programmable Logic Controller at the Southside Pump Station failed casing sewer to overflow wier board to the Walnut Pump Station. | See Report | SSO Reached Receiving Water | Little Calumet River
25891 | 39965 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-08-30 18:50 | 2013-08-31 01:00 | 2013-09-03 11:43 | 0 |  | Columbia Ave Pumping Station Outfall #002 | Fuses blown at main substation due to intense thunderstorm and high winds. NIPSCO replaced fuses power restored at 1:00am | As soon as power was restored plant flow was maximized to reduce CSO discharge. No action planned. | SSO Reached Receiving Water | Grand Calumet River
25891 | 40379 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-09-18 09:50 | 2013-09-18 09:50 | 2013-09-25 13:47 | 0 |  | Pipe break 36 inch forcemain Robertsdale Station about 75 ft from siphon under IHC. | Equipment Failure 36 inch from Robertsdale Pump Station broke during heavy rains on 9/8/13. Location of failure approx 75 ft from Lake George Brunch of Indiana Harbor Canal. Evidence of sinkhole suggests wastewater ran over the ground towards the canal. HSD visit to site on 9-20-13 the leak was not active or overflowing. Unknown how much or for how long the overflow occurred. during the rain event Pipe located on British Petroleum Property BP notify HSD of sinkhole on (-19-13. | See Report
25891 | 40244 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-09-18 21:30 | 2013-09-18 12:00 | 2013-09-20 07:20 | 0 |  | Treatment Bypassed Tertiary Filter Bypass Valve | Rain 2.86 inches Exceeded Max Capacity High secondary effluent flow and the #8 Tertiary filter is out of service for media replacement resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Building. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 40245 | IN0023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-09-19 12:10 | 2013-09-19 05:40 | 2013-09-20 07:20 | 0 |  | Tertiary filter Bypass Valve | High secondary effluent flow and the #8 Tertiary filter is out of service for media replacement resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Building. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 40934 | IN0023060 Outfall 001 | HAMMOND SEWAGE TREATMENT | Lake | 2013-10-08 10:45 | 2013-10-08 15:00 | 2013-10-11 12:00 | 0 |  | 5143 Columbia Ave Hammond In 46327 | Construction Related 10/8/13 10:45am Excavation contractor- Bowen engineering -hit and broke a chlorine gas line. HSD personnel near the site immediately closed the supply valve-estimate 2 min of gas escaped to air (1.4lbs gas). Line repaired vacuum re-established chlorination of effluent returned at 3pm | Repaired Pipe Contractor was terminated. |  | Grand Calumet River
25891 | 42000 | IN0023060 Outfall 001 | HAMMOND SEWAGE TREATMENT | Lake | 2013-11-17 17:40 | 2013-11-18 14:28 | 2013-11-19 14:19 | 0 |  | Teriary Filter Bypass Valve | Rain 0.91 inches High secondary effluent flow and turbidity resulted in a high inffluent channel level at the Tertiary filter building necessitating the partial bypass of the process. | See Report |  | Grand Calumet River
25891 | 43307 | IN0023060 Outfall 001 | HAMMOND SEWAGE TREATMENT | Lake | 2013-12-21 21:24 | 2013-12-21 | 2013-12-24 12:10 | 5386000 | gallons | Tertiary Filter Bypass Valve | Exceeded Max Capacity Rain 0.42 inches high secondary effluent flow and turbidity resulted in a high influent channel level at the Tertiary filter building necessitating the partial bypass of the process. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
25891 | 43306 | IN0023060 Outfall 001 | HAMMOND SEWAGE TREATMENT | Lake | 2013-12-22 | 2013-12-22 07:20 | 2013-12-24 12:09 | 15701000 | gallons | Tertiary filter Bypass Valve | Exceeded Max Capacity Rain 0.08 inches High secondary efluent flow and turbidity resulted in a high influent channel level at the Tertiary filter building necessitating the partial bypass of the process. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Grand Calumet River
20807 | 42539 | IN0023621 | DALECARLIA UTILITIES | Lake | 2013-12-16 04:00 | 2013-12-16 06:00 | 2013-12-16 13:38 | 0 |  | MH #395 6700 Block of 145th Lift station #3 | Equipment Failure | See Report | SSO Reached Receiving Water | Cedar Creek
20807 | 42568 | IN0023621 | DALECARLIA UTILITIES | Lake | 2013-12-16 04:00 | 2013-12-16 06:00 | 2013-12-16 09:50 | 0 |  | MH #395 6700 Block of 145th NE Cedar Creek | Equipment Failure | See Report | SSO Reached Receiving Water | Cedar Creek
12075 | 35927 | IN0024457 | Schererville Waste Water Treatment Plant | Lake | 2013-04-17 09:00 | 2013-04-17 10:00 | 2013-04-17 08:58 | 500 | gallons | Manhole @ 83rd Lane 7740 Retention Pond | Untreated Release Equipment Failure Sewer was plugged between 8365 Blaine Place and 7650 83rd lane. Once the Public Works department jetted the line between these two points the overflow stopped. We did have about an inch of rain that night cleaned up area of minor debris. | We jetted the line out due to sewer plug. Once we have a dry spell in precipitation we are going to schedule sending the sewer camera up the pipe to see if there are any tree roots or debris in the line. | SSO Affected Private Property
12075 | 37534 | IN0024457 | Schererville Waste Water Treatment Plant | Lake | 2013-06-02 18:30 | 2013-06-02 19:30 | 2013-06-06 14:00 | 50 | gallons | 1109 Old Lincoln Hwy Schererville | Equipment Failure Town sewer line was plugged. The resident at 1109 Old Lincoln Hwy had about an inch of water around the floor drain in the basement. | The town sewer pipe had a block within it once the blockage was cleared by Public Works Staff the water began to recede in the basement of the residents home. The sewer pipe is on the list to jet out periodically as a preventative maintenance measure. | SSO Basement Backup
12075 | 37550 | IN0024457 | Schererville Waste Water Treatment Plant | Lake | 2013-06-10 13:30 | 2013-06-10 22:00 | 2013-06-10 15:00 | 26138 | gallons | 717 Morraine Trace Schererville | Equipment failure resident started about 5 in dwelling. Town sewer line was plugged. | The Town sewer pipe had a block within it once the blockage was cleared by Public Works Staff the water started to recede in the residence. The sewer pipe is on the list to jet out periodically as a preventative measure. | SSO Affected Private Property
12075 | 43308 | IN0024457 | Schererville Waste Water Treatment Plant | Lake | 2013-12-26 16:00 | 2013-12-26 18:00 | 2013-12-27 13:32 | 0 |  | 8167 Surbin Terrace Crown Point In | Equipment Failure Basement Back-Up Sewer Line on 81st place was plugged. Employee saw water in basement but unable to estimate how much water exactly as it had reseeded by the time he got there. | See Report
1640 | 35617 | IN0033081 | LAKE DALECARLIA REGIONAL WASTE DISTRICT | Lake | 2013-01-02 | 2013-01-02 23:59 | 2013-01-08 09:20 | 0 |  | In the road | Cracked Force Main feeding to WWTP resulted in an untreated release of unknown proportion. | Contractor on site who cleaned up sewage release from cracked main. Parts were picked up and repairs made that same day. | SSO Reached Public Land; Subsurface Soil (> 6 inches deep)
17381 | 35547 | IN0037176 | TWIN LAKES UTILITIES | Lake | 2013-04-04 09:00 | 2013-04-04 10:18 | 2013-04-04 14:48 | 390 | gallons | MH 211 Sewer Main Backup Ground | Untreated Release Equipment FailureCleaned and televised sewer main. Problem found to be root infiltration into sewer main. Roots were remove and section of sewer main scheduled for replacement. | Applied lime to area We are currently identifying and repairing sources of I&I | SSO Affected Private Property
17381 | 40270 | IN0037176 | TWIN LAKES UTILITIES | Lake | 2013-09-21 13:10 | 2013-09-21 13:13 | 2013-09-22 09:20 | 0 |  | N Lakeshore Dr (Pro Shop) | Construction Related Construction site trash pump discharge hose leak. | Repair hose applied lime to area | SSO Affected Private Property
12072 | 35069 | IN0039331 | DYER WASTE WATER TREATMENT PLANT | Lake | 2013-01-29 19:00 | 2013-01-30 15:00 | 2013-02-05 10:23 | 1143000 | gallons | Dyer Wastewater Treatment Plant Dyer IN | Partial bypass of tertiary filters due to high flows caused by snow melt. | Bypassed flow was remixed with the tertiary treated effluent in the dechlorination chamber which is prior to the parshall flume and fial efflunt autosampler. | SSO Occurred at Treatment Plant
12072 | 34449 | IN0039331 | DYER WASTE WATER TREATMENT PLANT | Lake | 2013-03-10 04:50 | 2013-03-11 23:30 | 2013-03-13 22:20 | 3232000 | gallons | Secondary Clarifiers (Before Tert Filters) Chlorine Contact Chamber | Rain event of <0.5 inches. This was a partial bypass of the tertiary filters due to high flows caused by melting snow. The bypassed flow was remixed with the tertiary treated effluent in the dechlorination chamber which is prior to the parshall flume and final effluent auto sampler. |  | SSO Affected Private Property
12072 | 35412 | IN0039331 | DYER WASTE WATER TREATMENT PLANT | Lake | 2013-04-11 00:10 | 2013-04-11 23:40 | 2013-04-12 08:41 | 1120000 | gallons | Dyer WWTP Dyer IN | Precipitation event caused high flows and partial bypass of the tertiary filters. Bypassed flow was remixed with the tertiary treated effluent in the dechlorination chamber which is prior to the parshall flume and final effluent autosampler. | No further action taken. | SSO Occurred at Treatment Plant
12072 | 35980 | IN0039331 | DYER WASTE WATER TREATMENT PLANT | Lake | 2013-04-15 18:45 | 2013-04-16 23:50 | 2013-04-17 08:37 | 2096000 | gallons | Dyer Wastewater Treatment Plant | Precipitation event caused high flows at the WWTP which caused a treatment bypass. Effluent was bypassed from Secondary Clarifiers (before Tertiary Filters) to the Chlorine Contact Chamber. | The bypassed flow was remixed with the tertiary treated effluent in the dechlorination chamber which is prior to the parshall flume and final effluent autosampler. | SSO Occurred at Treatment Plant
12072 | 36091 | IN0039331 | DYER WASTE WATER TREATMENT PLANT | Lake | 2013-04-17 17:20 | 2013-04-20 20:20 | 2013-04-23 09:56 | 0 |  | Secondary Clarifiers (Before Tert Filters) | Rain 2.80 This was a partial bypass of the tertiary filters due to high flows. The bypassed flow was remixed with the tertiary treated effluent in the dechlorination chamber which is prior to the pasrhall flume and final effluent autosampler. |  | SSO Occurred at Treatment Plant
12072 | 37839 | IN0039331 | DYER WASTE WATER TREATMENT PLANT | Lake | 2013-06-12 19:15 | 2013-06-13 07:00 | 2013-06-13 10:04 | 1367000 | gallons | Bypass of Tertiary Treatment System | Exceeded Max Capacity Rain 1.87 inches. This was a partial bypass of the tertiary filters due to high flows. The bypassed flow was remixed with the tertiary treated effluent in the dechlorination chamber which is prior to the parshall flume and final effluent autosampler. |  | SSO Occurred at Treatment Plant
12072 | 41716 | IN0039331 Outfall 001 | DYER WASTE WATER TREATMENT PLANT | Lake | 2013-11-06 06:50 | 2013-11-06 12:25 | 2013-11-07 11:00 | 0 |  | Bypass of Tertiary Treatment System | Rain 0.86 inchesExceeded Max Capacity this was a partial bypass of the lertiary filters due to the high flows. The bypassed flow was remixed with the lertiarty treated effluent in the dechlorination chamber which is prior to the parshall flume and final effluent auto sampler. | See Report | SSO Occurred at Treatment Plant
19346 | 36218 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-04-17 21:00 | 2013-04-19 10:00 | 2013-04-20 14:12 | 3015443 | gallons | Manhole #3005 at Entrance to Homestead Park (18868 gallons) Manhole #1230 at 8231 5th Street (2145640 gallons) Manhole #1345 at 8505 5th Street (869.803 gallons) Storm Sewer | Untreated Release Rain 2.56 inches the overflow was recorded by flow meters located at the respective locations. Total Released 3.015443 gallons | The cause of the overflow was a result of heavy rain storms. The Highland Sanitary District is aggressively implementing sewer improvement projects that address inflow/infiltration problems in the community. those projects include manhole and sanitary sewer line programs and programs that eliminate sump pumps and foundation drain discharges to the sanitary sewer. | Storm Sewer
19346 | 36216 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-04-18 02:52 | 2013-04-18 16:00 | 2013-04-24 14:12 | 6460750 | gallons | 12 Centrifugal Pump at N 5th Street Pump Station (1700 gpm) (5634750gal) 6 Centrifugal Pump is Duluth Street Street and Grace Place (826000) Storm Sewer | Untreated Release Rain 4.06 inches. As a consequence of heavy rainstorms the sanitary sewer system in the N 5th Street Pump Station Basin surcharged presenting a threat for basement flooding. the district set up bypass pumping in two locations in order to minimize the threat of basement flooding. Estimated total bypass for the period was 6.460750 gallons. | Surcharge levels were monitored throughout the period of bypass in order to minimize the duration of the bypass. Pumps were shutdown as soon as surcharging did not pose a threat to basement flooding. The cause of the overflow was a result of heavy rain storms. The Highland Sanitary District is aggressively Implementing sewer improvement projects that address inflow/infiltration problems in the community. Those projects include manhole and sanitary sewer line programs and programs that eliminate sump pumps and foundation drain discharges to the sanitary sewer. | Storm Sewer
19346 | 36220 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-04-18 13:55 | 2013-04-18 15:55 | 2013-04-24 14:12 | 210000 | gallons | 6 Centrifugal Pump at Duluth Street and Grace Place (210000 gal) Storm Sewer | Untreated Release Rain 4.06 inches As a consequence of heavy rainstorms the sanitary sewer system in the 41st Street Pump Station Basin surcharged presenting a threat for basement flooding. The District set up bypass pumping in order to minimize the threat of basement flooding. Estimated total bypass for the period was 210000 gallons. | Surcharge levels wee monitored throughout the period of bypass in order to minimize the duration of the bypass. Pumps were shutdown as soon as surcharging did not pose a threat to basement flooding. The cause of the overflow was a result of heavy rain storms. The Highland Sanitary District is aggressively implementing sewer improvement projects that address inflow/infiltration problems in the community. Those projects include manhole and sanitary sewer line programs and programs that eliminate sump pumps and foundation drain discharges to the sanitary sewer. | Storm Sewer
19346 | 39539 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-07-08 12:00 | 2013-07-08 14:00 | 2013-07-11 17:34 | 0 |  | Manhole #3005 @ Entrance to Homestead Park (3562 gallons) | Rain 1.74 inches The overflow was recorded by flow meters located at the respective locations. Total Released 92344 gallons. During the storm one of the three effluent pumps at the North Street Sanitary Sewer Lift Station was out of service (impeller repair)which reduce capacity from 6000gpm to 3800 gpm. We are confident that had not the pump not been out of service the SSO would not have occurred.
19346 | 40210 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-09-18 | 2013-09-18 12:00 | 2013-09-18 23:40 | 0 |  | manhole # 3 near Johnson School and 5th Street | SSO-wet weather complaint | Smith directed reporter to fax OWQ a report of the incident 9-19-13. Incident referred to OWQ via e-mail.
19346 | 40314 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-09-18 20:30 | 2013-09-18 22:00 | 2013-09-18 22:40 | 0 |  | Manhole #1345 @ 8505 5th Street (65380 gallons) | The overflow was recorded by flow meter located at the respective locations. Total released 402202 gallons | See Report | SSO Affected Private Property
19346 | 40312 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-09-18 20:30 | 2013-09-19 01:30 | 2013-09-18 22:40 | 0 |  | Manhole #1230 @ 8231 5th Street (327692 gallons) | The overflow was recorded by flow meters located at the respective locations. Total released 402020 gallons. | See Report | SSO Affected Private Property
19346 | 40310 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-09-18 21:00 | 2013-09-19 01:00 | 2013-09-23 02:26 | 0 |  | Manhole #3005 @ Entrance to Homeslead Park (8948) | The overflow was recorded by flow meters located at the respective locations. Total released 402020 gallons. | See Report | SSO Affected Private Property
19346 | 41724 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-10-30 21:00 | 2013-10-30 22:00 | 2013-10-31 14:40 | 0 |  | Manhole #3005 @ entrance to Homestead Park (3805 gallons) Manhole #1345 @ 8505 5th Street (2708 gallons) | Rain 1.99 or 2.58 inches. The overflow was recorded by flownmeters located at the respective locations. Flowmeter at manhole #1230 was dislodged from the pie during the overflow. Based upon the data on the other two flow meters we estimate that the overflow lasted approximate 1-2 hours. The meter has been replaced and stabilized. | See Report | SSO Reached Receiving Water | Little Calumet River
19346 | 41734 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-10-31 14:05 | 2013-10-31 14:05 | 2013-10-31 14:40 | 0 |  | Manhole #1230 @ 8231 5th Street (Unknown Gallons) | Rain 1.99 & 2.58 inches The overflow was recorded by flowmeters located at the respective locations. flowmeter at manhole #1230 was dislodged from the pipe during the overflow. Based upon the data on the other two flow meters we estimate that the overflow lasted approximate 1-2 hours. The meter has been placed and stabilized. | See Report | SSO Reached Receiving Water | Little Calumet River
19346 | 42081 | IN0039381 - Terminated | HIGHLAND WATER WORKS | Lake | 2013-11-17 14:15 | 2013-11-17 15:15 | 2013-11-21 15:37 | 0 |  | Manhole #3005 @ Entrance to Homestead Park (9015 gallons) | The overflow was recorded by flowmeter located at the respective location |  | SSO Reached Receiving Water | Little Calumet River
10699 | 35131 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-01-22 | 2013-01-22 16:30 | 2013-01-22 20:56 | 0 |  | 523 North Wisconsin Street Hobart IN. Force Main break | Break in force main at 523 N. Wisconsin St. caused an untreated release. | Force main excavated and break repaired. | SSO Reached Receiving Water | Lake George
10699 | 35055 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-01-29 20:30 | 2013-01-30 08:20 | 2013-01-29 21:16 | 0 |  | Lift Station #2 705 North Wisconsin Street Hobart IN 46342 | Heavy rain and snow melt. One pump at Main Lift Station out of service for repair. Untreated Release | Scheduled improvements on sanitary and storm water sewers in immediate area | SSO Reached Receiving Water | Deep River
10699 | 35062 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-01-29 21:00 | 2013-01-30 08:30 | 2013-01-30 00:32 | 0 |  | Manhole 505-018 at 3rd and Wisconsin Hobart IN | Heavy rain event triggered untreated relase from Manhole 505-018. | Lift Station running at 100% of capacity. Cit is videoing sanitary sewers looking for storm water infiltration and engineering ways to stop infiltration. | SSO Reached Receiving Water | Lake George
10699 | 35060 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-01-30 00:31 | 2013-01-30 05:30 | 2013-01-29 21:16 | 0 |  | Manhole 705-063 Hobart IN | Heavy rain and snow melt along with one pump at main lift station being out of service for repair caused and untreated relase from manhole 705-063. | Repair of faulty pump at main lift station. scheduled improvements to sanitary and storm water sewers. | SSO Reached Receiving Water | Deep River
10699 | 35215 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-01-31 07:20 | 2013-01-31 08:15 | 2013-01-31 13:10 | 0 |  | Manhole #902-022 West of Lift Station 3820 East 33rd Lane Hobart IN | Blockage in line between manhole and Lift Station resulted in an untreated release from manhole to receiving waters | cleaned out line and restored flow. Schedule regular maintenance and clean out. | SSO Reached Receiving Water | Deep River; Spring Creek
10699 | 34918 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-02-05 15:00 | 2013-02-05 16:15 | 2013-02-05 21:15 | 0 |  | Force Main at intersection of Rand Street and Kelly Street. Hobart IN 46342 | Accidental break occurred during construction of new storm sewers causing an Untreated Release into Deep River. Break occurred in the Force Main at Rand and Kelly Streets. | Temporary dike made to stop flow into river. Lift Station #21 shut down while break was repaired. | SSO Reached Public Land; SSO Reached Receiving Water | Deep River
10699 | 34670 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-03-10 05:15 | 2013-03-11 02:30 | 2013-03-10 08:11 | 0 |  | Lift Station #2 705 N Wisconsin St. Hobart IN 46342 | Untreated Release Heavy dilution of storm water and snow melt Rain .73 Heavy rain and snow melt. Combined rain amounts over 2 days plus 7 inches of snow melt. | Further testing for storm and ground water infiltration. | SSO Reached Receiving Water | Deep River
10699 | 35606 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-11 02:48 | 2013-04-11 04:24 | 2013-04-11 08:23 | 0 |  | Lift station #2 705 N Wisconsin St Hobart IN Deep River | Untreated Release Rain 1.25 inches Heavy rain within 24 hours. | Flow metering currently installed at source of suspected I&I | SSO Reached Receiving Water | Deep River
10699 | 35840 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-15 22:54 | 2013-04-16 10:49 | 2013-04-16 13:51 | 0 |  | Lift Station #2 705 N Wisconsin St Hobart IN 46342 The creek leading to Deep River. | Untreated Release Rain 1.33 inches Heavy dilution of storm water. | Attempt to locate I&I | SSO Reached Receiving Water | Deep River
10699 | 35902 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-15 22:54 | 2013-04-16 10:49 | 2013-04-16 14:07 | 0 |  | Lift Station #2 705 N Wisconsin St Hobart IN 46342 Deep River | Untreated Release Rain 1.33 inches Heavy rain within 24hrs | Attempt to locate I&I | SSO Reached Receiving Water | Deep River
10699 | 35888 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-15 23:25 | 2013-04-16 10:15 | 2013-04-16 14:07 | 0 |  | 3rd & Wisconsin MH #505-018 Lake George | Untreated Release Rain 1.33 inches | All pumps 100% at Lift Station. Flow monitoring South Mundel Storm & Sanitary Rehab project underway. | SSO Affected Private Property; SSO Reached Receiving Water | Lake George
10699 | 35839 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-16 05:20 | 2013-04-16 06:58 | 2013-04-16 13:51 | 0 |  | Man Hole #705-063 Deep River below Lake George Dam | Untreated Release Rain 1..33 inches Heavy Rain within 24 hrs. | Heavy rain within 24 hours compliance with IDEM | SSO Reached Receiving Water | Deep River
10699 | 35922 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-16 05:20 | 2013-04-16 06:58 | 2013-04-16 14:12 | 0 |  | Man Hole #705-063 Deep River | Untreated Release Rain 1.33 inches heavy rainfall | Compliance with IDEM | SSO Reached Receiving Water | Deep River
10699 | 36625 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-17 23:58 | 2013-04-19 10:30 | 2013-04-19 | 0 |  | Man Hole #705 - 063 Deep River | Untreated Release Rain 2.09 inches Heavy rainfall due to severe weather. | Compliance plan with IDEM | SSO Reached Receiving Water | Deep River
10699 | 36617 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-18 00:12 | 2013-04-19 10:52 | 2013-04-19 | 0 |  | Lift station #2 705 N Wisconsin St. Hobart IN 46342 Creek leading to Deep River | Untreated Release Rain 2.09 inches Severe rain over 2 days | Compliance Plan with IDEM | SSO Reached Receiving Water | Deep River
10699 | 36099 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-18 00:34 | 2013-04-19 09:00 | 2013-04-18 21:12 | 0 |  | Manhole #505-018 3rd and Wisconsin | Precipitation event triggered an untreated release from a manhole to receiving waters. 1.33 niches of rain on 4-15-13 heavy ground saturation. | Flow monitoring of sanitary sewers underway. Mundel storm and sanitary project underway. | SSO Reached Receiving Water | Lake George
10699 | 36065 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-18 00:39 | 2013-04-18 05:00 | 2013-04-18 00:24 | 0 |  | Manhole 605-003 on South Lake Park Avenue | Precipitation event caused untreated release from manhole to receiving waters. | Lift station pumping at 100 % capacity. Monitoring flow and Mundel storm and sanitary project underway. | SSO Reached Receiving Water | Lake George
10699 | 36064 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-18 00:44 | 2013-04-18 03:00 | 2013-04-18 00:24 | 0 |  | Manhole 704-002 Cleveland and North Linda | Precipitation event triggered and untreated release from manhole to receiving waters. | Lift station pumping at 100%. Monitoring flow. Mundel storm and sanitary project underway. | SSO Reached Receiving Water | Frog Creek
10699 | 37841 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-06-12 21:42 | 2013-06-12 23:57 | 2013-06-12 11:00 | 0 |  | Manhole #705-063 Deep River | Exceeded Max Capacity Rain 1.69 inches. Severe thunderstorms and flooding. | Secure manhole lid to limit bypass. Currently attempting to locate I&I and make repairs to infrastructure where needed according to compliance plan with IDEM. | SSO Reached Receiving Water | Deep River
10699 | 38932 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-06-26 07:56 | 2013-06-26 14:06 | 2013-06-26 08:01 | 0 |  | Lift Station #2 705 N. Wisconsin St Hobart In 46342 | Rain .99 inches Exceeded Max Capacity. Severe thunderstorms and flooding | See Report | SSO Reached Receiving Water | Deep River
10699 | 40232 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-09-18 21:10 | 2013-09-19 09:43 | 2013-09-19 10:46 | 0 |  | Lift Station #2 705 N Wisconsin St Hobart In 46342 | Severe thunderstorms and flooding. | See Report | SSO Reached Receiving Water | Deep River
10699 | 40231 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-09-18 21:30 | 2013-09-19 01:20 | 2013-09-18 10:46 | 0 |  | 505 - 018 3rd and Wisconsin | Rain 2.9 inches Bypass overflow heavy rain. | See Report | SSO Reached Receiving Water | Lake George
10699 | 40237 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-09-18 21:44 | 2013-09-19 10:34 | 2013-09-19 10:46 | 0 |  | Man hole #705-063 Hobart In 46342 | Rain 3.05 inchesSevere thunderstorms and flooding | See Report | SSO Reached Receiving Water | Deep River
10699 | 41442 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-10-31 10:30 | 2013-10-31 01:57 | 2013-10-31 08:19 | 0 |  | Lift Station #2 705 N Wisconsin St Hobart In 463542 | Rain 2.08 inches Exceeded Max Capacity Heavy amounts of rainfall in a shore amount of time combined with flooding. | See Report | SSO Reached Receiving Water | Deep River
10699 | 41719 | IN0061344 | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-11-06 09:05 | 2013-11-06 10:35 | 2013-11-07 07:30 | 0 |  | Lift Station #2 705 N Wisconsin St Hobart In 46342 | Rain 1.09 inches Exceeded Max Capacity Heavy amount of rainfall in a short amount of time. | See Report | SSO Reached Receiving Water | Deep River
10699 | 42309 | IN0061344 Organization Notified - Hobart Wastwater Board | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-12-04 12:05 | 2013-12-04 13:00 | 2013-12-05 09:30 | 0 |  | 39th avenue at Colborne St Hobart In 46342 | Equipment Failure HSD staff notified of water leaking form ground at 39th Avenue and Colborne Street by unidentified citizen. HSD personnel arrived on the scene shortly after and identified the leak a break in the B inch force main leading from Lift station #5 located at 4005 w 37th Avenue. | See Report | SSO Reached Public Land
10699 | 35885 | IN0061344 No damage | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-04-16 05:20 | 2013-04-16 06:58 | 2013-04-16 14:07 | 0 |  | Man Hole #705-063 Deep River | Untreated Release Rain 1.33 inches Heavy Rain within 24hrs. | Compliance with IDEM | SSO Affected Private Property; SSO Reached Receiving Water | Deep River
10699 | 43305 | IN0061344 Organization Notified (Hobart Wastewater Board) | HOBART WASTE WATER TREATMENT PLANT | Lake | 2013-12-24 10:35 | 2013-12-24 12:55 | 2013-12-25 08:31 | 0 |  | 245 N Pennsylvania Street Hobart In 46342 | Equipment Failure HSD staff notified of water leaking from ground at 245 N Penn St HSD personnel arrived on the scene shortly after and identified the lead as a break in the 8 inch force main leading from Lift Station #2 located at 705 N Wisconsin St. | See Report | SSO Reached Public Land
25891 | 35493 | IN023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-08 09:55 | 2013-04-08 12:38 | 2013-04-10 10:45 | 3810000 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Rain 0.35 inches. High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increased. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. All partial bypasses of the Tertiary bldg are recombined with Tertiary filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
25891 | 36645 | IN023060 | HAMMOND SEWAGE TREATMENT | Lake | 2013-04-18 | 2013-04-19 | 2013-04-19 12:41 | 57240 | gallons | Tertiary Bypass Valve Grand Calumet River | Partially Treated Release Rain 3.65 inches High secondary effluent flow and turbidity resulted in a high level alarm for the influent channel level necessitating the partial bypass of the Tertiary Filter Bldg. | Filter backwash frequency increase. For flow no action planned. HSD is required to maximize flows during wet weather events in order to minimize CSO discharge events and volumes. As a result hydraulic loading may result in future partial bypasses of the Tertiary filters to relieve hydraulic stress on the Tertiary treatment stage. all partial bypasses of the Tertiary Bldg. are recombined with Tertiary Filter effluent prior to the contact tank. The final effluent for HSD is sampled after the flows are combined. | SSO Reached Receiving Water | Grand Calumet River
18238 | 36061 | INJ031089 | INDEPENDENCE HILL CONSERVANCY DISTRICT | Lake | 2013-04-18 00:30 | 2013-04-18 06:30 | 2013-04-18 13:09 | 1200 | gallons | 3416 West 78th Avenue | Precipitation event and malfunctioning check valve resulted in an untreated release into a residential basement. | IHCD has lined sewers to prevent any infiltration coming in to the sewers. IHCD has a program for the homeowner to replace the old deteriorated building sewer laterals with a new PVC line which is partially funded by IHCD. IHCD also has a sump pump disconnection incentive program for the homeowners. IHCD is considering either to repair the check valve or install a new check valve in order to avoid future sewage backup into this property. | SSO Basement Backup
20515 | 35632 | INJ063592 | LAKE STATION WATER & SEWER | Lake | 2013-01-11 14:10 | 2013-01-11 14:45 | 2013-01-14 16:48 | 0 |  | 408 Liverpool Road | Residential grease obstruction in main sewer line resulted in an untreated release into residential basement. | Cleaned main sewer line from upstream manhole to downstream manhole. Noted grease being discharged from residence. Met with homeowner about discharging grease into sewer. Poor main installation is scheduled for replacement in the Spring. | SSO Basement Backup
20515 | 35633 | INJ063592 | LAKE STATION WATER & SEWER | Lake | 2013-01-12 11:57 | 2013-01-12 12:40 | 2013-01-14 16:48 | 0 |  | 2740 Wells | Apparent root blockage in main line resulted in untreated release into residential basement | Jetted main line from downstream manhole to upstream manhole. Opened small blockage. Will need to camera line to see what is causing the blockage. It looks as if it could be roots. At that time we will cut the roots out. | SSO Basement Backup
20515 | 36317 | INJ063592 | LAKE STATION WATER & SEWER | Lake | 2013-04-16 23:50 | 2013-04-17 13:00 | 2013-04-22 15:27 | 106500 | gallons | 2548 Dearborn Street manhole | Precipitation event and infiltration from storm sewer resulted in untreated release from manhole to ditch and receiving water. | Operated the Central & Allen lift station at the slowest rate possible without creating backups and any other overflows in other areas prior to the Central station. Central and Allen station pumps to the area which was affected. Lift station at 23rd and DeKalb could not handle receiving flow from Central and Allen station. Crews were sent out to clean storm water grates to assist in shedding water away from sanitary manholes. Clean up area and apply lime. Continue to investigate and eliminate storm water infiltration into the sanitary system. | SSO Reached Receiving Water | Burns Ditch
20515 | 36315 | INJ063592 | LAKE STATION WATER & SEWER | Lake | 2013-04-17 23:50 | 2013-04-19 01:20 | 2013-04-22 15:26 | 13500 | gallons | Viking Village Lift Station Wet Well | Precipitation event and I & I of storm water to the Sanitary Sewer System resulted in untreated release from lift station and wet well to receiving waters. | Employees cleaned ditch line of debris prior to storm but the excessive amount of storm water again clogged the storm sewer with debris causing inflow to the SSS. Have been unable to find the point of inflow. Used a bypass pump to pump out ditch to reduce flow into sanitary sewer. Investigating running a new storm water pipe or digging out an open ditch to allow storm runoff to get to the river. | SSO Reached Receiving Water; Storm Sewer | Deep River
20515 | 38238 | INJ063592 | LAKE STATION WATER & SEWER | Lake | 2013-06-28 10:50 | 2013-06-28 12:50 | 2013-07-02 10:44 | 0 |  | 2548 Dearborn St Manhole Ditch line that leads to Burns Ditch | Rain 2.5 inches. Received a total of 2.5 inches of rain for which a large amount fell within a short time period over charging sanitary system. Flow rate was approximately 10 gpm from 10:50 pm till 11.50am on 6/28/13 for a total of 600 gallons from 11:50am to 12:50pm a flow rate of 5 gpm was monitored for 300 gallons. Over SSO stopped at 12:50am for grand total SSO of 900 gallons. | Operated the Central & Allen lift station at the slowest rate possible without creating backups and any other overflows in other areas prior to the Central Station. Central and Allen station pumps to the area which was affected. Lift Station at 23rd & DeKalb which receives its flow from Central could not handle receiving flow. In addition crews where sent out to clean storm water grates to assist in shedding water away from sanitary manholes. Clean up area and apply lime. Continue investigating and eliminating storm water infiltration into sanitary system. | SSO Affected Private Property; SSO Reached Receiving Water | Burns Ditch
20515 | 38236 | INJ063592 | LAKE STATION WATER & SEWER | Lake | 2013-07-01 12:50 | 2013-07-01 13:45 | 2013-07-02 10:44 | 0 |  | 425 Liverpool Rd Basement | Residence had called in with a sewer backup in there basement upon inspection it was noticed that manhole D^-27 was backed up checked next down stream manhole D^-026 and found it to be backed up as well went down stream to manhole D6-025 and found it backed up continued down stream to manhole D6-024 and found it not backed up. Jetted from that manhole south hit a blockage at 220ft. Pulled back large amount of grit and rags Jetted line twice to clear away all grit and rags. | Video tape line to see if there are roots in line or damage. | SSO Basement Backup
20515 | 42634 | INJ063592 | LAKE STATION WATER & SEWER | Lake | 2013-12-20 16:00 | 2013-12-20 17:00 | 2013-12-23 | 0 |  | 2520 Putnam Street Basement | Unknown Basement Backup manhole upstream of literal was backed up. | See Report | SSO Basement Backup; SSO Affected Private Property
20515 | 41420 | INJ063592 Gary Sanitary Line Marsh Land Area | LAKE STATION WATER & SEWER | Lake | 2013-10-29 10:00 |  | 2013-10-29 10:00 | 0 |  | 15th ave Forcemain to Gary Gravity Forcemain Collapsed 13 feet from discharge | The forcemain is collapsed at about 13 feet from the Gary sanitary Sewer intercepter Sewer is flowing above ground and entering Sanitary sewer manholedo and easy task to repair. Contacted all sanitary district members and a local contractor to help with this matter. Dave Greinke with IDEM has come out and inspected the area and will be on site from time to time. Estimated amount of release is 1000000 Gallons. | To help Mitigate I have installed a berm of sand around the area to confine the flow to a constricted area. Currently working with Engineers and Contractor to come up with a plan of action to stop the overflow. | SSO Affected Private Property
13872 | 37840 | Reached Receiving Water- No Name Given | Gary Sanitary District Waste Water Treatment Plant | Lake | 2013-06-12 20:30 | 2013-06-13 10:45 | 2013-06-13 12:54 | 2866536 | gallons | Effluent Bypass Gate Closed 100% | Exceeded Max Capacity Rain .57 inches. Excessive rain conditions. Plant flow exceed maximum Capacity of Treatment Process. | Continue to follow the wet weather plan. | SSO Reached Receiving Water
20486 | 36559 | Swamp north of facility | CLINE AVENUE PUMPING STATION | Lake | 2013-04-18 12:50 |  | 2013-04-18 13:15 | 0 |  | Equalization Basin at Cline Avenue Pump Station South of Little Calumet River Swamp nor of Facility | Untreated Release Rain 6.43 inches The bypass incident was necessary because of drenching rains that hit the area on already saturated round. Phone contact was made with Ms Deborah Brents at 1:15pm on 4/18/2013. Ms Brents requested that the town submit the incident reports in the future instead of contacting by phone. Date and time release stopped rainfall totals and an estimate of flow released will be available after the flows recede and bypass pumping ends. An amended Incident Report will be submitted at that time. Rainfall readings at the Cline Pump Station in April 2013 totals 6.43 inches as of April 18th. This total includes .36 inches on 4/8 1.05 on 4/10 24 on 4/11 1.27 on 4/15 2.45 on 4/17 and .87 on 4/18 | Pumping to swamp to ensure the health safety and welfare of the Town of Griffin Citizens. The Town will continue to pursue the reduction of infiltration and inflow into the sanitary sewer collection system as well as additional storage facilities or increased pumping capacity to the Hammond Sanitary District. | SSO Affected Private Property | Little Calumet River
20486 | 36572 | Unpermitted | CLINE AVENUE PUMPING STATION | Lake | 2013-04-18 12:50 | 2013-04-19 20:00 | 2013-04-18 13:15 | 6300000 | gallons | Equalization Basin at Cline Avenue Pump Station South of Little Calumet River Swamp North of Facility | Untreated Release Rain 6.43 inches. This report is a follow-up to the initial report sent in on April 192013. The bypass incident was necessary because of drenching rains that hit the area on already saturated ground. Phone contact was made with Ms Deborah Brents at 1:15pm on 4/18/13. Rainfall readings at the Cline Avenue Pump Station in April 2013 totals 6.43 inches as of April 18. This total includes .36 on 4/8 1.05 on 4/10 24 on 4/11 1.27 on 4.15 2.45 on 4.17 and .87 on 4/18. 6.37 inches of rain fell during the 10-day period of April 8 to 18 and a total of 4.65 inches from April 15 to April 18 | Pumping to swamp to ensure the health safety and welfare of the Town of Griffith citizens. The Town will continue to pursue the reduction of infiltration and inflow into the sanitary sewer collection system as well as additional storage facilities or increased pumping capacity to the Hammond Sanitary District. | SSO Reached Receiving Water | Little Calumet River
32708 | 40505 | IN0001911 | BEDFORD WATER WORKS ILLINOIS STREET PLANT | Lawrence | 2013-09-29 08:00 | 2013-09-29 14:00 | 2013-09-30 14:30 | 0 |  | 2407 Illinois St | Equipment Failure A drain valve failed on a flock tank which allowed a discharge of solids from the Water Plant. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | East Fork White River
32642 | 42609 | IN002523 Outfall 004 LAT-LONG wasn t entered the numbers gave and error. | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-12-14 09:34 | 2013-12-14 23:48 | 2013-12-20 15:30 | 0 |  | 22nd & Fst LS | Rain 0.38 inches There was a lot of melting of snow on ground. | See Report | SSO Reached Receiving Water | Leatherwood Creek
32642 | 34962 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-02-05 | 2013-02-05 15:30 | 2013-02-06 15:23 | 100000 | gallons | manhole on gravity sewer on Ludlow St. near Spider Creek | Manhole line became obstructed resulting in overflow | Crew will clean up debris on ground around manhole and creek bank. Will add this location to our routine maintenance list of sewer lines to clean. | SSO Reached Receiving Water | Spider Creek
32642 | 34861 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-02-19 09:00 | 2013-02-19 15:30 | 2013-02-20 14:00 | 50000 | gallons | North N St. Lift Station Breckenridge Road | Multiple pump failures caused an Untreated Release from Lift Station | Lift station pump #1 was out for repair and pump #2 failed before pump #1 was returned. Repair shop rushed repair of #2 and delivered the same afternoon.We will clean up any debris found. | SSO Reached Receiving Water | Salt Creek
32642 | 35443 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-03-20 15:00 | 2013-03-20 16:00 | 2013-03-22 08:58 | 0 |  | 1917 Circle Drive | Sewer Main dog caused Unteated release into residential basement | Line cleaned and overflow drained back into sanitary sewer. Cleaned basement floor for home owner. Place this line on our routine clean list. | SSO Basement Backup
32642 | 35393 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-11 | 2013-04-12 | 2012-04-12 15:37 | 55000 | gallons | Lift Station #004 located at 22nd and F strees in Bedford IN | Precipitation event triggered an Untreated Release from Lift Station #004 at 22nd and F streets. | Will clean up any remaining debris. Investigate to determine the source of I & I. | SSO Reached Receiving Water; Surface Soil | Leatherwood Branch
32642 | 35392 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-11 | 2013-04-12 | 2013-04-12 15:37 | 4510 | gallons | Bedford Heights lift station #008. Bedford IN | Precipitation event triggered an Untreated Release from the Bedford Heights Lift Station 008. | We will clean up any residual debris and investigate to determine the source of I &I. | SSO Reached Public Land; SSO Reached Receiving Water | Bailey Branch
32642 | 36021 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-16 03:30 | 2013-04-17 08:00 | 2013-04-17 15:30 | 21000 | gallons | 22 and F Street Lift Station | Precipitation event exceeded capacity of lift station resulting in untreated release to receiving waters. | Will clean up any residual. Attempt to find source of I & I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 36432 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-18 03:00 | 2013-04-19 12:00 | 2013-04-20 15:04 | 748 | gallons | Windwood Lift Station Edgewood | Precipitation event and I & I exceeded the capacity of a lift station resulting in untreated release to unnamed ditch and receiving waters | Clean up any residual left from the overflow. Try to locate source of I & I. | SSO Reached Receiving Water | Spider Creek
32642 | 36435 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-18 03:00 | 2013-04-19 11:00 | 2013-04-20 16:58 | 57000 | gallons | Bedford Heights Lift Station 008 | Precipitation event and I & I contribution resulted in an untreated release from lift station to receiving waters. | We will clean up any resiual left behind. Try to locate source of I & I. | SSO Reached Receiving Water | Bailey Branch; Pleasant Run Creek
32642 | 36430 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-18 03:00 | 2013-04-19 15:00 | 2013-04-20 16:58 | 69000 | gallons | 22nd and M Street Lift Station 004 | Precipitation event and I & I contribution exceeded the capacity of lift station resulting in an untreated realease to receiving waters. | Clean up any residual left from overflow. Try to locate source of I & I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 36427 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-18 03:00 | 2013-04-19 09:00 | 2013-04-20 16:58 | 6000 | gallons | 22nd and M Street Lift Station 003 | Precipitation event and I & I contribution exceeded the capacity of a lift station resulting an untreated release from Lift station to receiving waters | Clean up any residual left from discharge. Try to locate source of I & I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 36682 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-04-24 10:10 | 2013-04-24 11:26 | 2013-04-26 17:26 | 1000 | gallons | 22 and F Streets Lift Station | Precipitation event triggered an untreated release from lift station to receiving water. | We will clean up any residual. Try to find source of I & I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 36774 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-05 07:30 | 2013-05-06 18:00 | 2013-05-06 15:38 | 152000 | gallons | Spider Creek Lift Station #007 | Flow from precipitation event exceeded the capacity of a lift station resulting in an untreated release to receiving water. | We will clean up any residual. Find source of I & I. | SSO Reached Receiving Water | Spider Creek
32642 | 36776 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-05 08:22 | 2013-05-05 22:30 | 2013-05-06 15:39 | 46000 | gallons | 22nd and F Streets - Lift Station #004 | Flow from precipitation event exceeded capacity of lift station resulting in an untreated release to receiving water. | We will clean up any residual. Find source of I & I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 36775 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-05 08:30 | 2013-05-06 15:15 | 2013-05-06 15:38 | 65000 | gallons | Windwood Lift Station - Edgewood Addition | Flow from precipitation event exceeded capacity of lift station resulting in an untreated release to receiving water. | We will clean up any resiual. Find source of I & I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 36773 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-05 08:30 | 2013-05-06 20:45 | 2013-05-06 15:38 | 0 |  | Bedford Heights Lift Station #008 | Flow from precipitation event exceeded the capacity of lift station resulting in an untreated release to receiving water. | We will clean up any residual. Find source of I & I. | SSO Reached Receiving Water | Bailey Branch
32642 | 37009 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-16 11:30 | 2013-05-16 11:07 | 2013-05-17 03:26 | 70000 | gallons | 22nd & M St. LS #003 Leatherwood Creek | Untreated Release Rain 0.52 inches We will clean up any residual. | Find source of I&I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 37008 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-16 11:30 | 2013-05-16 11:07 | 2013-05-17 15:26 | 11000 | gallons | 22nd and F St LS #004 Leatherwood Creek | Untreated Release Rain 0.52 We will clean up any residual. | Find source of I&I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 37010 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-16 11:30 | 2013-05-16 11:07 | 2013-05-17 15:26 | 141000 | gallons | Spider Creed LS #007 Spider Creek | Untreated Release Rain 0.52 inches We will clean up any residual. | Find source of I & I | SSO Reached Receiving Water | Spider Creek
32642 | 37011 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-05-16 11:40 | 2013-05-16 06:25 | 2013-05-17 15:25 | 130000 | gallons | Windwood LS Edgewood Spider Creek | Untreated Release Rain 0.52 inches We will clean up any residual. | Find source of I & I | SSO Reached Receiving Water | Spider Creek
32642 | 37288 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-01 08:45 | 2013-06-01 14:00 | 2013-06-01 18:00 | 135000 | gallons | Spider Creek L/S | Rain 2.3 inches L/S Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 37275 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-01 08:52 | 2013-06-01 15:30 | 2013-06-01 18:00 | 42000 | gallons | 22nd & Fst Lift Station | Rain 2.13 inches | Will clean up amy residue Find source of I&I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 37278 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-01 09:39 | 2013-06-01 12:22 | 2013-06-01 18:00 | 6000 | gallons | Bedford Heights LS | Rain 2.13 inches | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Bailey Branch; Pleasant Creek
32642 | 37520 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-03 04:00 | 2013-06-03 15:30 | 2013-06-03 15:00 | 109000 | gallons | Spider Creek L/S Spider Creek | Rain 2.13 inches LS Overflow | Will clean up any residue Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 37518 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-03 04:19 | 2013-06-03 15:08 | 2013-06-03 15:00 | 9000 | gallons | 22nd & Fst LS Leatherwood Creek | Rain 2.13 inches LS Overflow | Will clean up any residue Find source of I&I | SSO Affected Private Property; SSO Reached Receiving Water | Leatherman Creek
32642 | 37539 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-06 06:04 | 2013-06-06 10:26 | 2013-06-07 03:30 | 9744 | gallons | Broadview LS | Rain 2.29 inches LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 37558 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-06 08:30 | 2013-06-06 18:00 | 2013-06-11 09:00 | 135000 | gallons | Spider Creek LS | Rain 2.29 inches LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 37557 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-06 15:00 | 2013-06-06 16:30 | 2013-06-11 09:00 | 10000 | gallons | Manhole @ 22nd & G St Leatherwood Creek | Rain 2.13 inches Sewer line clog caused an overflow from manhole. | Will clean up any residue. Find source of I&I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 37556 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-06 16:00 | 2013-06-06 18:30 | 2013-06-11 09:00 | 0 |  | Basement @ 2214 27th St | Rain 2.29 inches House Lateral. High flow caused a back up in the home owners basement. | Cleaned basement after it drained back to sanitary sewer. | SSO Basement Backup
32642 | 37541 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-06 23:28 | 2013-06-07 06:28 | 2013-06-07 15:30 | 131000 | gallons | 22nd & Fst LS LS Overflow | Rain 2.29 inches LS Overflow | Will clean up any residue. Find source of I&I. | SSO Reached Receiving Water | Leatherwood Creek
32642 | 38220 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-26 02:00 | 2013-06-26 12:00 | 2013-07-02 15:30 | 0 |  | Spider Creek LS LS Overflow | Rain 2.08 inches | Will clean up any residue. Find source of I%I | SSO Reached Receiving Water | Spider Creek
32642 | 38329 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-26 02:06 | 2013-06-26 18:57 | 2013-07-03 | 479344 | gallons | Windwood LS | Rain 2.08 inches. LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 38325 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-26 03:11 | 2013-06-26 16:00 | 2013-07-03 09:00 | 79477 | gallons | 22nd & Fst LS | Rain 2.08 inches. LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 38321 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-26 03:52 | 2013-06-26 09:20 | 2013-07-03 10:00 | 20866 | gallons | Bedford Heights LS | Rain 2.8 inches LS Overflow | Will clean up any residue. find source of I&I | SSO Reached Receiving Water
32642 | 38347 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-26 04:00 | 2013-06-26 05:37 | 2013-07-03 09:00 | 4759 | gallons | North N St LS | LS Overflow | Will clean up any residue. Find source of I & I | SSO Reached Receiving Water | Salt Creek
32642 | 38320 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-26 06:30 | 2013-06-26 10:00 | 2013-07-03 09:00 | 30005 | gallons | Brioadview LS | Rain 2.08 inches LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 38344 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-27 17:00 | 2013-06-27 23:30 | 2013-07-03 10:15 | 358735 | gallons | Windwood LS | Rain 1.16 inches LS Overflow | Will clean up any residue. Find source of I & I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 38319 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-27 18:00 | 2013-06-27 23:30 | 2013-07-03 08:30 | 75142 | gallons | Spider Creek LS | Rain 1.16 inches LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 38349 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-29 16:00 | 2013-06-29 21:00 | 2013-07-03 10:15 | 288149 | gallons | Windwood LS LS Overflow | Rain 0.99 inches LS Overflow | Will clean up any residue. Find source of I & I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 38324 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-29 16:30 | 2013-06-29 18:30 | 2013-07-03 08:30 | 16231 | gallons | Spider Creek LS | Rain 0.99 inches LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 38342 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-29 16:30 | 2013-06-29 22:06 | 2013-07-03 09:45 | 57801 | gallons | 22nd & Fst LS LS Overflow | Rain 0.99 inches LS Overflow | Will clean up any residue. Find source of I & I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 38348 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-30 15:00 | 2013-07-01 | 2013-07-03 09:45 | 25987 | gallons | 22nd & Fst LS LS Overflow | Rain 0.23 inches LS Overflow | Will clean up any residue. Find source of I & I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 38334 | IN0025623 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-30 16:30 | 2013-06-30 11:30 | 2013-07-03 08:50 | 64336 | gallons | Spider Creek LS | Rain 0.23 inches. LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 38706 | IN0025623 Affected Waterbody was Bailey Branch Pleasant Run Creek | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-07-08 10:59 | 2013-07-18 11:25 | 2013-07-18 15:15 | 218 | gallons | Bedford Heights LS | Equipment Failure Control problem at station alarm notified crew they responded and reset equipment. | Will clean up any residue | SSO Reached Receiving Water
32642 | 37538 | IN0025623 Affected Waterbody is: Bailey Branch Pleasant Run Creek | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-06 08:21 | 2013-06-06 19:42 | 2013-06-07 03:30 | 28248 | gallons | Bedford heights LS. | Rain 2.29 inches LS Overflow | Will Clean up any residue. Find source of I&I. | SSO Reached Receiving Water
32642 | 40809 | IN0025623 Outfall 003 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-06 10:41 | 2013-10-08 18:30 | 2013-10-08 13:30 | 0 |  | 22nd & M ST L S | Rain 2.95 inches | Will clean up any residue find source f I&I | SSO Reached Receiving Water | Leatherman Creek
32642 | 40930 | IN0025623 Outfall 003 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-07 09:00 | 2013-10-07 17:30 | 2013-10-11 23:30 | 0 |  | 22nd & M St LS | Lift Station had a pump control problem repaired as soon as possible and put back in service. | Will clean up any residue | SSO Reached Receiving Water | Leatherwood Creek
32642 | 41703 | IN0025623 Outfall 003 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-30 07:00 | 2013-11-01 14:00 | 2013-11-06 08:50 | 0 |  | 22nd & M St LS | Rain 1.28 inches The level control system failed. | Will clean up any residue. We are installing a float on the overflow pipe to alert us as soon as a problem occurs. |  | Leatherwood Creek
32642 | 42305 | IN0025623 Outfall 003 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-11-17 18:07 | 2013-11-17 20:06 | 2013-12-14 14:00 | 0 |  | Bedford Heights LS | Rain 1.04 inches sorry for delay in reporting discovered this wasn t reported while reviewing monthly data. | See Report | SSO Reached Receiving Water | Bailey Creek; Pleasant Run Creek
32642 | 41685 | IN0025623 Outfall 004 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-31 12:31 | 2013-11-01 04:00 | 2013-11-06 09:00 | 0 |  | 22nd & Fst LS | LS Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Leatherwood Creek
32642 | 40812 | IN0025623 Outfall 007 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-06 01:30 | 2013-10-07 02:30 | 2013-10-08 13:30 | 0 |  | Spider Creek L S | Rain | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 41706 | IN0025623 Outfall 007 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-31 10:00 | 2013-10-31 14:00 | 2013-11-06 09:05 | 0 |  | Spider Creek LS | Rain 1.28 inches | Will clean up any residue Find source of I&I | SSO Reached Receiving Water | Spider Creek
32642 | 40831 | IN0025623 Outfall 008 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-06 07:00 | 2013-10-06 11:46 | 2013-10-08 13:45 | 0 |  | Bedford heights L/S | Rain 2.95 inches | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Bailey Branch
32642 | 41705 | IN0025623 Outfall 008 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-31 10:13 | 2013-11-01 02:00 | 2013-11-06 08:45 | 0 |  | Bedford Heights LS | Rain 1.28 inches | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Bailey Branch
32642 | 40813 | IN0025623 Outfall 009 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-06 04:00 | 2013-10-06 09:00 | 2013-10-08 13:45 | 0 |  | North N St L S | L/S Overflow | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Salt Creek
32642 | 40833 | IN0025623 Outfall 009 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-06 04:00 | 2013-10-06 09:00 | 2013-10-08 13:45 | 0 |  | North N St L S | Rain 2.95 inches | Will clean up any residue. Find source of I&I | SSO Reached Receiving Water | Salt Creek
32642 | 40807 | IN0025623 Outfall 004 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-10-06 02:34 | 2013-10-06 17:37 | 2013-10-08 13:00 | 0 |  | 22nd & Fst L S | LS Overflow | Will clean up any residue Find source of I&I | SSO Reached Receiving Water | Leatherman Creek
32642 | 42608 | IN0025623 Outfall 007 | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-12-14 10:22 | 2013-12-14 14:00 | 2013-12-20 13:30 | 0 |  | Spider Creek LS | There was a lot of melting of snow on ground. | See Report | SSO Reached Receiving Water | Spider Creek
32642 | 37543 | IN0025623 Waterbody affected is a unnamed branch to Salt Creek | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-07 08:53 | 2013-06-07 10:26 | 2013-06-07 | 2787 | gallons | North Nst LS | This is an new overflow point we found I will forward the Lat & Lon as soon as I get it LS Overflow. | Will clean up any residue. Find source of I&I | SSO Affected Private Property | Salt Creek
32797 | 40463 | IN0038920 | BRIARWOOD SUBDIVISION | Lawrence | 2013-09-25 23:00 | 2013-09-26 11:30 | 2013-09-27 11:05 | 0 |  | Manhole Before WWTP | Equipment Failure Blockage occurred in gravity line running into the WWTP Headworks. | Removed Blockage See Report | SSO Affected Private Property
32642 | 37519 | Waterbody Affected is: BAILEY BRANCH PLEASANT RUN CREEK | BEDFORD WASTE WATER TREATMENT PLANT | Lawrence | 2013-06-03 03:41 | 2013-06-03 16:38 | 2013-06-03 15:00 | 10000 | gallons | Bedford Heights LS Bailey Branch Pleasant Run Creek | Rain 2.13 inches LS Overflow | Will clean up any residue Find source of I&I | SSO Reached Receiving Water
42709 | 39412 | 32476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-07-15 09:26 | 2013-07-15 09:26 | 2013-07-15 11:10 | 0 |  | Rangeline Rd. Lift Station SSO | Power Failure Exceeded Max Capacity. Power failure at Rangeline Rd. lift station for unknown reasons at this time. WPC personnel are on site to pump out the lift station and determine why the station had a power failure. Light and power have been dispatched to the location. | See Report | SSO Reached Public Land; SSO Reached Receiving Water
42709 | 39752 | 32476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-08-08 14:30 | 2013-08-08 17:31 | 2013-08-09 09:27 | 0 |  | Primary Clarifiers | Rain Event Rain .79 inches | Flow was being maximized in conjunction with our operational plan | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
40869 | 34742 |  | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-02-26 15:00 |  | 2013-02-27 11:00 | 0 | gallons | SSO 003 and SSO 004 overflow point north of 308 N. John Street | Rain event on 2/26/2013 dropped 1.4 inches of rain causing untreated release from SSO 003 and 004. | Waiting for rain to stop. No further measures taken. | SSO Reached Receiving Water | Pipe Creek
42709 | 34722 |  | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-16 13:45 |  | 2013-03-16 10:50 | 0 |  | Meters 03-49 | Equipment Failure Primary effluent meter (49) and final effluent (03) went down overnight PLC issues. | Electricians are coming in to investigate IT is also coming in. They were confident they could get these meters back on line. Final Effluent meter at Outfall is functioning ok. This will not effect our final effluent.
42058 | 38875 |  | Edgewood Town Hall | Madison | 2013-06-25 13:00 | 2013-06-25 18:10 | 2013-06-26 03:15 | 0 |  | There was a blockage in the main sewer line downstream from the manhole. This resulted in sewage backing up until it overflowed from the manhole. | ManholeThere was a blockage in the main sewer line downstream from the manhole. This resulted in sewage backing up until it overflowed from the manhole. | Removed Blockage | SSO Affected Private Property
40869 | 35238 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-01-11 06:00 |  | 2013-10-11 13:24 | 0 |  | SSO 003 and overflow point north of 308 North John Street Frankton IN | Precipitation event resulted in Untreated Release from SSO 003 and overflow point into receiving waters |  | SSO Reached Public Land; SSO Reached Receiving Water | Pipe Creek
40869 | 35090 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-01-30 04:00 |  | 2013-01-30 13:51 | 0 |  | SSO 003 and overflow point north of 308 North John Street Frankton IN | Untreated Release from SSO 003 triggered by precipitation event |  | SSO Reached Receiving Water | Pipe Creek
40869 | 35426 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-04-11 09:00 |  | 2013-04-12 07:58 | 0 |  | SSO 003 and SSO 004 overflow point north of 308 N. John St. | Precipitation event triggered Untreated Release from SSO 003 and SSO 004 Overflow point North of 308 North John Street to Pipe Creek | No action. | SSO Reached Receiving Water | Pipe Creek
40869 | 36032 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-04-17 03:00 |  | 2013-04-17 13:58 | 0 |  | SSO 003 and SSO 004 point north of 308 North John Street | Precipitation event resulted in creek flooding and Sanitary Sewer Overflows of untreated release to receiving waters. |  | SSO Reached Receiving Water | Pipe Creek
40869 | 37869 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-06-13 09:00 |  | 2013-06-13 10:55 | 0 |  | SSO 003 and SSO 004 (manhole north of 308 N John St.) Pipe Creek | Rain 1.7 inches. 1.6 inches of rain in a 12 hour period and creek flooding. |  |  | Pipe Creek
40869 | 39524 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-06-30 10:00 |  | 2013-07-01 09:00 | 0 |  | SSO #003 and SSO #004 | Rain 2.5 inches of rain in less than 24 hours and creek flooding. |  | SSO Reached Receiving Water | Pipe Creek
40869 | 40229 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-09-19 08:30 |  | 2013-09-19 10:30 | 0 |  | SSO 003 | Rain 2.4 inches 2.4 inches of rain in less than 6 hours. |  | SSO Reached Receiving Water | Pipe Creek
40869 | 40980 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-10-06 09:00 | 2013-10-07 01:00 | 2013-10-07 07:45 | 0 |  | SSO 003 Pipe Creek | 2.5 inches of rain in approximately 24 hours. | See Report | SSO Reached Receiving Water | Pipe Creek
40869 | 43411 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-12-20 09:00 | 2013-12-25 19:00 | 2013-12-27 07:06 | 0 |  | SSO #001 and SSO #002 | Rain 2.9 inches 2.9 inches of rainfall and over 6 inches of snow melting. | See Report | SSO Reached Receiving Water | Pipe Creek
40869 | 43318 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-12-20 09:00 |  | 2013-12-20 15:00 | 0 |  | SSO 001 | Rain 3 inches .3 inches of rainfall and over 6 inches of snow melting. | See Report | SSO Reached Receiving Water | Pipe Creek
40869 | 41575 | IN0020028 | FRANKTON MUNICIPAL WASTE WATER TREATMENT PLANT | Madison | 2013-10-31 21:00 |  | 2013-11-01 11:35 | 0 |  | SSO 003 and SSO 004 | Rain 3.0 3.0 inches of rain in less than 18 hours and creek flooding. | See Report | SSO Reached Receiving Water | Pipe Creek
40082 | 34362 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-01-13 03:00 |  | 2013-01-13 09:15 | 50000 | gallons | Manhole north of Village Pantry Surcharge | Untreated Release Precipitation 2.68 inches | Maximize flow to WWTP. Adding on overflow line. | SSO Reached Public Land
40082 | 35952 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-01-13 03:00 |  | 2013-01-13 03:00 | 50000 | gallons | Manhole north of Village Pantry | Precipitation event triggered an untreated release from a manhole to storm sewer. | Maximize flow to WWTP. Adding an overflow line. | SSO Reached Public Land; Storm Sewer
40082 | 35948 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-01-13 03:00 |  | 2013-01-13 09:24 | 200000 | gallons | Manhole on 11th Street Bridge | Precipitation event caused untreated release from manhole to receiving waters. | Maximize flow to treatment plant. | SSO Reached Receiving Water | Bills Creek
40082 | 35951 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-01-13 03:00 |  | 2013-01-13 09:23 | 50000 | gallons | Manhole on Chestnut Street | Precipitation event triggered an untreated release from a manhole to surrounding ground. | Maximize flow to WWTP. Adding an overflow line. | SSO Reached Public Land
40082 | 36275 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-18 21:30 |  | 2013-04-19 06:26 | 0 |  | Manhole on Chestnut Street | Precipitation event triggered untreated release from manhole to surrounding ground. | adding an overflow line in manhole to the south to help relieve this manhole. | SSO Reached Public Land
40082 | 36278 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-18 21:30 |  | 2013-04-19 06:26 | 0 |  | Manhole north of VP. | Precipitation event caused surcharge and untreated release from manhole to storm sewer. | Adding overflow line in manhole. | SSO Reached Public Land; Storm Sewer
40082 | 36276 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-18 23:00 |  | 2013-04-19 06:26 | 0 |  | Manhole at 11th Street bridge | Precipitation event caused surcharge and untreated release from manhole to receiving waters. | LTCP | SSO Reached Receiving Water | Bills Creek
40082 | 36611 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-22 | 2013-04-22 12:00 | 2013-04-22 08:30 | 0 |  | WWTP | Equipment Failure No 1 Clarifier scrapper arm not turning. Draining clarifier to find the problem. Will notify when back on line. No 1 & No 3 clarifiers working properly
40082 | 36119 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-24 05:00 |  | 2013-04-24 09:39 | 0 |  | Manhole North at VP surcharging Storm Sewer | Untreated Release Rain 1.30 inches | Adding an overflow line in manhole. | Storm Sewer
40082 | 36121 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-24 05:00 |  | 2013-04-24 09:41 | 10000 | gallons | Manhole North on Chestnut Ground | Untreated Release Rain 1.30 inches | Adding overflow line to manhole at VP | SSO Affected Private Property
40082 | 36120 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-24 05:00 |  | 2013-04-24 09:41 | 0 |  | Manhole North of VP surcharging Storm Sewer | Untreated Release Rain 1.30 inches | Adding and overflow line in manhole | Storm Sewer
40082 | 36117 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-24 05:00 |  | 2013-04-24 09:39 | 10000 | gallons | Manhole North on Chestnut Ground | Untreated Release Rain 1.30 inches | Adding overflow line to manhole at VP | SSO Affected Private Property
40082 | 37773 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-05-27 18:00 | 2013-05-29 | 2013-06-11 12:34 | 100 | gallons | Crawl space. | Power went out due to a storm at the Willows Lift Station. Causing a back up into 305 Old mill Cr. Dr under owners house. | Adding a slada system to lift station. | SSO Basement Backup
40082 | 37483 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-05-28 |  | 2013-06-10 12:51 | 0 |  | 305 Old Mill Creek Drive | Jeremy Friel of Alexandria IN states there was a sanitary sewer overflow on 5/28/13 that resulted in raw sewage getting into his crawl space. Friel was told overflow was a result of equipment failure.
40082 | 38696 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-06-13 02:00 | 2013-06-13 12:00 | 2013-06-13 13:30 | 0 |  | Manhole | Rain .04 inches Manhole Manhole surcharging to the North of VP on Washington St. | Clean sewers down stream from manhole. | SSO Affected Private Property
40082 | 38705 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-06-13 02:00 | 2013-06-13 12:00 | 2013-06-13 13:30 | 0 |  | Manhole | Rain .04 inches Manhole Manhole surcharging to the North of VP on Washington St. | Clean sewers down stream from manhole.
40082 | 38697 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-06-15 05:00 | 2013-06-13 02:30 | 2013-06-13 13:30 | 100 | gallons | Manhole | Rain 2.04 inches Equipment Failure Manhole surcharging at Old miller Cr Dr. due to lift station failure. Repaired and surcharge stopped. | Plan to reroute line to bigger station. | SSO Affected Private Property
40082 | 39408 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-06-30 07:30 | 2013-06-30 10:30 | 2013-07-01 07:00 | 0 |  | Manhole | Rain 2.57 inches Manhole North of Village Pantry surcharging | See Report
40082 | 39407 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-06-30 08:48 | 2013-06-30 10:30 | 2013-07-01 07:00 | 0 |  | Manhole | Rain 2.57 inches Manhole on Chestnut | See Report | SSO Affected Private Property
40082 | 39401 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-06-30 09:30 | 2013-06-30 10:30 | 2013-07-01 07:12 | 0 |  | Manhole at 11th Street and Highway #9 | Rain 2.57 inches Manhole at intersection of the street and Indiana 9 on NW of intersection surcharged for approx 1 hr. | Going to jet sewer to clear out piping. | SSO Reached Receiving Water | Bills Creek
40082 | 39402 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-06-30 16:00 | 2013-06-30 16:30 | 2013-07-01 07:30 | 0 |  | Ram Graphers Lift Station | Rain 2.57 inches Pump Station Failure | See Report | SSO Reached Public Land
40082 | 38641 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-07-13 02:00 | 2013-07-13 12:00 | 2013-06-13 13:38 | 500 | gallons | Manhole | Rain 2.04 inches Manhole | LTCP Clean lines
40082 | 39414 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-07-16 | 2013-07-16 23:59 | 2013-07-16 09:45 | 0 |  | Clarifiers #1.#2 #3 | Taking down no# 3 clarifier for repairs. no#1 and no #2 clarifiers will still be online.
40082 | 40164 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-09-16 12:00 | 2013-09-16 14:30 | 2013-09-17 08:00 | 0 |  | 1212 S Harrison St | House Lateral City line blocked Jetted line to clear blockage. | Removed Blockage See report | SSO Affected Private Property
40082 | 43350 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-12-21 22:30 |  | 2013-12-22 09:03 | 100000 | gallons | SR 9 & 11 St. Alexandria | 4 inches snow melt Rain 2.33 inches | See Report | SSO Reached Receiving Water | Alexandria Creek
40082 | 43316 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-12-22 | 2013-12-22 | 2013-12-22 07:53 | 100000 | gallons | ST R 9 & 1100 N | Exceeded max Capacity 4 Snow Melt Rain 2.33 inches | See Report | SSO Reached Receiving Water | Pipe Creek
40082 | 43320 | IN0020044 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-12-22 | 2013-12-22 | 2013-12-22 07:53 | 100000 | gallons | manhole Nortrh of Manhole at St Rd 100N & 300 | Exceeded Max Capacity 4 snow melt Rain 2.33 inches. | See Report | SSO Affected Private Property
41882 | 44671 | IN0024562 | SUMMITVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Madison | 2013-12-21 06:00 | 2013-12-22 19:30 | 2014-03-03 14:55 | 98500 | gallons | Wet Well L S #2 East North Main | See Report | See Report | SSO Reached Receiving Water | Mud Creek
42709 | 35567 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-09 09:00 | 2013-01-13 08:00 | 2013-01-09 14:56 | 0 |  | Biosolids plant | Treat Process Bypass. Biosolids plant not operating. No city water. | Construction crew running new line. Final effluent will not be affected. | SSO Occurred at Treatment Plant
42709 | 35592 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-09 12:00 |  | 2013-01-09 16:22 | 480 | gallons/day | Ground next to Kennedy Crossing next to the Wheeler Avenue Drinking Water Plant. | Damaged water line is leaking untreated City water into a storm drain and then into receiving waters. | This is coming from Raw Water Well (clean city water prior to treatment). The damaged line will be located and repaired. Ongoing preventative maintenance. | SSO Reached Receiving Water | White River
42709 | 35635 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-11 22:15 | 2013-01-15 23:31 | 2013-01-16 10:48 | 99999999 | gallons | Primary Clarifiers | Precipitation event resulted in a partially treated release from Primary Clarifiers to receiving waters. | Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 35593 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-14 | 2013-01-19 | 2013-01-04 14:02 | 0 |  | Main Plant Lift Station | Main Plant Lift Station will be bypass pumped for approximately 5 (five) days to install 5th lift station pump along with electrical upgrades. | Ten day notice. Sunbelt pumps will be set up during this process and the stand by pumps will be monitored 24 hours per day by a qualified mechanic. Flow will be diverted to the old plant headworks. Final effluent will not be affected. | SSO Occurred at Treatment Plant
42709 | 35849 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-14 17:22 | 2013-01-14 18:15 | 2013-01-14 19:56 | 500 | gallons | Manhole at 4217 Clark | Partial blockage of sewer line by grease resulted in an untreated release from a manhole to a ditch | Vacuum ditch restore flow clean sewer. Continue preventative maintenance. | SSO Reached Public Land
42709 | 35664 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-18 09:00 | 1/22/1315 00:00:00 | 2013-01-18 08:30 | 0 |  | final Clarifier #5 City of Anderson WWTP | Precipitation event apparently triggered a failure of final clarifier necesitating its shut down which did not affect final effluent. | Clarifier shearing pins. took out of service and drained to determine cause of problem. Final effluent not affected by the bypass of this step in treatment process. Continued P/M | SSO Occurred at Treatment Plant
42709 | 35001 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-22 09:45 | 2013-02-11 15:00 | 2013-02-04 14:02 | 0 | gallons | Secondary Plant Grit Auger at Dity of Anderson WWTP anderson IN | The grit auger at our secondary plant will not turn. We will drain the grit sweep pit to determine cause. | No Release. Treatment Bypass. Partially treated release. Continued P/M | SSO Occurred at Treatment Plant
42709 | 35120 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-22 09:45 | 2013-02-04 15:00 | 2013-01-22 09:44 | 0 |  | City of Anderson WWTP Anderson In | Grit auger at secondary plant not turning. Bypass of treatment process partially treated release. | Drain grit sweep pit to determine cause and repair. Final effluent will not be affected. Continued Preventative Maintenance | SSO Occurred at Treatment Plant
42709 | 35121 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-27 21:35 | 2013-01-28 09:55 | 2013-01-29 10:08 | 5700000 | gallons | City of Anderson WWTP anderson IN | Precipitation event caused partially treated release from Primary Clarifiers. | Flow was being maximized in conjuntion with our operational plan. | SSO Occurred at Treatment Plant | White River
42709 | 35162 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-30 02:38 | 2013-01-31 15:35 | 2013-02-01 10:09 | 28600000 | gallons | City of Anderson WWTP Anderson IN | Precipitation event caused partially treated release from Primary Clarifiers into White River. | Rain event. Flow was being maximized in conjunction with our operational plan | SSO Reached Receiving Water | White River
42709 | 35163 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-01-31 |  | 2013-01-31 14:33 | 0 |  | City of Anderson WWTP Anderson In | Ten day Notice. Primary Plant electrical tie-in for new raw pumps | No Release. Final effluent not affected. Electrical tie-in for lever transmitter/float for new Raw Wet Weather pumps will take place and our existing pumps will be off line for approximately 2-4 hours. Our old existing raw pumps will be on line during this time to handle any flow. This project will be done during dry weather. Continued Preventative Maintenance | SSO Occurred at Treatment Plant
42709 | 35076 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-01 03:00 | 2013-02-02 11:15 | 2013-02-02 11:24 | 0 |  | City of Anderson WWTP Anderson IN | Data loss for meters 015 020 107 016 014 017 066 106 027 103 104 105 due to loss of battery back up power to processor panel. No release | Maintained timely readings at the meters. Continue preventative maintenance plan and maintain spare parts stock. continue preventative maintenance schedule.
42709 | 35050 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-02 07:00 | 2013-02-06 15:00 | 2013-02-01 14:36 | 0 |  | City of anderson WWTP Anderson IN | Final Clarifier #4 will be taken out of service for Annual Preventative maintenance. | No release. Continued Preventative Maintenance | SSO Occurred at Treatment Plant
42709 | 35074 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-03 16:00 | 2013-02-08 15:00 | 2013-02-03 14:07 | 0 |  | Primary Clarifier #2 at Anderson WWTP Anderson IN | Primary Clarifier #2 taken out of service to drain to inspect and repair short flights | Bypass of treatment process. Continued Preventative Maintenance Program | SSO Occurred at Treatment Plant
42709 | 35065 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-04 09:00 | 2013-02-05 12:00 | 2013-02-04 16:11 | 0 |  | City of Anderson WWTP Anderson IN | Data loss for meters 015 202 107016 014 017 066 106 027 103 104 105. Online recorders have gone out of service. | No effluent released. Operators taking readings at meters. Electrical crew on the way. Search for source of problem and repair it. | SSO Occurred at Treatment Plant
42709 | 34956 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-04 16:00 | 2013-02-08 15:00 | 2013-02-04 17:00 | 0 |  | City of Anderson WWTP | Secondary Clarifier #4 jammed sweep arm | No release. Maintenance will need to pump it down and clear the jam. Continue preventiv maintenance
42709 | 35064 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-04 16:00 | 2013-02-08 15:00 | 2013-02-04 17:00 | 0 | gallons | City of Anderson WWTP Anderson IN | Secondary Clarifier #4 jammed sweep arm. No release | Maintenance will pump it down and clear the jam. Continue Preventive Maintenance. | SSO Occurred at Treatment Plant
42709 | 34958 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-07 18:00 | 2013-02-14 15:00 | 2013-02-07 15:05 | 0 |  | Primary Clarifier #1 at City of Anderson WWTP | Primary Clarifier #1 will be taken out of service to drain inspect and repair short flights | No release. Continued Preventive Maintenance | SSO Occurred at Treatment Plant
42709 | 34967 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-07 23:48 | 2013-02-08 02:43 | 2013-02-08 14:40 | 2000000 | gallons | Primary Clarifiers at the City of Anderson WWTP. | Precipitation event (.30 Inch) triggered an overflow from the Primary Clarifiers to White River. Partially treated release. | Rain Event. Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 34920 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-11 12:00 | 2013-02-11 15:00 | 2013-02-11 15:10 | 0 | gallons | Occurred at the City of Anderson WWTP. | Data loss for meters 053 054 and 055 due to loss of power at meter base caused by construction equipment hitting a panel. No release of effluent. | Repaired power feed to meters. Continue preventative maintenance plan and maintain spare parts stock. Warn construction companies of existing conduit. | SSO Occurred at Treatment Plant
42709 | 34935 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-12 14:00 | 2013-02-14 15:00 | 2013-02-13 07:24 | 0 | gallons | City of Anerson WWTP Anderson IN. final clarifier #6 | Treatment Process Bypass to perform preventative maintenance on Final Clarifier #6 | No Release. Preventative Maintenance performed on Final Clarifier #6. P/M plan continued | SSO Occurred at Treatment Plant
42709 | 34905 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-14 09:30 | 2013-02-15 15:00 | 2013-02-14 09:20 | 0 |  | City of Anderson WWTP Filter Plant | Filter #2 at Filter plant will be taken out of service to repair air leak. No effluent released | Continued P/M | SSO Occurred at Treatment Plant
42709 | 34875 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-15 11:30 | 2013-02-15 14:30 | 2013-02-15 15:00 | 0 | gallons | City of Anderson WWTP | Data loss for Meter 053 due to signal wire connection | No release. Checked all signal wires will continue preventative maintenance plan. Warned construction company of Panel Location | SSO Occurred at Treatment Plant
42709 | 34874 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-19 | 2013-02-25 15:00 | 2013-02-19 07:20 | 0 |  | East Primary Secondary Plant. Anderson IN | East Primary at the Secondary Plant was taken out of service to inspect and repair short flights. | Continued P/M | SSO Occurred at Treatment Plant
42709 | 34838 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-20 10:00 | 2013-02-20 12:00 | 2013-02-20 09:50 | 0 |  | City of Anderson WWTP Secondary Plant Processor | Bypass of a Treatment Process in the Treatment Plant due to a card failure on Secondary Plant Processor | Check signal wires & continue O.M.s Maintain stock and continue P.M.s
42709 | 34812 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-25 08:30 | 2013-02-25 09:00 | 2013-02-25 15:56 | 100 | gallons | Incident occurred at the Ed Martin Lift Station and affected the ground at the site. | Pumps had kicked out at Ed Martin lift station causing overflow to ground at the site. | The Sewer Department cleaned up the area. Both pumps were pulled and cleaned. The autodialer had failed and was repaired also. A work order will be written to check all verbatims to verify their operation. | SSO Reached Public Land; Surface Soil
42709 | 34735 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-02-26 08:25 | 2013-02-27 04:50 | 2013-02-27 12:55 | 19200000 | gallons | Primary Clarifiers | On 2/26/2013 a 1.12 inch rainfall triggered a Partially Treated Release from the Primary Clarifiers | Rain Event caused the problem. After rain stopped operation returned to normal. | SSO Reached Receiving Water | White River
42709 | 34611 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-02 | 2013-03-02 07:45 | 2013-03-02 07:45 | 0 |  | No Release | Bypass of a treatment process. Secondary clarifier #6 jammed sweep arm. | Maintenance will need to pump it down and clean the jam. Continue preventive maintenance. | SSO Affected Private Property
42709 | 34595 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-06 08:15 | 2013-03-06 16:00 | 2013-03-06 08:10 | 0 |  | No release | Bypass of Treatment Process Equipment Failure Replacing meter 49 due to erratic readings. | Replacing meter follow preventative maintenance plan as directed. | SSO Occurred at Treatment Plant
42709 | 34926 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-07 | 2013-03-17 | 2013-04-04 08:42 | 0 |  | Electrical tie-in Bus B | Bypass of a Treatment Process Construction Related Bus B will be shut down so electrical contractor (IE) can pull and land the feeders for permanent power into the new preliminary treatment facility (PTF) | Our final effluent will not be affected. Bus B feed had to also be taken out at the transformer feed.
42709 | 34603 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-07 12:36 | 2013-03-07 | 2013-03-07 12:36 | 0 |  | Electrical tie-in Bus B | Bypass of a Treatment Process Construction Related Bus B will be shut down so electrical contractor (IEI) can pull and land the feeders for permanent Power into the new preliminary treatment Facility (PTF) | Our final effluent will not be affected. Continued P/M
42709 | 34498 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-11 01:14 | 2013-03-11 04:15 | 2013-03-12 09:25 | 1900000 | gallons | Primary Clarifiers White River | Partially Rain .29 inchesRain Event | Primary Clarifiers White River | SSO Reached Receiving Water | White River
42709 | 34780 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-14 | 2013-03-24 | 2013-03-14 13:27 | 0 |  | Clarifiers #7 and #8 Flow Split | Bypass of a Treatment Process Construction Related | FA Wilhelm will be by pass pumping a 72 inch line for the construction of flow split #2. Our final effluent will not be affected. And the West Aeration basin and discharge the flow into the center of the four existing clarifiers. Continue \PM | SSO Occurred at Treatment Plant
42709 | 34727 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-16 13:00 | 2013-03-22 15:00 | 2013-03-16 13:54 | 0 |  | Meters 24252829 65 | Construction related Equipment Failure During construction FA Wilhelm hit a fiber optic line which feeds information to our Bio-Solids section meters. FA Wilhelm is on plant grounds to determine what measures need to be taken to fix. | Our final effluent will not be affected. Continue P/M | SSO Occurred at Treatment Plant
42709 | 34949 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-18 15:36 | 2013-03-18 18:53 | 2013-03-18 14:26 | 24000000 | gallons | Primary Clarifiers White River | Partially Treated Release Rain .23 inches Rain Event | Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 35142 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-23 17:44 | 2013-03-26 19:02 | 2013-03-27 14:43 | 447000 | gallons | Primary Clarifiers White River | Partially Treated Release Snow 6-8 inches Snow Melt | Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 35440 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-26 15:00 | 2013-04-01 15:00 | 2013-03-26 15:17 | 0 |  | City of Anderson WWTP | Final Clarifier #3 shearing pins continuously. No release. Partially treated effluent and treatment process bypassed. | Inspect and determine reason for sheared pins. Continued P/M. | SSO Occurred at Treatment Plant
42709 | 35137 | In0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-28 10:00 | 2013-04-04 15:00 | 2013-03-28 10:29 | 0 |  | Final Clarifier #5 Clarifiers 346 | Bypass of a Treatment Process Equipment Failure Final clarifier #5 taken out of service for preventative maintenance to inspect and jet sweep arms. | Continued P/M | SSO Occurred at Treatment Plant
42709 | 35281 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-31 18:00 | 2013-04-04 | 2013-03-31 09:28 | 0 |  | #2 Primary clarifier #1-3-4 Primary | Bypass of a Treatment Process Equipment Failure Gear and short flight issues | Maintenance estimated 3 days for this project. Annual PMS will all be done. this will hot effect our final effluent. | SSO Occurred at Treatment Plant
42709 | 35510 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-02 10:00 | 2013-04-02 10:30 | 2013-04-02 10:38 | 0 |  | Frozen Bisulfife Diffuser White River | Bypass of a Treatment Process Equipment Failure Frozen sodium bisulfite diffused also take discharge line partially frozen | Standby pump had bad hose and also would not pump. Hose being replaced heaters are running on discharge lines. We went approximately 30 minutes without bisulfite feed tanks also failed. | SSO Reached Receiving Water | White River
42709 | 35496 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-09 01:00 | 2013-04-12 03:00 | 2013-04-09 12:31 | 0 |  | Primary Clarifier #6 Clarifiers 3.45 | Bypass of a Treatment Process Clarifier #6 was taken out of service to drain and inspect. We suspect during construction and bypass pumping debris has fallen in and obstructed the sweep arms causing drive pins to shear. | Construction personnel were notified of this situation and are actively pursuing ways to keep debris form fallen into the clarifiers. Continued P/M
42709 | 35364 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-10 18:20 | 2013-04-12 23:55 | 2013-04-13 14:12 | 37300000 | gallons | Anderson Water Pollution Control Anderson IN | A precipitation event necessitated taking the fine screen headworks offline to prevent an overflow in the fine screen headworks building. Result was release of partially treated effluent. | No other action taken. Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant
42709 | 35391 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-12 15:00 | 2013-04-19 15:00 | 2013-04-14 15:18 | 14000000 | gallons | City of Anderson WWTP Anderson IN | In Primary Clarifier #3 the north side flights are shearing pins. South side flights and short flights are still in operation and flow is still going to the primary as of this date. Final effluent is not affected. | Primary Clarifier #3 will be inspected to determine cause of failure. Suspect that gear box needs to be rebuilt. No release and no impact on final effluent. Preventative Maintenance Program will continue | SSO Occurred at Treatment Plant
42709 | 36420 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-16 15:18 | 2013-04-21 07:15 | 2013-04-22 07:05 | 94200000 | gallons | Anderson WWTP Primary Clarifiers | Precipitation event triggered a partially treated release from WWTP to receiving waters. | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 36193 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-19 08:21 | 2013-04-19 08:30 | 2013-04-19 09:27 | 7500 | gallons | Deer Creekk Lift Station | Precipitation and lift station failure resulted in an untreated release from the lift station to ground surrounding the lift station. | Sewer maintenance staff bypass pumping the the station adn cleaning the area while maintenance staff are repairing the lift station. Repairs and preventative maintenance will be ongoing. | SSO Reached Public Land
42709 | 36350 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-22 09:03 | 2013-04-29 15:00 | 2013-04-22 10:01 | 0 |  | City of Anderson WWTP | Primary Clarifier #3 taken out of service due to a broken long flight and wear strips coming off. | Flow diverted to Clarifiers #1 #2 and #4. No untreated or partially treated release. Continued Prventative Maintenance. | SSO Occurred at Treatment Plant
42709 | 36311 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-23 | 2013-04-24 | 2013-04-25 06:55 | 0 |  | Data Loss | Bypass of a Treatment Process Equipment Failure Lost communication - Data loss | Card went bad. Meters at stations were working. Therefore we has most totalizes not effected. Final effluent was not effected. Lost meters from the parshell flow to final effluent. | SSO Affected Private Property
42709 | 36672 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-23 13:21 | 2013-04-26 15:24 | 2013-04-27 11:42 | 7500000 | gallons | Waste Water Treatment Plant Primary Clarifiers | Precipitation event caused a partially treated release from the primary clarifiers to receiving water. | Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 36683 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-23 13:21 | 2013-04-26 15:24 | 2013-04-27 11:42 | 75000000 | gallons | WWTP | Pricipitation event triggered a partially treated release from the Primary Clarifiers to receiving water. | Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 36619 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-25 13:00 | 2013-05-03 15:00 | 2013-04-25 13:26 | 0 |  | Anderson WWTP | Clarifier #4 taken outof service to inspect return line and jet out sweep arms. We suspect debris from sonstruction has fallen into clarifier. Final effluent will not be affected. | Continued PM. Clarifiers 35678 still in services. No impact on final effluent. | SSO Occurred at Treatment Plant
42709 | 36664 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-26 | 2013-05-07 | 2013-04-26 08:43 | 0 |  | Morton Street In line storage project. | Ten day notice of implementation of system upgrade project | The 2 new storage structures will be bypassed during final phases of construction. Dams will be temporarily built upstream from structures and pumped around to a downstream site. Sunbel Rentals is the sub contractor fro R.L. Turner(?). Service Tech will be on site at all times during project.In the event of rain the structures will be cleaned of materials and the flow will process as normal through the area. This project will not cause any unwanted release and will not affect operations or sewer maintenance. | SSO Occurred at Treatment Plant
42709 | 36693 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-28 04:48 | 2013-04-28 23:39 | 2013-04-29 08:53 | 4200000 | gallons | Primary clarifiers WWTP | Precipitation event triggered a partially treated release from the primary clarifiers to receiving water. | flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 36731 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-04-30 13:00 | 2013-05-07 15:00 | 2013-04-30 13:33 | 0 |  | City of Anderson WWTP | Equipment failure due to construction debris required that Final Clarifier #6 be removed from service to be cleaned and jet swept. | Bypassing only one out of 7 clarifiers. Final effluent will not be affected.Continue with Preventative Maintenance Program. | SSO Occurred at Treatment Plant
42709 | 36738 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-01 08:00 | 2013-05-06 07:00 | 2013-05-01 14:50 | 0 |  | City of Anderson WWTP | Conveyor belt from presses to cake mixer is locked up. | Final effluent not affected. No bypass or treatment. Continue Preventive Manintenance Program. | SSO Occurred at Treatment Plant
42709 | 36818 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-09 19:41 | 2013-05-10 05:00 | 2013-05-10 14:39 | 4 | gallons | Primary Clarifiers | Rain .78 inches | Flow was being maximized in conjunction with our operational plan | SSO Occurred at Treatment Plant
42709 | 37024 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-17 17:28 | 2013-05-17 22:13 | 2013-05-18 14:55 | 4800000 | gallons | Primary Clarifiers | Rain Event .77 inches | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 37027 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-20 13:00 | 2013-05-24 15:00 | 2013-05-20 13:26 | 0 |  | Final Clarifier #3 | Treatment Bypass Equipment Failure Final Clarifier #3 taken out of service to inspect why sheer pins are breaking and to inspect sweep arms. | Continued P/M | SSO Occurred at Treatment Plant
42709 | 37091 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-22 18:40 | 2013-05-22 21:30 | 2013-05-23 10:30 | 2 | gallons | Primary Clarifiers | Treatment Bypass Rain .35 inches Rain Event | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant
42709 | 37159 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-24 10:00 | 2013-05-24 13:30 | 2013-05-24 15:52 | 0 |  | No Release | Power Failure Equipment Failure. Due to the failure of a redundant power switch meter data recording capability was lost. Operators were still able to take readings at meters. | Equipment was repaired as quickly as possible staff worked through lunch. Evaluate need for reconfiguration of equipment. We will update and purchase new equipment as necessary. | SSO Affected Private Property
42709 | 37167 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-24 21:00 | 2013-06-05 15:00 | 2013-05-24 21:07 | 0 |  | Final Clarifier #3 | Equipment Failure final clarifier #3 taken out of service to determine why shear pins keep breaking. | Flow will be diverted to final clarifiers 45678 Continued P/M | SSO Occurred at Treatment Plant
42709 | 37235 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-27 04:47 | 2013-05-28 02:17 | 2013-05-28 13:21 | 10 | gallons | Primary Clarifiers | Treatment Bypass Rain 1.64 inches. | Flow was being maximized in conjunction with our operation plan. | SSO Affected Private Property | White River
42709 | 37236 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-27 04:47 | 2013-05-28 02:17 | 2013-05-28 13:22 | 10 | gallons | Primary Clarifiers | Treatment Bypass Rain 1.64 Rain | Flow was being maximized in conjunction with our operational plan. | SSO Affected Private Property | White River
42709 | 37197 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-29 09:25 | 2013-05-29 09:28 | 2013-05-29 09:24 | 0 |  | Final Clarifiers #7 #8 | Treatment Bypass Construction Related Final clarifiers #7 #8 return pumps will be shut down for approximately 2 minutes so electricians can download historical data. | Our final effluent will not be affected continued P/M | SSO Affected Private Property
42709 | 37511 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-31 11:30 | 2013-05-31 13:30 | 2013-05-31 15:31 | 0 |  | Primary Clarifiers City of Anderson WWTP | During a precipitation event plant flow was not maximized due to operator error and construction restrictions. Resulting in treatment bypass to receiving water. | Piping adjusted to maximize plant flow. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 37563 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-05-31 11:57 | 2013-05-31 17:49 | 2013-06-01 17:42 | 3800000 | gallons | Primary Clarifiers at Anderson WWTP | Precipitation event coupled with flow maximization in plant caused a treatment bypass to receiving waters. | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 37639 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-01 04:15 | 2013-06-01 11:25 | 2013-06-03 07:05 | 7300000 | gallons | City of Anderson WWTP Primary Clarifiers | Precipitation event triggered bypass of primary clarifiers at WWTP to receiving water. | Flow was being maximized in conjunction with operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 37687 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-01 17:15 | 2013-06-21 15:00 | 2013-06-10 13:16 | 0 |  | Final Clarifier #3 | Equipment Failure Unknown. Final clarifier #3 taken out of service to determine why high torque alarm and shear pins keep breaking. | Our maintenance staff along with MK BETTS engineering will work together to determine what the problem is. Clarifiers 45678 will receive flow. Continued P/m | SSO Occurred at Treatment Plant
42709 | 37564 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-01 17:15 | 2013-06-10 15:00 | 2013-06-01 17:42 | 0 |  | Anderson WWTP | Final Clarifier #3 taken out of service due to continued high torque alarm and breaking shear pins. | Manintenance staff and MK BETTS engineering working together to determine source of problem. Clarifiers 4567 and 8 will receive flow. | SSO Occurred at Treatment Plant
42709 | 37762 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-07 | 2013-06-07 23:59 | 2013-06-07 | 0 |  | No Release | Construction Related To tie in our new PTF Wilhelm will be by passing our primary effluent from the normal 36 force main to old 30 Force Main and Temp. Piping from Sunbelt rentals to aeration Basins. | At this time they will be using our primary effluent pumps to get flow to the aeration basins. The new dry weather pump station needs to be tied into 36 force main. Also the influent to the new PTF and effluent from PTF will be tied in. Project estimate at 3 days max. This should not effect our final effluent or the White River. | SSO Occurred at Treatment Plant | White River
42709 | 37757 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-07 01:30 | 2013-06-07 03:30 | 2013-06-07 10:06 | 0 |  | No Release (Data Loss) | Power Failure Equipment Failure Due to surge tank motor burning up it caused a short (ground fault) which kicked out the main feed breaker to the tertiary plant. Data was lost to meters #46 03 and 50 for approximately two (2) hours. | Electricians were called to the scene to determine what the problem was. Electricians isolated the faulty surge tank motor from the system and unwired it. | SSO Occurred at Treatment Plant
42709 | 37788 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-12 10:00 | 2013-06-19 15:00 | 2013-06-12 10:29 | 0 |  | Primary Clarifier #1 | Equipment Failure Primary clarifier #1 taken out of service to repair drive chain for short flight s. Flow will be diverted to Primary s #23 and 4. Our final effluent will not be affected. | Continued P/M s | SSO Occurred at Treatment Plant
42709 | 37946 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-13 02:55 | 2013-06-13 13:15 | 2013-06-14 11:19 | 2 | gallons | Primary Clarifiers White River | Rain 1.16 inches rain event. | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 37959 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-14 02:12 | 2013-06-14 14:15 | 2013-06-14 15:21 | 300 | gallons | Primary effluent bypass channel. | While FA Wilhelm construction was testing the new wet weather pumps we had an effluent by pass for approximately three (3) minutes due to the switch over back to the old raw pump station which was currently in service at the time. | Pumps were put back to normal full operation and plant flow leveled off immediately. Continued P/M s | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 38862 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-22 17:25 | 2013-06-22 21:52 | 2013-06-23 09:19 | 0 |  | White River | Rain .98 inches | Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water | White River
42709 | 38863 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-23 17:42 | 2013-06-23 18:45 | 2013-06-24 12:37 | 0 |  | Primary clarfiers | Rain .31 inches | Flow was being maximized in conjunction with our operational plan.
42709 | 37794 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-24 |  | 2013-06-12 13:59 | 0 |  | No Release | Construction Related Temporary pumps and piping will be set up to redirect plant flow from Primary plant to the new Preliminary plant. Please see attached letters from FA Wilhelm concerning this by pass. | Estimated time to complete project will be approximately one (1) day. Our final effluent will not be affected.
42709 | 38892 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-26 02:20 | 2013-06-26 08:40 | 2013-06-26 13:02 | 0 |  | White River | Rain .53 inches Construction Related. See Report | See Report | SSO Reached Receiving Water | White River
42709 | 39056 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-26 02:23 | 2013-06-26 08:40 | 2013-06-27 08:35 | 0 |  | Primary Clarifiers | Rain Event Treatment Bypassed |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 39058 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-26 02:23 | 2013-06-26 08:40 | 2013-06-27 08:30 | 0 |  | Primary Clarifiers | Rain .70 inches. |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 39183 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-28 18:11 | 2013-06-28 23:30 | 2013-06-29 16:08 | 0 |  | Primary Clarifiers | Rain .70 inches rain event | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 39188 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-29 14:30 | 2013-06-29 19:00 | 2013-06-30 09:40 | 0 |  | White River | Rain .34 inches rain event | See Report | SSO Reached Receiving Water | White River
42709 | 38252 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-06-30 06:54 | 2013-07-01 14:38 | 2013-07-02 09:44 | 0 |  | Primary Clarifiers | Rain 1.56 inches | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 39522 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-07-02 02:41 | 2013-07-03 05:20 | 2013-07-05 14:55 | 0 |  | Primary Clarifiers | Rain 1.24 inches Rain Event | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 39584 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-07-18 | 2013-07-18 08:34 | 2013-07-18 10:00 | 0 |  | No Release | Power Failure We will lose tower overflow and main plant lift station data during the tie in of the new MGD circular chart. | See Report
42709 | 39423 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-07-18 16:00 | 2013-07-19 16:00 | 2013-07-19 09:00 | 0 |  | No Release | Construction Related Power Failure During construction of old system tie in to new PTF plant construction crews hit the fiber optic line which feeds information to our wonderware system. Operators can still get readings at the meters. The meters effected were 222324 25 26 and 27 | See Report
42709 | 39622 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-07-29 | 2013-07-29 23:59 | 2013-07-09 16:30 | 0 |  | Bypass of Treatment Biotowers | The fine screen in front of the biotowers failed and has to be pulled for repairs. This required that we bypass the biotowers during the removal process. | See Report | SSO Occurred at Treatment Plant
42709 | 40410 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-08-02 21:45 | 2013-08-03 01:15 | 2013-10-01 13:31 | 0 |  | #4 Aeration Basin | Equipment Failure #4 Aeration basin will be taken out of service for the replacement of diffusers and bad piping. | See Report
42709 | 39738 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-08-03 03:50 | 2013-08-03 09:50 | 2013-08-04 09:49 | 0 |  | Primary Clarfiers | Rain .73 inches | Flow was being maximized in conjunction with our operational plan. | SSO Reached Receiving Water
42709 | 39742 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-08-08 08:00 | 2013-08-12 16:00 | 2013-08-08 13:16 | 0 |  | Belt Presses | Equipment Failure. Belt presses shut down during repair of hydraulic cylinder on press #1 | Final effluent will not be effected. Maintenance crew is replacing cylinder continue PM
42709 | 39826 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-08-27 08:00 | 2013-08-28 15:00 | 2013-08-27 08:47 | 0 |  | Biosolids section | Equipment Failure Belt press #2 not working. Broken belt sensor not functioning correctly. Final effluent will not be affected. | We are not operating the equipment until repairs are complete. Continuing preventive maintenance. | SSO Occurred at Treatment Plant
42709 | 40103 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-11 | 2013-09-11 17:00 | 2013-09-11 16:18 | 0 |  | Unknown Creek in Anderson | A problem was reported to the Stormwater Dept. Sewage was traced back to appear to be going from a sanitary line to a storm line. | A plug was placed in the line. 450 feet of storm line was flushed. Clean the storm line and televise to identify the problem. Repair the pipe to avoid this problem in the future. | SSO Reached Receiving Water
42709 | 40151 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-12 09:08 | 2013-09-12 10:00 | 2013-09-14 12:51 | 0 |  | Primary Clarifiers | Rain .40 inches rain event | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 40152 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-12 09:08 | 2013-09-12 10:00 | 2013-09-14 12:45 | 0 |  | Primary Clarifiers | Treatment Bypassed Rain Event | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 40255 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-19 06:05 | 2013-09-19 13:30 | 2013-09-20 12:30 | 0 |  | Primary Clarifiers | Rain 1.75 inches Rain Event | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 40278 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-20 20:05 | 2013-09-20 21:20 | 2013-09-21 10:00 | 0 |  | Primary Clarifiers | Rain .64 inches Rain Event | Flow was being maximized in conjunction with our operational plan | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 40281 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-21 01:30 | 2013-09-21 03:30 | 2013-09-21 09:53 | 0 |  | Primary Clarifiers | Primary Clarifiers | Rain .64 inches Rain Event | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 40287 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-23 10:00 | 2013-09-23 15:00 | 2013-09-23 10:27 | 0 |  | Final Clarifier #4 | Equipment Failure Final clarifier #4 taken out of service to inspect and determine why shear pins keep breaking. Our final effluent will not be affected. | Continued P/M s | SSO Occurred at Treatment Plant
42709 | 39621 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-30 07:30 | 2013-09-30 08:30 | 2013-09-30 10:02 | 0 |  | Manhole Ditch/Field | Equipment Failure Leak reported yesterday we could not find it. Discovered upon further investigation this manhole. | See Report
42709 | 41176 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-22 21:30 | 2013-10-24 10:00 | 2013-10-22 14:15 | 0 |  | Biosolids Section | Equipment failure Cement Tech cake mixer not working. Replacing the output auger assembly. Final effluent will not be affected. | We are not operating the equipment until repairs are complete. Continuing preventive maintenance. | SSO Occurred at Treatment Plant
42709 | 42106 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-11-24 19:16 | 2013-11-24 20:01 | 2013-11-24 22:28 | 0 |  | Park Rd north of 38th Manhole | Equipment Failure air relief valve failure. | See Report | SSO Affected Private Property
42709 | 42151 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-11-25 12:06 | 2013-11-25 12:21 | 2013-11-25 13:23 | 0 |  | Manhole | Equipment failure Customer complaint | Removed Blockage See Report | SSO Reached Public Land
42709 | 42388 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-10 11:07 | 2013-12-10 12:30 | 2013-12-10 20:22 | 0 |  | Manhole | Equipment Failure due to blockage in outlet of a converted lift station removed a head gasket that had condoms and the likes all tangled up in it. | Removed Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water | Killbuck Creek
42709 | 43349 | IN0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-21 22:01 | 2013-12-22 10:00 | 2013-12-22 11:38 | 10000 | gallons | Clean out at 4204 Clark | Rain 2 inches Checked at midnight last nite entire area under water. All manholes and storm pumps surcharged. | Removed Blockage | SSO Reached Public Land; SSO Affected Private Property
42709 | 43440 | IN0032476 Outfall 001 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-23 09:10 | 2013-12-23 12:00 | 2013-12-23 14:30 | 0 |  | Failure to maximize | Equipment Failure Rain 4 inches We believe level sensors have failed causing the pumps not to run properly in automatic. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 41126 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-05 09:20 | 2013-10-05 15:23 | 2013-10-06 14:45 | 0 |  | Primary Clarifiers | Rain 1.80 inches | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
12657 | 41046 | IN0032476 Outfall 005 | Carmel Waste Water Treatment Plant | Madison | 2013-10-06 04:08 | 2013-10-06 08:30 | 2013-10-07 09:46 | 0 |  | Primary Clarifiers | Rain 1.51 inches | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 41178 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-22 13:30 | 2013-10-22 13:35 | 2013-10-22 14:11 | 0 |  | Final Clarifier #6 | Equipment Failure While maintenance staff were pumping down Final Clarifier #6 into the scope pit the line securing the discharge pipe broke loose allowing the clarifier discharge to go into the ground. | Repaired pipe See Report | SSO Occurred at Treatment Plant
42709 | 41823 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-28 09:58 | 2013-10-28 10:48 | 2013-11-12 14:37 | 0 |  | Sanitary Sewer overflow rangeline Rd. Liftstation | Power Failure Rangeline Rd. lift station lost power feed due to a blown fuse on main power transformer. WPC electricians along with Light and Power personnel assessed the situation and replaced the fuse. | Repaired Pump Station See Report | SSO Reached Public Land; SSO Reached Receiving Water | White River
42709 | 41125 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-28 13:51 | 2013-11-11 13:51 | 2013-10-18 13:00 | 0 |  | #3 aeration basin | Equipment Failure #3 aeration basin will be taken out of service to replace diffusers and repair piping. | Repaired Pipe See Report | SSO Occurred at Treatment Plant
42709 | 41368 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-28 14:41 | 2013-10-28 10:48 | 2013-10-28 13:03 | 0 |  | Sanitary sewer overflow Rangeline Rd. liftstation | Power failure Rangeline R. lift station lost power feed due to a blown fuse on main power. WPC electricians along with light an power personnel assessed the situation and replaced the fuse. | Repaired Pump Station See Report | SSO Reached Public Land; SSO Reached Receiving Water | White River
42709 | 41512 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-31 03:10 | 2013-11-01 04:55 | 2013-11-01 09:09 | 0 |  | Primary Clarifiers | Rain 1.8 inches Rain Event | Flow was being maximized in conjunction with our operational plan. Continued P/M s | SSO Reached Receiving Water
42709 | 41944 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-11-17 03:15 | 2013-11-17 21:20 | 2013-11-18 10:40 | 0 |  | Primary Clarifiers | Rain 1.6 inches | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 42607 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-11-18 14:00 | 2013-12-18 | 2013-11-20 10:10 | 0 |  | #3 filter pump motor blasting | Equipment Failure #1 & #2 | See Report
42709 | 43408 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-20 11:30 | 2013-12-25 04:00 | 2013-12-25 11:57 | 0 |  | Primary Clarifiers | Rain 3.86 inches | See Report | SSO Reached Receiving Water | White River
42709 | 43422 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-21 09:00 | 2013-12-21 09:45 | 2014-01-03 14:40 | 500 | gallons | manhole from solids handling belt presses | Exceeded Max Capacity Rain 1.7 inches Due to high flow the manhole from solids handling overflowed because main Lift Station was over capacity. | See Report | SSO Reached Receiving Water | White River
42709 | 43326 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-21 09:30 | 2013-12-21 09:45 | 2013-12-21 14:55 | 500 | gallons | Manhole from solids handling bel presses | Exceeded Max Capacity Rain 1.7 inches Due to high flow the manhole from solids handling overflowed because main plant. Lift station was over capacity. | See Report | SSO Reached Receiving Water | White River
42709 | 43321 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-21 18:00 | 2013-12-21 19:00 | 2013-12-21 19:30 | 500 | gallons | Deer Creek Station | Exceeded max Capacity Rain 4 inches Due to the High Flow Lift Station pumps couldn t keep up. umps were doing all it could | See Report | SSO Affected Private Property
42709 | 43406 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-23 09:10 | 2013-12-23 12:00 | 2013-12-23 14:15 | 0 |  | Failure to maximize | Equipment Failure Rain 4 inches We believe level sensors have failed causing the pumps not to run properly in automatic. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 43413 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-30 14:00 | 2014-01-07 15:00 | 2013-12-30 13:35 | 0 |  | Final Clarifier #6 No Release | Equipment Failure Final clarifier #6 taken out of service to inspect and repair bottom sweep drive bearing and also replace sheer pin |  | SSO Occurred at Treatment Plant
42709 | 41717 | IN0032476 Outfall 005 #6 Secondary Clarifier repairs were completed on 11-21-13 per followup per phone conversation with Mr Caldwell on 11-21-13. | Anderson Municipal Sewage Treatment Plant | Madison | 2013-11-06 14:00 | 2013-11-21 08:30 | 2013-11-07 08:00 | 0 |  | #6 Secondary Clarifier | Equipment Failure Flow will be diverted to #1234578 secondary clarifiers | See Report | SSO Reached Receiving Water | White River
42709 | 41115 | IN0032476 Reached ditch and receiving water however river name wasn t given. | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-11 11:00 | 2013-10-11 20:30 | 2013-10-11 14:58 | 0 |  | Sanitary Sewer | Untreated Release | Plug sewer by pass pump Repair sanitary sewer | SSO Reached Receiving Water
42709 | 39824 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-08-26 13:00 | 2013-08-26 15:00 | 2013-08-27 13:22 | 0 |  | No Release | Equipment Failure filter plant bar screen was taken out of service and can not be repaired due to outdated parts. A new bar screen has been quoted and ordered and should arrive in 4 to 6 weeks. | Continued P/M | SSO Occurred at Treatment Plant
42709 | 40648 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-09-29 11:40 | 2013-09-29 15:40 | 2013-09-30 09:32 | 0 |  | Primary Clarifiers | Rain .95 inches Treatment Bypass | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
42709 | 40780 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-05 09:20 | 2013-10-05 15:23 | 2013-10-06 14:45 | 0 |  | Final Clarifiers | Rain 1.80 inches | Flow was being maximized in conjunction with our operational plan. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water
42709 | 41053 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-07 10:00 | 2013-10-15 15:00 | 2013-10-07 10:00 | 0 |  | East Old Primary Clarifier | Equipment Failure east Old Primary Clarifier taken out of service to inspect and repair short fights. | Our final effluent will hot be affected. Continued P/M s | SSO Occurred at Treatment Plant
42709 | 43324 | IN0032476 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-21 08:15 | 2013-12-22 07:00 | 2013-12-21 22:21 | 0 |  | Manhole from solids main plant lift station | Exceeded Max Capacity Rain 4 inches | See Report | SSO Reached Receiving Water | White River
42709 | 35172 | IN0032476 Projected testing of switch grears the week of 4-8-2013 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-03-28 | 2013-04-07 | 2013-03-28 15:39 | 0 |  | Testing of Zone interlock system | Bypass of a Treatment Process Construction Related Power Failure Testing of zone interlock system for existing electrical switch gears will take place the week of 4-8-2013 | Intermittent power outages will take place during this time. Our final effluent will not be affected.
42709 | 39541 | IN0032478 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-07-10 15:15 | 2013-07-10 17:45 | 2013-07-11 11:01 | 0 |  | Primary Clarifiers | Rain .64 inches | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water
42709 | 43725 | IN0032478 Outfall 005 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-12-30 14:00 | 1914-02-18 14:30 | 2013-12-27 13:54 | 0 |  | Final clarifier #6 No Release | Equipment Failure Final clarifier #6 taken out of service to inspect and repair bottom sweep drive bearing and also replace sheer pin. | See Report | SSO Occurred at Treatment Plant
40186 | 35796 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-01-16 18:00 |  | 2013-01-17 13:21 | 550000 | gallons | CSO #016 | Precipitation event triggered untreated release from CSO to receiving waters | Maintaining maximum flow at WWTP. | SSO Reached Receiving Water | Big Duck Creek
40186 | 35797 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-01-16 18:00 |  | 2013-01-17 13:12 | 1100000 | gallons | CSO #101 | Precipitation event triggered utreated release from CSO | Maintaining peak flow at WWTP. | SSO Reached Receiving Water | Big Duck Creek
40186 | 35115 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-01-19 12:00 |  | 2013-01-22 14:16 | 3097000 | gallons | Elwood WWTP Elwood IN | Extreme precipitation event casued Big Duck Creek to overflow its banks and flood into the EQ Basin/ Outfall 101. The flooding resulted in Tratment Bypass partially treated release blending with final effluent. | Discharge was not disinfected. Turned off aeration and mixing to EQ cell that overflowed to allow contents to settle. Operational strategy for EQ Basin is to keep Basin empty as possible to maximize capture during wet weather. | SSO Reached Receiving Water | Big Duck Creek
40186 | 35117 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-01-20 | 2013-01-20 23:59 | 2013-01-22 14:16 | 2517000 | gallons | Elwood WWTP Elwood IN | Extreme precipitation event cause Big duck Creek to overflow its banks and flood the EQ Basin/Outfall 101 resulting in non disinfected effluent partial treatment release treatment bypass. | Turned off aeration and mixing to EQ cell that overflowed to allow contents to settle. Operational strategy for EQ Basin is to keep basin empty as possible to maximize capture during wet weather. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Big Duck Creek
40186 | 35118 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-01-21 | 2013-01-21 23:59 | 2013-01-22 14:16 | 2314000 | gallons | Elwood WWTP Elwood IN | Extreme precipitation event caused Big Duck Creek to overflow its banks and flood EQ Basin/Outfall 101. Result was partially treated release not disinfected due to treatment process bypassnd the effluent blended with the flood waters of the creek. | Turned off aeration and mixing to EQ cell that overflowed to allow contents to settle. Operational strategy for EQ Basin is to keep basin empty as possible to maximize capture during wet weather. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Big Duck Creek
40186 | 35087 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-02-07 06:30 | 2013-02-07 13:40 | 2013-02-07 16:30 | 496666 | gallons | Secondary clarifier effluent Elwood WWTP Elwood IN | Motor for the tertiary filter spent backwash pump failed causing the mudwell tank to overflow. To avoid additional flooding it necessary to bypass tertiary filters. Partially treated release. | No release to Waters of theState. Overflow contained on site. Bypassed tertiary filters pumped spent backwash water from mudwell to head of plant for treatment. Found new motor picked it up and installed it. Stopped bypass at 1:40 P.M. Stored some flow in the available space in the EO without overflowing CSO 101. Obtained two quotes to purchase a spare motor. | SSO Occurred at Treatment Plant
40186 | 34942 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-02-13 22:20 | 2013-02-14 04:00 | 2013-02-14 10:01 | 693332 | gallons | CSO 005 Elwood IN | CSO 005 had an Untreated discharge due to a major water main break. | After using all pumping equipment available including renting a 6 pump and turning of aeration blower in anticipation of discharge from CSO10 that didn t happen the water main break was finally repaired and flow returned to normal. City is investigating the purchase of a 6 pump. | SSO Reached Receiving Water | Big Duck Creek
40186 | 36018 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-04-11 08:00 | 2013-04-11 | 2013-04-17 12:47 | 0 |  | 1344 South E. Street | Precipitation event caused and untreated release into a residential basement. | Basement backup was caused by the excessive amount of water in the collection system which created pressure on the residential lateral. The residential lateral was cleaned but now blockage or obstruction was found. When the levels in the collection system dropped the backup stopped. Recommended to the homeowner that she install a check valve to prevent future backups during these extreme precipitation events. The City of Elwood is in the process of purchasing a camera truck to start filming the collection system to find and diagnose trouble areas. | SSO Basement Backup
40186 | 35807 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-04-13 | 2013-04-15 14:40 | 2013-04-15 14:40 | 500 | gallons | Manhole along Big Duck Creek. It is the 2nd manhole along the creek West of 19th street. Big Duck Creek | Untreated Release This was a blocked line between two manholes along Big Duck Creek. | At 1:00pm John Sexton notified Terry Morris about a manhole along Bid Duck Creek that was overflowing. John was notified by a malignance worker for Elwood Community Schools. The collection system crew Terry Morris (CSO Operator) and myself went to the manhole. The lift station was fine and we found a manhole overflowing (trickling out). The next manhole downstream was low John vacuumed the line tried to shoot the line. He then ran his cutter in the line and opened the line up which stopped the overflow. They also vacuumed another load out of the line to relieve any pressure on that line. We will start pulling the manholes along the section of Big Duck Creek for awhile to investigate whether this was a one time event or if it is a trouble area that needs more attention. | SSO Reached Receiving Water | Big Duck Creek
40186 | 36035 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-04-17 07:00 |  | 2013-04-17 14:46 | 250 | gallons/day | Manhole along Big Duck Creek. It is the second manhole along the creek west of 19th Street. | Precipitation event(s) caused high creek levels and full sewer lines from I & I. Result is untreated release into receiving waters. | Installed a sump pump in the G Street Lift Station In an attempt to relieve this line. The lift station is pumping at capacity.We will continue to monitor this line daily for data. Once the levels of Big Duck Creek go down and the ground dries a little (there is not access road) we can get our Vac truck out to inspect this line. The City of Elwood is purchasing a camera truck. It is our intent to video inspect the collection system to find and diagnose trouble areas. | SSO Reached Receiving Water | Big Duck Creek
40186 | 36671 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-04-24 08:00 | 2013-04-25 16:30 | 2013-04-26 12:34 | 5850 | gallons | Junction box along Big Duck Creek. It is the second manhole along the creek. West of 19th Street. | Precipitation event(s) caused an untreated release from Junction Box in manhole to receiving waters. | This is a problem area the city is addressing. The precipitation the city has received has contributed to this being labeled as ongoing . There is no access road and the grounds wer saturated preventing access to this location. The collection system crew used their back truck and ran a cutter up this line and opened it.We are checking this line every day to make sure it doesn t continue to clog. The city is in the process of purchasing a camera truck and it the intent to camera these types of problem areas to properly address these areas. | SSO Reached Receiving Water | Big Duck Creek
40186 | 36249 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-04-24 08:00 |  | 2013-04-24 02:57 | 3 | gallons | Junction box along Big Duck Creek. It is the second manhole along the creek. West 0f 19 St. Big Duck Creek | Untreated Release Rain 1.47 inches. Elwood received 1.47 of rain on top of almost 5 from the 18th and 19th of April. This is running full and going into Big Duck Creek. I was notified at 3:00pm by our staff who was putting in a new G Street Pump. The sewers are running full from the previous rains and this one contributed and made this overflow. | W have installed a new G Street Pump. We are currently running a 3 trash pump along with this new pump to alleviate some of the system. We will inspect this line when we can get our Vac Truck along the creek without getting stuck. | SSO Reached Receiving Water | Big Duck Creek
40186 | 36845 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-05-11 08:10 | 2013-05-11 09:20 | 2013-05-12 11:30 | 28014 | gallons | P Street Lift Station | Power Failure Pump Station Failure AEP power company had scheduled power outages for maintenance. I was notified that it would be on May 4th by a third party. The power outage happened on May 11th 2013. This power outage caused the breakers to both P Street lift station pumps to kick out. The operator on duty was checking lift stations and noticed the problem. The power outage was about 10-15 minutes. | I called in Terry Morris (our CSO/Lift Station employee). He reset the breakers to the pumps and the overflow stopped. I was contacted about the power outage by our weekend employee JOHN Mort. I walked him through the power outage at the plant an told him to be on the lookout when he checked lift stations for any problems. | SSO Reached Receiving Water | Little Duck Creek
40186 | 36797 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-05-11 08:10 | 2013-05-11 09:20 | 2013-05-12 12:19 | 28014 | gallons | P Street Lift Station | Power Failure Pump Station Failure AEP power company had scheduled power outages for maintenance. I was notified that it would be on May 4th by a third party. The power outage happened on may 11 2013. This power outage caused the breakers to both P Street Lift Station pumps to kick out. The operator on duty was checking lift stations and noticed the problem. The power outage was about 10-15 minutes. | Repaired Pump Station. I called in Terry Morris (our CSO Lift Station employee). He reset the breakers to the pumps and the overflow stopped. I was contracted about the power outage by out weekend employee Josh Mort. I walked him through the power at the plant an told him to be on the lookout when he checked lift stations for any problems. I will contact AEP on 5-13-13 and implement a plan to be notified personally when a scheduled power outage occurs. I will also discuss on finding out what power grid each lift station is on and dispatch employees immediately to those lift stations that are involved within the power outage for that grid. It has been our experience that power outages normally do not kick the circuit breaker out. | SSO Reached Receiving Water
40186 | 38394 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-06-12 23:59 |  | 2013-03-13 01:34 | 0 |  | 1107 South B Street Ground | We had 2.19 inches of rain fall starting on June 12 2013 @ 11:20am June 13 2013. The rain started again @ 5:45am on June 13 2013 giving us a total of 2.19 inches of rain. Doug Gripp who oversees our CSO monitoring equipment said the rain intensity number was 1.130/inches per hour. The owner contacted the City utility office. Glenn Murray City Utility Superintendant notified me @ 6:20am. I went out to the address and the collection system crew were about to clean up the debris that had come out. There was not much debris but the cleaned up the spill. The sewer lines are running full. The WWTP raw flow is about 12MGD. All four raw pumps are pumping at maximum capacity. The estimate of flow released was based on visual and picture data. This line is one of the lowest points. When we get massive amounts of rain I short periods of time this line fills up. | We took before and after pictures. The mess was cleaned up. The City of Elwood just recently purchases a camera truck it is the intent of the city to comers trouble spot. It will be recommended to that we camera this line to see if there is a problem. Again this line is at the lowest point and I would seem that the heavy sudden rain s causes the collection system to run full and discharge from this manhole.
40186 | 38392 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-06-13 | 2013-06-13 13:00 | 2013-06-13 01:33 | 0 |  | 29th and South L Manhole Ground | Rain 2.19 inches We had 2.19 of ran fall starting o June 12 2013 @ 11:20am until 2:00am June 13th 2013. The rain stated again @ 5:45 am on June 13 2013 giving us a total 2.19 of rain. Doug Gripp who oversees our CSO monitoring equipment said the rain intensity number was 1.130/inches per hour. This manhole was spotted by the City Ellwood s Street Commissioner. The WWTP raw flow is about 12MGD. All four raw pumps are pumping at maximum capacity. The sewers are running full. We monitored this all day and end the water was trickling out until it stopped. | There was no noticeable debris. We checked an the area looks clean from debris. The City of Elwood just recently purchased a camera truck. It is the intent of the city to camera troubles pots. It will be recommended that we camera this line and investigate for problems. Again the heavy sudden rains seemed to cause the collection system to run full and discharge out of the manhole. | SSO Occurred at Treatment Plant
40186 | 40837 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-10-08 06:20 | 2013-10-06 16:20 | 2013-10-07 15:06 | 0 |  | P Street Lift Station | Rain 1.04 inches Equipment Failure Normal operation of the lift station consist of two pumps in service and one backup up on 7/8/2013 the east pump malfunction. We replaced that with our back up and sent the broken pump out for quote for a rebuild. On 9/16/2013 the west pump motor burned up leaving us with only one pump. We called in BBC and Covelen to review lift station records and to make any suggestions. In the mean time we were getting new pump quotes and rebuild quotes. On 10/2/2013 the Board of Works approved an new pump and a rebuild pump for this lift station. | See Report | SSO Reached Receiving Water | Little Duck Creek
40186 | 42108 | IN0032719 | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-11-22 09:45 | 2013-11-22 09:45 | 2013-11-22 14:06 | 0 |  | CSO #16 | Rain 1.49 inches On 11/17/2013 precipitation for the day was 1.1 . The POTW has experienced higher influent flows since this rain event. On 11/21/2013 it rained 39 with an additional 12 between 12:00am to 7:15am on Friday 11.22/2013. the collection system is running full and it seems some of the CSO s on the verge of overflowing. At 8:45am I noticed CSO 16 discharging. There were no other CSO discharging except for a small spike in CSO 5. Fridays are the days the City of Elwood Water Department backwash their filters. This backwash wales is on the same line as CSO 16 | See Report | SSO Reached Receiving Water | Big Duck Creek
40186 | 36477 | IN0032719 To the best of my knowledge no damage is being done to the aquatic life or receiving stream. | ELWOOD SEWAGE TREATMENT PLANT | Madison | 2013-04-18 |  | 2013-04-19 05:15 | 0 |  | Numerous manholes catch basins CSO s and Big Duck Creek out of it s banks. Big Duck Creek | Untreated Release Rain 4.60 inches Elwood Indiana received 4.60 inches of rain from 12:00am (4/18/13) to 3:55am (4/19/13).This amount of rain caused Big Duck to flood out of it s banks. This amount of rain also caused the collection system to run full. Elwood was still trying to catch up from the last rain event on 4/10/13 and 4/11/13. The City is in a State of Emergency massive flooding on the Northeast side of town G Street lift station is underwater. The WWTP Raw Influent is 12.4MGD. I notified the Emergency Response Spill line @ 5:15am. I also contacted our state inspector (Becky Ruark) at 7:48am and 11:50am. I called the OWQ at 12:15am. | As soon as the levels recede we can start to look at G Street Lift Station and assess the situation in more detail. | SSO Reached Receiving Water | Big Duck Creek
41104 | 35800 | IN0041572 | Anderson Water Utility Site 2 | Madison | 2013-01-16 13:33 |  | 2013-01-17 16:36 | 0 |  | Raw Finished Water Line | A failed coupling on a 24 inch Raw Line resulted in release of Raw and city water to receiving waters. | Contractors hired to effect repairs | SSO Reached Receiving Water | White River
40085 | 35955 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-01-13 10:06 |  | 2013-01-13 12:17 | 0 |  | Pendleton Main Lift Station | Precipitation event exceeded capacity of lift station resulting in untreated release to receiving waters. | Ongoing project of improving main lines in Pendleton. | SSO Reached Receiving Water | Fall Creek
40085 | 36241 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-04-19 07:00 | 2013-04-20 20:30 | 2013-04-19 07:58 | 0 |  | P-Main Lift Station | Precipitation event exceed the capacity of lift station resulting in untreated release from the lift station to receiving waters | Wait til things slow down. Still replacing main line in Pendleton. | SSO Reached Receiving Water | Fall Creek
40085 | 36240 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-04-19 07:15 | 2013-04-19 12:02 | 2013-04-19 07:58 | 0 |  | CR ?00 Lift Station | Precipitation event exceeded capacity of lift station resulting in untreated release to receiving waters. | Wait til things slow down. Look for people removing clean out caps to drain their yard. | SSO Reached Receiving Water | Fall Creek
40085 | 38871 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-05-07 13:39 | 2013-05-07 13:48 | 2013-05-07 14:05 | 0 |  | F.M at Hardees L/S Small Ditch | Directional Borc-unit hit our F.M at the Hardees L/S |  | SSO Reached Receiving Water
40085 | 38870 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-05-14 14:42 | 2013-05-15 10:30 | 2013-06-12 10:30 | 0 |  | 5961 S Reformatory Rd Farm Field | Home owner 1 1/4 F.M. lateral leaking at the main. Ticket 1305143218 | Dug up and repaired leak. | SSO Affected Private Property
40085 | 37638 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-05-14 14:42 | 2013-05-15 10:30 | 2013-06-12 09:59 | 0 |  | 5961 S Reformatory RA Farm Field. | Untreated Release Equipment Failure. Home owner 11/4 F.M. Lateral leaking at the main. 811 Ticket #1305143218. Dug up and repaired leak. | Dug up and repaired leak. | SSO Affected Private Property
40085 | 38735 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-06-10 14:30 | 2013-06-10 14:45 | 2013-06-10 16:30 | 50 | gallons | North sludge holding tank. | Equipment failure Exceeded Max Capacity Sludge Holding Tank The RDP Biosolids Processing equipment has been down for repairs. The brushes to the heating elements failed when we started the equipment on 6/3/13. We had previously completed and extended run on 5/24/13. The sludge in the sludge holding tanks is old and we have struggled to supermate effectively recently. There is foam on the sludge holding tanks due to the sludge being old today at 2:30pm some of the foam overflowed the north sludge holding tank. We cleaned the foam up with water spray and are currently operating the RDP system. | Cleaned up the foam with water spray and hosed down the sides and top edge of the north tank. We are running the RDP system to reduce the level of sludge in the sludge holding tanks. The plan is to run the RDP system for the next 2 to 3 weeks to reduce the sludge in the sludge holding tanks and reduce the foaming issue.
40085 | 37554 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-06-10 14:30 | 2013-06-10 14:45 | 2013-06-10 16:30 | 50 | gallons | North Sludge Holding Tank | Equipment Failure Exceed Max Capacity The RDP Biosolids Processing equipment has been down for repairs. The brushes to the heating elements failed when we started the equipment on 6/3/13. We had previously completed an extended run on 524/13. The sludge in the sludge holding tanks is old and we have struggled to supermate effectively recently. there is foam on the sludge holding tanks due to the sludge being old. Today at 2:30pm some of the foam overflowed the north sludge holding tank. We cleaned the foam up with water spray and are currently operating the RDP system. | Cleaned up the foam with water spray and hosed down the sides and top edge of the north tank. We are running the RDP system to reduce the level of sludge in the sludge holding tanks. The plan is to run the RDP system for the next 2 to 3 weeks to reduce the sludge in the sludge holding tanks and reduce the foaming issue. | SSO Occurred at Treatment Plant
40085 | 38736 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-06-12 09:00 | 2013-06-12 09:55 | 2013-06-12 09:55 | 0 |  | CR 100 L/S Fall Creek/ Golf Course | Power Failure Lost a phase to our lift station. | Portable generator was installed. | SSO Affected Private Property
40085 | 37635 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-06-12 09:00 | 2013-06-12 09:55 | 2013-06-12 09:32 | 0 |  | CR 100 L/S Fall Creek/Golf Course. | Untreated Release Power Failure. | Duke Energy lost a phase to our Lift Station. Portable generator was installed. | SSO Affected Private Property; SSO Reached Receiving Water | Fall Creek
40085 | 39172 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-09-27 15:40 | 2013-09-27 19:30 | 2013-09-02 15:50 | 0 |  | FM at US36 & CR 300W | Construction Related FM was hit by a directional bore unit. Borning for GLGC line. | Repaired Pipe See Report | SSO Affected Private Property
40085 | 41626 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-09-27 15:40 |  | 2013-09-27 15:50 | 0 |  | FM @ US36 & CR 300W | Construction Related FM was hit by a directional bore unit running from GLEC line | Repaired Pipe | SSO Affected Private Property
40085 | 41057 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-10-04 15:30 | 2013-10-04 15:40 | 2013-10-07 23:00 | 0 |  | Force main @ 6395 Fox Run | Construction Relate Backhoe hit main FM installing a pool line. | Repaired Pipe See Report | SSO Affected Private Property
40085 | 43330 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-12-21 14:00 |  | 2013-12-21 14:40 | 1000 | gallons | CR 100 Lift Station Farm Field | Rain 1 inch plus snow | See Report | SSO Reached Public Land; SSO Affected Private Property
40085 | 43352 | IN0049026 | FALL CREEK WASTE WATER TREATMENT PLANT | Madison | 2013-12-22 12:30 |  | 2013-12-22 15:53 | 0 |  | See Report | Rain water level is above manhole. | See Report | SSO Reached Receiving Water | Fall Creek
40082 | 36613 | IN0061344 | Alexandria Municipal Waste Water Treatment Plant | Madison | 2013-04-22 | 2013-04-22 12:00 | 2013-04-22 11:33 | 0 |  | WWTP | Drained and cleaned No 1 clarifier scrapper arm working. Sludge completed No 1 clarifier back online.
42709 | 41129 | N0032476 | Anderson Municipal Sewage Treatment Plant | Madison | 2013-10-19 13:00 | 2013-10-22 13:00 | 2013-10-21 08:58 | 0 |  | Biosolids Section | Equipment Failure Cement Tech cake mixer not working. Broken hydraulic line. Final effluent will not be affected. | We are not operating the equipment until repairs are complete. Continuing preventive maintenance. | SSO Occurred at Treatment Plant
20517 | 35921 |  | LAWRENCE STREET & WATER DEPARTMENT | Marion | 2013-01-13 01:00 | 2013-10-13 15:00 | 2013-01-13 18:09 | 12000 | gallons | Manhole in middle of road at 4602 North Post Road | Precipitation event resulted in an untreated non permitted release from manhole to the street. | Barricade the area. We have begun a program of yearly capital improvement projects designed to eliminate SSO. | SSO Reached Public Land; Paved Surface
12903 | 35954 |  | LAWRENCE UTILITIES | Marion | 2013-01-13 01:00 | 2013-01-13 11:00 | 2013-01-13 13:02 | 15000 | gallons | 8943 East 46th Street | Precipitation event triggered untreated release from manhole to road. | Baricaded area. We have begun a program of yearly capital improvement projects designed to eliminate SSO. | SSO Reached Public Land; Paved Surface
20517 | 35923 |  | LAWRENCE STREET & WATER DEPARTMENT | Marion | 2013-01-13 01:00 | 2013-01-13 11:00 | 2013-01-13 13:02 | 30000 | gallons | 7103 Oaklandon | Precipitation event triggered an untreated non permitted release to receiving water. | Sand bag and rake area spread lime.We have begun a program of yearly capital improvement projects designed to eliminate SSO. | SSO Reached Public Land | North Branch
12903 | 35985 |  | LAWRENCE UTILITIES | Marion | 2013-04-16 |  | 2013-04-17 10:52 | 500 | gallons | Residential basement | Precipitation event triggered high levels in lines and an untreated release into a residential basement. | Explained situation to customer and advised that he will see relief as soon as mains downstream return to normal flow. Explained what city is doing by way of capital projects to address old sewer issues in this part of town where sewers are 60+ years old. Advised that he may want to consult plumber regarding instllation of sewer lateral check valve but that check valve would onlywork if properly maintained and that if mains are backed up and valve is closed he cannot use internal plumbing as it will not drain out. | SSO Basement Backup
12903 | 35982 |  | LAWRENCE UTILITIES | Marion | 2013-04-16 18:30 | 2013-04-17 10:30 | 2013-04-17 13:29 | 28800 | gallons | 46th and Post Road | Precipitation event caused untreated release from manhole to storm sewer. | Baricades placed at overflow location. City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSO. | SSO Reached Public Land
12903 | 35983 |  | LAWRENCE UTILITIES | Marion | 2013-04-17 09:00 | 2013-04-17 10:15 | 2013-04-17 13:29 | 75 | gallons | 5013 Ekitley Avenue | Precipitation event triggered an untreated non permitted release from a manhole to storm sewer. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSO.
12903 | 35984 |  | LAWRENCE UTILITIES | Marion | 2013-04-17 10:00 | 2013-04-17 10:30 | 2013-04-17 13:29 | 300 | gallons | 45th and Clinton Avenue | Precipitation event and backed up lines necessitated shutting down a pump at a lift station to stop SSO from manhole. | Shut down 1 pump at Lift Station 14. City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSO.
12903 | 36318 |  | LAWRENCE UTILITIES | Marion | 2013-04-19 07:00 | 2013-04-19 10:22 | 2013-04-22 07:28 | 3030 | gallons | 5013 Kitley Avenue ( 2 Manholes) | Precipitation event resulted in non permitted untreated release from sanitary manhole to storm sewer. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSOs. | SSO Reached Public Land; Storm Sewer
12903 | 36177 |  | LAWRENCE UTILITIES | Marion | 2013-04-19 07:00 |  | 2013-04-19 09:41 | 0 |  | 5013 Kitley Avenue | Precipitation event triggered untreated unpermitted discharge from 2 manholes to storm sewer. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSOs. Combined flow from both manholes estimated at 30 gpm. | SSO Reached Public Land
12903 | 36175 |  | LAWRENCE UTILITIES | Marion | 2013-04-19 07:10 |  | 2013-04-19 09:41 | 0 |  | 46th and Post Road | Precipitation event triggered untreated release from 3 manholes to storm sewers. | City of Lawrence Utilities is in the process of completinga SSES to determine the best solution to prevent any future SSOs. Combined overflow from manholes was estimated at 30 gpm. | SSO Reached Public Land; Storm Sewer
12903 | 36320 |  | LAWRENCE UTILITIES | Marion | 2013-04-19 07:10 | 2013-04-20 15:00 | 2013-04-22 07:28 | 56100 | gallons | 46th and Post Road - (3 manholes) | Precipitation event triggered non permitted untreated release from 3 manholes to the storm sewer system. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSOs. | SSO Reached Public Land; Storm Sewer
12903 | 36174 |  | LAWRENCE UTILITIES | Marion | 2013-04-19 08:05 |  | 2013-04-19 09:41 | 0 |  | 7103 Oaklandon Road | Precipitation event triggered an untreated release from manhole to receiving waters. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSOs. | SSO Reached Receiving Water | North Branch
12903 | 36321 |  | LAWRENCE UTILITIES | Marion | 2013-04-19 08:05 | 2013-04-22 14:30 | 2013-04-22 07:29 | 88750 | gallons | 7103 Oaklandon Road | Precipitation event triggered a non permitted and untreated release from manhole to receiving waters. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent any future SSOs. | SSO Reached Receiving Water | North Branch
12903 | 36164 |  | LAWRENCE UTILITIES | Marion | 2013-04-24 10:44 |  | 2013-04-24 12:36 | 50000000 | gallons | 7103 Oaklandon Rd North Branch Ditch | Untreated Release Rain 1.64 rain | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent future SSOs | SSO Reached Receiving Water
| 36304 |  | All Star Carpet Care | Marion | 2013-05-01 |  | 2013-05-01 15:50 | 0 |  | Northeast side of Indianapolis Windsong is bounded by: 86th St on the north Fox Rd on the south Geist Reservoir on the west Oaklandon Rd on the east.All Star Carpet Guy lives on the east side of Rodondo Drive | Sherry Boyle President of the Windsong Lake Homeowner¿s Board called and states a person in a van from All Star Carpet Care who lives on the east side of Rodondo Drive in the Windsong Lake Addition is dumping water containing she knows not what into the neighborhood sewer drain. She has called All Star Carpet Care to let them know this practice is wrong but she wants them to know why it is wrong and is concerned about the fish in Windsong Lake which runs into Geist Reservoir. She called the Mayor s Action Line and they gave her IDEM s number. | Andy sent this to the City of Indy.
12903 | 41929 |  | LAWRENCE UTILITIES | Marion | 2013-11-16 11:00 | 2013-11-17 06:00 | 2013-11-18 09:14 | 0 |  | 46th & Post Rd (3 manholes @ intersect) | Rain 2.5 inches | See Report | SSO Affected Private Property
12903 | 41927 |  | LAWRENCE UTILITIES | Marion | 2013-11-17 07:00 | 2013-11-16 06:00 | 2013-11-18 09:02 | 0 |  | 5013 Kitley Ave ( 2 manholes) | rain 2.5 inches | See Attachment | SSO Affected Private Property
17464 | 43445 | IN0021300 Outfall 002 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-12-21 10:00 |  | 2013-12-21 11:30 | 5 | gallons | W73 | Exceeded Max Capacity Heavy rain and combo of snow melting | See Report | SSO Reached Receiving Water | Buck Creek
17464 | 35953 | IN0021300 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-01-11 17:00 | 2013-01-11 20:00 | 2013-01-12 20:15 | 50 | gallons | Manhole # E-30 | Line blockage triggered untreateated release from manhole to surrounding ground and storm sewer | Cleared blockage and cleaned area with water. | SSO Reached Public Land; Storm Sewer
17464 | 35242 | IN0021300 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-01-13 11:30 |  | 2013-01-14 10:02 | 10000 | gallons | Manhole w-73 Cumberland IN | Precipitation event resulted in collection system overflow with an untreated release to paved surface and ditch | Placed SBR in storm mode | SSO Reached Public Land
17464 | 36242 | IN0021300 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-04-17 06:33 | 2013-04-17 14:30 | 2013-04-19 08:52 | 48000 | gallons | Manhole w-73 | Precipitation event caused manhole overflow to surrounding ground and unnamed stream. | SBR in storm mode. | SSO Reached Public Land; SSO Reached Receiving Water
17464 | 36028 | IN0021300 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-04-17 06:33 | 2013-04-17 | 2013-04-17 07:54 | 0 |  | Manhole W-73 | Untreated Release | Heavy rain caused collection system overflow SBR in storm mode. | SSO Reached Receiving Water
17464 | 36246 | IN0021300 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-04-19 08:00 |  | 2013-04-19 09:00 | 0 |  | Manhole w-73Manhole BC-1 | Precipitation event caused collection system overflow of untreated release from manholes to unnamed receiving waters. | SBR in Storm Mode | SSO Reached Public Land; SSO Reached Receiving Water
17464 | 36030 | IN0021300 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-04-19 08:00 | 2013-04-19 14:30 | 2013-04-22 16:46 | 0 |  | Manhole W73 manhole BC 1 Ground Stream | Heavy rain caused collection system overflow. | SBR in storm mode Updated Form | SSO Affected Private Property; SSO Reached Receiving Water
17464 | 43442 | IN0021300 Outfall 002 | CUMBERLAND SEWAGE UTILITY | Marion | 2013-12-21 10:00 | 2013-12-22 16:00 | 2013-12-21 11:30 | 1250000 | gallons | W73 | Exceeded Max Capacity Heavy rain and combo of snow melting. River covered at least 2 manholes. | See Report | SSO Reached Receiving Water | Buck Creek
10868 | 35618 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-02 14:12 | 2013-01-02 15:30 | 2013-01-04 07:39 | 76 | gallons | 3215 North Alton Avenue | Pipe collapse. Untreated release to ground. | Excavated and repaired sewer. Cleaned sewer blockage. Removed debris. | SSO Affected Private Property
10868 | 35587 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-04 21:55 | 2013-01-05 00:45 | 2013-01-09 07:00 | 1661 | gallons | 2376 East 54th Street | Sewer blockage caused an untreated release from manhole. Blockage was grease and debris. | Removed debris cleaned sewer blockage. | SSO Reached Public Land
10868 | 35852 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-11 10:00 | 2013-01-11 11:19 | 2013-01-15 07:11 | 3859 | gallons | 499 Big Hill Circle | Grease obstruction in sewer resulted in untreated release to receiving waters | Cleared sewer blockage flushed area. | SSO Reached Public Land; SSO Reached Receiving Water | Mill Run
10868 | 35899 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-12 18:50 | 2013-01-12 20:17 | 2013-01-18 09:35 | 50 | gallons | 8215 Beechwood Avenue | Precipitation event and blockage resulted in untreated release. Found lateral cap off at a later time. Originally came in as a back up. | Cleared sewer blockage cleaned up debris and flushed area. | SSO Affected Private Property
10868 | 35880 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-12 21:36 | 2013-01-13 01:30 | 2013-01-17 09:52 | 25 | gallons | 3827 St. Simons Court | Sewer blockage and lift station electrical problem resulted in an untreated release to a residence. | Cleared sewer blockage. Repaired lift station. | SSO Basement Backup
10868 | 35878 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 01:00 | 2013-01-13 07:40 | 2013-01-17 09:52 | 25 | gallons | 6530 Yellowstone Parkway | Lift station pump failure caused an untreated release into a residential building. | Repaired lift station pump. | SSO Basement Backup
10868 | 35901 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 03:31 |  | 2013-01-18 09:35 | 25 | gallons | 7917 Kimlough Drive | Precipitation event and sewer blockage caused residential backup. | Cleared sewer blockage. Wet weather I & I contribution. | SSO Basement Backup
10868 | 35911 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 09:30 | 2013-01-14 08:28 | 2013-01-18 09:35 | 1500 | gallons | 2725 Wicker Road | Precipitation event and wet weather I & I contribution resulted in excessive flows at Southport WWTP caused overflow from manhole on SW diversion sewer to surrounding ground. | Flush area. | SSO Occurred at Treatment Plant
10868 | 35915 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 09:31 |  | 2013-01-18 09:35 | 25 | gallons | 5520 South State Street | Precipitation event and wet weather I & I contribution resulted in untreated release to surrounding ground. |  | SSO Affected Private Property
10868 | 35914 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 09:31 |  | 2013-01-18 09:35 | 25 | gallons | 1615 East Epler Avenue | Precipitation event I 7 I wet weather contribution resulted in untreated release to surrounding ground. |  | SSO Affected Private Property
10868 | 35917 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 11:10 |  | 2013-01-18 09:35 | 250 | gallons | 3002 Arbor Street | Precipitation event and wet weather I & I contribution resulted in an untreated release to a ditch and receiving water. |  | SSO Reached Receiving Water | Lick Creek
10868 | 35906 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 13:12 | 2013-01-13 13:13 | 2013-01-18 09:35 | 49 | gallons | 6850 West 86th Street | Lift Station debris in pump pipe and valve along with precipitation event triggered and untreated release to surrounding ground and receiving waters. | Removed debris. | SSO Reached Receiving Water | Eagle Creek
10868 | 35910 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 17:45 |  | 2013-01-18 09:35 | 127479 | gallons | 6102 Boy Scout Road | Precipitation event adn I & I contribution resulted in untreated release to surrounding ground. | Removed debris. | SSO Reached Public Land; SSO Affected Private Property
10868 | 35909 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-13 17:56 |  | 2013-01-18 09:35 | 0 |  | 2263 Country Club Road | Precipitation event and I & I contribution resulted in an untreated release. |  | SSO Affected Private Property
10868 | 35919 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-14 02:35 |  | 2013-01-17 09:52 | 20 | gallons | 6844 Arjay Drive | lift station pump failure resulted in untreated release to surrounding ground. Associated with LS209. | Repair Lift Station | SSO Affected Private Property
10868 | 36678 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-14 03:07 | 2013-01-15 14:59 | 2013-04-26 16:49 | 10511 | gallons | 8623 East Washington Street | Private Line Problem. This is a private line and manhole CEG main that was down and flowing is where CEG responsibility starts. Untreated release to Paved area and street. | Cleared sewer blockage. | SSO Reached Public Land; SSO Affected Private Property; Paved Surface
10868 | 35853 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-14 10:00 |  | 2013-01-15 07:11 | 1000 | gallons | 3125 East Bradbury Avenue | Precipitation event and I & I contribution resulted in untreated release to storm structure and receiving waters. | flushed area removed debris | SSO Reached Public Land; SSO Reached Receiving Water | Bean Creek
10868 | 35879 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-14 13:21 |  | 2013-01-17 09:52 | 1000 | gallons | 2001 South Bridgeport Road | Precipitation event along with wet weather I & I (discovered after rain event) caused an untreated release to ground around manhole. | Remove debris flushed area | SSO Affected Private Property
10868 | 35913 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-16 10:30 |  | 2013-01-18 09:35 | 25 | gallons | 626 Front Royal Drive | Precipitation event i & I wet weather contribution resulted in untreated release to paved area/street. |  | SSO Reached Public Land; Paved Surface
10868 | 35916 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-16 14:35 |  | 2013-01-18 09:35 | 150 | gallons | 7851 Noel Road | Precipitation event and wet weather i & I contribution resulted in untreated release to surrounding ground. |  | SSO Affected Private Property
10868 | 35775 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-17 12:15 | 2013-01-17 14:15 | 2013-01-21 08:39 | 3517 | gallons | 5600 South Concord Street | Lift Station force main rupture resulted in untreated release to ground around lift station. | Excavated and repaired sewer. | SSO Reached Public Land
10868 | 35662 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-21 13:30 | 2013-01-21 15:50 | 2013-01-22 07:08 | 20 | gallons | 6844 Balmoral Road | Sewer blockage caused untreated release into residential basement. | Cleared sewer blockage release resolved. | SSO Basement Backup
10868 | 35655 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-24 11:30 | 2013-01-25 11:00 | 2013-01-28 07:17 | 34434 | gallons | 3700 South Harding Street | Lift Station Force Main Rupture resulted in an untreated release from the main to public and private land. | Excavated soil and repaired sewer. | SSO Reached Public Land; SSO Affected Private Property
10868 | 35126 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-25 13:49 | 2013-01-25 14:57 | 2013-01-28 07:17 | 20 | gallons | 2357 North Capitol Avenue Indianapolis IN | Sanitary sewer backup into residence | Cleared debris and blockage in sewer. | SSO Basement Backup; SSO Affected Private Property
10868 | 35027 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-28 09:55 |  | 2013-02-04 07:25 | 250 | gallons | 7611 Brookview Lane Indianapolis IN | Wet weather I/I contribution. Manhole overflowed during rain event on 1/12-13/2013. Per home owner. Start and stop times unknown. Light clean up needed. | Remove debris flush area | SSO Reached Receiving Water; Surface Soil | Dry Run
10868 | 35028 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-28 10:15 |  | 2013-02-04 07:25 | 150 | gallons | 3745 East 75th Street Indianapolis IN | Wet wather I/I contribution. Manhole overflowed during rain event on 1/12-13/2013. Unknown start and stop times. Light clean up needed. | Flush area Remove Debris | SSO Reached Receiving Water; Surface Soil | Dry Run
10868 | 35029 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-28 12:10 |  | 2013-02-04 07:25 | 50 | gallons | 1830 Winchester Drive Indianapolis IN | Wet weather I/I contribution. Unknown start and stop times from rain event on 1/12-13/2013. Follow up from event light clean up needed. | Remove debrisFlush area | SSO Reached Receiving Water; Surface Soil | Lick Creek
10868 | 35159 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-29 09:24 | 2013-01-29 11:00 | 2013-02-01 08:43 | 25 | gallons | 1151 West Thompson Road Indianapolis IN | Residential backup. | Cleaned sewer blockage and removed debris. TV sewer to make sure it is clear. | SSO Basement Backup
10868 | 35205 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-30 08:31 | 2013-01-30 09:15 | 2013-01-31 07:06 | 1075 | gallons | Lift Station at 8850 River Bend Parkway Indianapolis IN | Lift Station power failure resulted in Untreated Release | Lift Station Power Failure | SSO Reached Public Land; SSO Reached Receiving Water | Castle Creek
10868 | 35161 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-01-30 15:53 | 2013-01-30 20:23 | 2013-02-01 08:43 | 20 | gallons | 2319 South Keystone Avenue Indianapolis IN | Residential back up | Clean sewer blockage remove debris. TV and Clean | SSO Basement Backup
10868 | 35012 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-01 03:11 | 2013-02-01 04:18 | 2013-02-01 10:54 | 19635 | gallons | Lift Station at 8402 Woodburn Drive Indianapolis IN | Lift Station instrumentation failure resulting in Untreated Release. | Repaired instrumentation in lift station. | SSO Reached Receiving Water; Storm Sewer | Eagle Creek
10868 | 35026 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-01 11:00 |  | 2013-02-04 07:49 | 100 | gallons | 7107 Wiliams Creek Drive Indianapolis IN | Wet weather contribution. Unknown start ans stop times manhole probably overflowed during the rain event on 1/12-13/ 2013. Found during routine siphon inspections. | Remove Debris | SSO Reached Receiving Water; Surface Soil | White River
10868 | 35025 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-01 11:25 |  | 2013-02-04 07:49 | 100 | gallons | 6850 West 86th Street Indianapolis IN | Rain event on 1/12-13/2013 appears to have triggered an overflow at 6850 W. 86th St. | Removed debris | SSO Reached Receiving Water; Surface Soil | Eagle Creek
10868 | 35024 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-01 11:35 |  | 2013-02-01 14:22 | 100 | gallons | 4001 Beauport Road Indianapolis IN | Estimate100 gallon untreated release overflow. Unknown start and stop times. Rain event contributor to event. | Cleared debris to alleviate overflow that appears to have occurred during rain event on 1/12/2013-1/13/2013 | SSO Reached Receiving Water; Surface Soil | Falcon Creek
10868 | 35084 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-02 16:00 | 2013-02-02 17:41 | 2013-02-06 | 23000 | gallons | 3800 Wewt Southport Road Indianapolis IN | Primary clarifier #2. Drain plug installed to stop a leak dislodged and allowed Clarifier contents to discharge to the plant drain and through a manhole to the plant grounds. | Spil contained on site. No release to waters of the state. Contained in ditch/moat around the plant. Water vactored up and returned to the head of the plant for treatment. The clarifier tank has been removed from service and the faulty gate valve will be replaced by 2/8/13 and the tank placed back in service. | SSO Occurred at Treatment Plant
10868 | 34898 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-06 10:05 | 2013-02-06 11:05 | 2013-02-06 10:59 | 117 | gallons | 905 East Edgewood Avenue Indianapolis IN | Private boring contractor (TSW) for CEG hit the sewer and will make repairs. 117 gallon Untreated Release | EXCAVATE & REPAIR SEWER. RELEASE CONTAINED WITHIN EXCAVATION | SSO Reached Public Land; Subsurface Soil (> 6 inches deep)
10868 | 34347 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-06 10:05 | 2013-02-06 11:05 | 2013-02-06 10:59 | 117 | gallons | 905 East Edgewood Avenue | Untreated Release - Private contractor damage - hit sewer and will make repairs | This was a boring contractor (TSW) for CEG hit the sewer line and will make repairs. Excavate and repair sewer line. | SSO Affected Private Property
10868 | 34968 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-09 06:00 | 2013-02-09 14:43 | 2013-02-09 09:08 | 12772 | gallons | 5700 S. Concord St. Indianapolis IN | Lift station force main rupture. Sludge Line Southport to Belmont | Excavate and Repair sewer | SSO Reached Public Land; Subsurface Soil (> 6 inches deep) | Hare Ditch
10868 | 34904 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-12 18:35 | 2013-02-12 21:20 | 2013-02-12 19:04 | 484 | gallons | Basement at 86 Beachway Drive Indianapolis IN | Basement backup 86 Beachway Drive found Indianapolis IN Found sewer blocked by grease and debris | Cleaned sewer removing grease and debris causing backup. Plan to TV and clean. | SSO Basement Backup
10868 | 34922 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-14 11:23 | 2013-02-14 12:00 | 2013-02-14 12:24 | 36 | gallons | Release occurred at Lift Station located at 5807 Sunset Lane Indianapolis IN | Lift Station Air Relief Valve failed causing an untreated release at 5807 Sunset Lane | Air Relief Valve is isolated Lift station will replace. Release was contained on srface of ground. Area was flushed. | SSO Affected Private Property
10868 | 34787 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-23 12:50 | 2013-02-23 15:51 | 2013-02-23 14:03 | 20 | gallons | Customer Building at 8050 Murphy Court | uNTYREATED RELEASE INTO CUSTOMER HOME/BLDG. | Cleaned debris causing sewer blockage. Clean and T.V. | SSO Basement Backup
10868 | 34786 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-02-25 22:30 | 2013-02-26 12:14 | 2013-02-25 22:44 | 3981 | gallons | 8350 Chessie Drive | Untreated Release due to sewer blockage by roots. | Clean sewer blockage an flush area. T.V. and clean | SSO Reached Public Land; Paved Surface
10868 | 36677 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-03-04 18:00 | 2013-03-04 19:11 | 2013-04-26 15:49 | 25 | gallons | 5425 south Missouri Street | Main sewer blocked with debris causing residential backup of untreated release. | Cleared sewer blockage. | SSO Basement Backup
10868 | 34591 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-03-04 18:00 | 2013-03-04 19:11 | 2013-03-04 19:39 | 25 | gallons | 5425 S Missouri St Asset ID 511177511176 | Untreated Release Debris | Clean Sewer Blockage TV & Clean | SSO Affected Private Property
10868 | 36679 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-03-14 10:10 | 2013-03-14 15:30 | 2013-04-26 16:42 | 10 | gallons | 8620 Green Braes North Drive | Lift Station force main rupture resulted in an untreated release to surrounding ground. | Excavate and repair sewer. | SSO Reached Public Land
10868 | 35129 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-03-14 10:10 | 2013-03-14 15:30 | 2013-03-20 18:13 | 10 | gallons | 8620 Green Braes NDR Asset ID# 821602 821598 | Equipment Failure LS force main ruptured | Excavate & Repair Sewer | SSO Affected Private Property
10868 | 34976 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-03-14 10:10 | 2013-03-14 15:30 | 2013-03-20 07:16 | 10 | gallons | 8620 Green Braes N DR Asset 821602821598 Lot/yard/field spill contained | Untreated Release Equipment Failure. LS Force Main Rapture | Excavate & Repair Sewer | SSO Affected Private Property
10868 | 35436 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-03-20 14:17 | 2013-03-20 20:30 | 2013-03-22 07:10 | 25 | gallons | 12131 Admirals Pointe Circle | Private contractor caused damage to lift station resulting in Untreated Release to private property and receiving waters. | Flushed Area Used pump truck to hold down flow. Performed repairs to lift station. | SSO Affected Private Property; SSO Reached Receiving Water | Geist Reservoir
10868 | 36680 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-03-31 02:29 | 2013-03-31 05:19 | 2013-04-26 16:42 | 830 | gallons | 1934 Schwier Court | Grease obstruction caused an untreated release to storm structur and receiving water. | Clean sewer blockage and TV. | SSO Reached Public Land; SSO Reached Receiving Water; Storm Sewer | Straw Branch
10868 | 37301 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-04 22:21 | 2013-04-15 01:33 | 2013-04-14 22:44 | 938 | gallons | 8075 Lower Bay Ln Asset 490973 Paved Area/Street Gist Reservoir | Untreated Release Roots and Grease Overflow clean up complete 4/15 @ 9:13 | Clean sewer blockage flush area. Clean and TV | SSO Affected Private Property; SSO Reached Receiving Water | Geist Reservoir
10868 | 37240 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-05 19:57 | 2013-04-05 22:11 | 2013-05-28 13:36 | 654 | gallons | 7951 Susan Dr S #130549 Paved Area/Street Spill Contained | Untreated Release Debris | Remove debris flush area clean sewer blockage. TV and Clean | SSO Affected Private Property
10868 | 37297 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-07 18:47 | 2013-04-07 20:30 | 2013-04-07 19:04 | 10062 | gallons | 5616 Millhouse Rd Asset # 740160 Ditch Millhouse | Untreated Release Debris | Clean sewer blockage remove debris flush area. Clean and TV | SSO Affected Private Property
10868 | 37311 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-16 20:43 | 2013-04-16 21:59 | 2013-04-16 20:40 | 25 | gallons | 60 Coronado Rd Asset# 750610 Customer Home/Bldg Basement/Bldg. | Untreated Release Rain 1.44 inches Wet Weather I/I contribution surcharge sanitary main. |  | SSO Basement Backup; SSO Affected Private Property
10868 | 37314 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-17 09:35 | 2013-04-17 13:00 | 2013-04-17 14:20 | 2003 | gallons | 4611 Berkshire Ln Asset# 171542 Ditch Devon Creek | Untreated Release Rain 1/38 inches. Wet weather I/I contribution. | Remove debris flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Devon Creek
10868 | 37325 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 06:15 | 2013-04-23 08:44 | 2013-04-19 09:22 | 577222 | gallons | 9737 Fall Creek Rd Assert# 491018 Lot/Yard/Field Fall Creek | Untreated Release Rain 1.89 inches. Wet weather I/I contribution. Unknown start and stop times. Stop time is clean-up time. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Fall Creek
10868 | 37324 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 07:15 | 2013-04-22 08:34 | 2013-04-19 08:07 | 429717 | gallons | 3041 E Bradbury Ave Asset# 635004 Storm structure Bean Creek | Untreated Release Rain 1.26 inches. Wet weather I/I contribution rain event. Date and time of overflow stop is date and time of clean up. | Flush area. | SSO Reached Receiving Water; Storm Sewer | Bean Creek
10868 | 37312 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 07:50 |  | 2013-04-19 08:09 | 25 | gallons | 8085 S Meridian St Asset 510533 Paved Area/Street Buffalo Creek | Untreated Release Rain 1.73 inches. Wet weather I/I contribution. Unknown start and stop times found after rain event. Not overflowing at time of inspection. Light clean up needed. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Buffalo Creek
10868 | 37338 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 10:20 | 2013-04-23 14:47 | 2013-04-19 11:57 | 29437 | gallons | 2236 Country Club Rd Asset# 750123 Ditch Eagle Creek | Untreated Release Rain 2.6 inches. Wet weather I/I contribution surcharged sanitary main. Date and time of overflow stop is clean-up time. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Eagle Creek
10868 | 37340 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 10:20 | 2013-04-23 14:47 | 2013-04-19 11:57 | 58875 | gallons | 2241 Country Club Rd Asset# 750124 Ditch Eagle Creek | Untreated Release Rain 2.6 inches Wet weather I/I contribution surcharged sanitary main. Date and time of overflow stop is overflow clean-up time. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Eagle Creek
10868 | 37339 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 10:20 | 2013-04-23 14:48 | 2013-04-19 11:57 | 147212 | gallons | 2263 Country Club Rd. Asset# 750125 Ditch Eagle Creek | Untreated Release Rain 2.6 inches Wet weather I/I contribution surcharged sanitary main. Date and time of overflow stop is overflow clean-up time. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Eagle Creek
10868 | 37337 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 10:34 | 2013-04-28 03:00 | 2013-04-19 10:59 | 2443302 | gallons | 7632 Noel Rd Asset# LS201 Ditch Eagle Creek | Untreated Release Rain 2.6 inches. Wet weather I/I contribution. Estimated overflow stop time is Sunday at 3:00am. This was the time that one of the two pumps were re-installed and put back into service. | Use pump TRK to hold down FL repair lift station. | SSO Affected Private Property; SSO Reached Receiving Water | Eagle Creek
10868 | 37343 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 11:18 | 2013-04-23 14:48 | 2013-04-19 13:46 | 5832 | gallons | 3154 N Lawndale Ave Asset# 811070 Paved area/Street/ Spill contained. | Untreated Release Rain 2.6 inches. Wet weather I/I contribution surcharged sanitary main. date and time of overflow stop is overflow clean-up time. | Wet weather I/I contribution surcharged sanitary main. Date and time of overflow stop is overflow clean-up time. | SSO Affected Private Property
10868 | 37353 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 11:18 | 2013-04-23 14:48 | 2013-04-19 13:46 | 29159 | gallons | 3202 N Lawndale Ave Asset# 811071 Paved Area/Street Spill Contained. | Untreated Release Rain 2.6 inches. Wet weather I/I contribution surcharged sanitary main. Date and time of overflow stop is overflow clean-up time. | Flush area. | SSO Affected Private Property
10868 | 37355 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 13:22 | 2013-04-19 17:00 | 2013-04-19 15:10 | 213 | gallons | 9202 E 21st St Asset# 560428 Customer Home/Bldg Spill Contained | Untreated Release Rain 2.84 inches. Wet weather I/I contribution surcharged sanitary main. |  | SSO Affected Private Property
10868 | 37341 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 13:45 | 2013-04-19 14:00 | 2013-04-19 14:21 | 73 | gallons | 6844 Arjay Dr Asset# 510210 Lot/Yard/Field Spill Contained. | Untreated release Rain 1.97 inches. LS Instrumentation failure approx time of overflow stop was 2:00pm. | Repair Lift station. Run lift station on hand. | SSO Affected Private Property; SSO Reached Receiving Water
10868 | 37354 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 13:45 | 2013-04-19 14:00 | 2013-04-19 14:06 | 73 | gallons | 6805 Arjay Dr Asset# 510211 Lot/Yard/Field Spill Contained. | Untreated Release Rain 1.97 inches. | Repair Lift Station Run Lift Station On Hand | SSO Affected Private Property
10868 | 37316 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 14:08 | 2013-04-19 17:00 | 2013-04-19 15:18 | 1680 | gallons | 7002 Grandview Dr Asset# 903182 Storm Structure Crooked Creek. | Untreated Release Rain 2.98 inches. | Flush Area | SSO Reached Receiving Water; Storm Sewer | Crooked Creek
10868 | 37317 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 14:17 |  | 2013-04-19 15:20 | 500 | gallons | 7041 Grandview Dr Asset 904416 Lot/Yard/Field/ Crooked Creek | Untreated Release Rain 2.98 inches. Wet weather I/I contribution unknown start and stop times not overflow at time of inspection. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Crooked Creek
10868 | 37320 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 14:31 |  | 2013-04-19 15:23 | 500 | gallons | 2851 W 76th St Asset# 904465 Lot/Yard/Field Crooked Creek. | Untreated Release Rain 2.98 inches. Wet weather I/I contribution unknown start and stop times not overflowing at times of inspection. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Crooked Creek
10868 | 37323 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 14:51 | 2013-04-23 14:44 | 2013-04-19 16:41 | 10 | gallons | 1232 W 73rd St Asset# 900199 Lot/Yard/Fieldspill contained | Untreated Release Rain 2.98 inches. Wet weather I/I contribution surcharged sanitary main. Stop time is overflow cleanup time. | Flush area | SSO Affected Private Property
10868 | 37322 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-19 14:51 |  | 2013-04-19 15:24 | 100 | gallons | 3160 W 79th St Asset# 909519 Lot/Yard/Field Crooked Creek. | Untreated Release Rain 2.98 inches. | Flush area. | SSO Affected Private Property; SSO Reached Receiving Water | Crooked Creek
10868 | 37356 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-24 07:10 | 2013-04-24 14:30 | 2013-04-24 08:44 | 64472 | gallons | 6850 W 86th St Asset# 906133 Lot/Yard/Field Retention Pond | Untreated Release LS Pump Failure | Repair Lift Station Remove Debris. | SSO Affected Private Property
10868 | 37357 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-24 10:35 | 2013-04-25 07:00 | 2013-04-24 11:03 | 71799 | gallons | 3125 E Bradbury Ave Asset# 635004 Ditch Bean Creek | Untreated Release WET WEATHERI/I CONTRIBUTION SANITARY SYSTEM IS SURCHARGED. Stop time is overflow clean-up time. | Flush Area. | SSO Affected Private Property; SSO Reached Receiving Water
10868 | 37358 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-24 12:54 | 2013-04-25 07:00 | 2013-04-24 14:14 | 10 | gallons | 7950 W 10th St Asset# 750729 Ditch East Fork White Lick Creek | Untreated Release 0.1 inches. WET WEATHER I/I CONTRIBUTION NO CLEAN UP NEEDED. |  | SSO Affected Private Property; SSO Reached Receiving Water | White Lick Creek
10868 | 37359 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-25 12:35 |  | 2013-04-25 12:42 | 500 | gallons | 4002 Beauport Rd Asset# 810209 Ditch Falcon Creek. | Untreated Release. WET WEATHER I/I CONTRIBUTION Unknown start and stop time. Overflow had stopped upon arrival. | CLEAN SEWER BLOCKAGE REMOVE DEBRIS FLUSH AREA. | SSO Affected Private Property; SSO Reached Receiving Water | Falcon Creek
10868 | 37360 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-30 10:40 |  | 2013-04-30 15:01 | 200 | gallons | 770 E 73rd St Asset# 180029 Lot/Yard/Field Spill Contained | Untreated Release 2.84 inches. WET WEATHER I/I CONTRIBUTION unknown start & stop time happened during the rain event on 4/19 not overflowing now. | Flush Area | SSO Affected Private Property
10868 | 37361 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-04-30 10:40 |  | 2013-04-30 15:22 | 400 | gallons | 7107 Williams Creek Dr Asset# 180025 Lot/Yard/Field Spill Contained. | Untreated Release Rain 2.84 inches. WET WEATHER I/I CONTRIBUTION unknown start & stop time happened during the rain event on 4/19 not overflowing now. | Flush Area. | SSO Affected Private Property
10868 | 38665 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-05-01 10:12 | 2013-05-01 11:26 | 2013-05-01 10:55 | 5 | gallons | 1635 Expo Ln Lot/Yard/Field Asset Id# 750685 Spill contained | Grease Initial diagnosis indicates illegal disposal of oils from auto repair business. | Remove debris clean sewer blockage.
10868 | 38667 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-05-02 08:29 |  | 2013-05-02 11:18 | 0 |  | 6850 W 86th St Asset LS135 Lot/Yard/Field Spill contained. | Equipment Failure LS Debris in pump pipe valve start and stop times unknown. Amount unknown. | Remove debris repair lift station flush area. | SSO Affected Private Property
10868 | 38670 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-05-06 15:29 | 2013-05-06 15:51 | 2013-05-06 17:27 | 20 | gallons | 8210 Flat Branch Dr Asset Id# 439120 439119 Lot/Yard/Field/ Spill Contained. | Debris | Clean sewer blockage flush area. | SSO Affected Private Property
10868 | 39852 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-03 11:31 | 2013-07-03 12:58 | 2013-08-28 14:07 | 0 |  | 3919 Cooper Ln Asset Id 93080 | Debris | Clean sewer blockage flush area clean area | SSO Reached Receiving Water | Crooked Creek
10868 | 39853 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-10 19:06 | 2013-07-10 22:14 | 2013-08-28 14:07 | 0 |  | 1319 Munsee Circle 930738 Lot | Grease | Clean sewer blockage flush area clean & tv | SSO Affected Private Property
10868 | 39542 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-10 19:06 | 2013-07-10 22:07 | 2013-07-12 06:53 | 0 |  | 1319 Munsee Circle | Grease | See Report | SSO Affected Private Property
10868 | 39543 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-10 19:06 | 2013-07-10 22:07 | 2013-07-12 06:55 | 0 |  | 1319 Munsee Circle 930738 Lot | Grease | See Report | SSO Affected Private Property
10868 | 39420 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-17 08:07 | 2013-07-17 23:45 | 2013-07-19 09:00 | 0 |  | 10122 Skippers Ct Asset Id# 490081 - 480080 | Grease | Clean sewer blockage clean & T.V. | SSO Affected Private Property
10868 | 39854 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-17 20:07 | 2013-07-17 23:45 | 2013-07-19 13:58 | 0 |  | 10122 Skippers Ct 490081 - 490080 Custom Home/Bldg spill Contained | Grease | Clean sewer blockage clean & tv | SSO Basement Backup
10868 | 39855 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-18 10:03 | 2013-07-18 10:30 | 2013-07-18 10:12 | 0 |  | 5621 W 85th St Asset ID# 904210 Lot/Yard/Field Spill contained | Collapsed Pipe | Excavate & Repair Sewer | SSO Affected Private Property
10868 | 39459 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-07-18 10:03 | 2013-07-18 10:30 | 2013-07-23 06:55 | 0 |  | 5621 W 85th St Asset ID 904210 | Collapsed pipe | See Report | SSO Affected Private Property
10868 | 39664 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-08-04 09:52 | 2013-08-04 10:55 | 2013-08-26 09:55 | 0 |  | 3645 Aurelia Ct Asset ID# 480789 | Debris | Clean Sewer Blockage
10868 | 39663 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-08-04 09:52 | 2013-08-04 10:55 | 2013-08-06 07:09 | 0 |  | Lot/yard/Field Spill Contained | Debris | Clean Sewer Blockage
10868 | 40467 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-08-12 12:46 | 2013-08-12 13:25 | 2013-08-12 14:23 | 0 |  | 3919 Cooper Ln Asset Id# 93080 | Debris UW discovered overflow while performing routine siphon/CSO inspections. | Clean Sewer Blockage Flush area Clean | SSO Affected Private Property
10868 | 39760 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-08-12 12:46 | 2013-08-12 12:25 | 2013-08-13 06:59 | 0 |  | 3919 Cooper Ln Asset ID 930280 | Debris UW discovered overflow while performing routine siphon CSO inspection. | Clean sewer blockage Flush Area | SSO Affected Private Property
10868 | 39796 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-08-20 18:31 | 2013-08-20 21:30 | 2013-08-22 19:34 | 0 |  | 5930 Allisonwood Ct 13/254 - 13/253 | Structural Blockage | Jet clean blockage flush area clean & TV | SSO Affected Private Property; SSO Reached Receiving Water
10868 | 40468 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-08-20 18:31 | 2013-08-20 21:30 | 2013-08-20 19:01 | 0 |  | 5930 Allisonwood Ct 13/254 - 13/253 | Structural Blockage | Structural Blockage | SSO Affected Private Property; SSO Reached Receiving Water | Behner Brook
10868 | 40009 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-09-03 10:10 | 2013-09-03 11:28 | 2013-09-03 10:26 | 0 |  | 11610 Diamond Pointe Ct | Unknown Debreis Blockage Manhole | See Report | SSO Reached Public Land; SSO Affected Private Property
10868 | 41625 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-09-10 18:01 | 2013-09-10 23:45 | 2013-09-10 20:26 | 0 |  | 10221 E Thompson Rd Manhole #439424 | Equipment Failure Air relief Valve Malfunction | See Report | SSO Reached Public Land
10868 | 40104 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-09-10 18:51 | 2013-09-10 23:45 | 2013-09-10 20:26 | 0 |  | 2700 S Belmont St | Air Relief Valve malfunction. | Isolate Air Relief Valve flush and Vac area. Replace Air Relief Valve. | SSO Reached Public Land
10868 | 41623 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-09-11 10:13 | 2013-09-11 12:15 | 2013-09-11 10:09 | 0 |  | 10111 E Thompson Rd Manhole #439424 | Equipment Failure 3 inch that holds Air Relief Valve Broke | Repaired Pipe See Report | SSO Reached Public Land
10868 | 40225 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-09-19 10:07 | 2013-09-19 12:04 | 2013-09-19 14:41 | 0 |  | 5335 E 65th St Asset #L/S 501-160268 | Hole in Force Main | Repaired Pipe See Report | SSO Reached Public Land
10868 | 40376 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-09-25 09:33 | 2013-09-25 03:07 | 2013-09-25 01:30 | 0 |  | 4244 Redfern Dr Manhole #952610 | Debris blockage in CEG Sanitary Main caused overflow in private manhole (Beech Grove) | wRemoved Blockage Jet clean sewer blockageremoved blockage flush area. Clean & TV Sanitary Main | SSO Reached Public Land; SSO Reached Receiving Water | Beech Creek
10868 | 40603 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-09-30 11:20 | 2013-09-30 13:55 | 2013-09-30 11:55 | 0 |  | 5220 Stanley Rd Manhole #750465 | Unknown Utilized basin cleaner and jet to remove debris wrapped around a pressure ring that had fallen into pipe from rubber insert at top of manhole. | Removed Blockage See Report | SSO Reached Public Land; SSO Reached Receiving Water | North Creek
10868 | 40682 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-10-03 09:46 | 2013-10-03 13:42 | 2013-10-03 13:00 | 0 |  | 4883 Kentucky Ave Manhole # Unknown | Unknown Vandalism Lid was removed and debris was thrown in MH. shovel had lodged in invert and caused overflow. | Removed Blockage See Report | SSO Reached Public Land; SSO Affected Private Property
10868 | 41099 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-10-18 08:01 | 2013-10-18 09:17 | 2013-10-18 10:51 | 0 |  | 5741 Sherman Ave L/S 519-SMH 140339 | Unknown Hole in Force Main | Repaired Pipe See Report | SSO Reached Public Land; SSO Affected Private Property
10868 | 41644 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-11-04 10:41 | 2013-11-04 11:08 | 2013-11-04 10:58 | 0 |  | 1549 Countryside Ln Manhole #71004 | Unknown manhole inundated with roots. | Removed Blockage See Report | SSO Reached Public Land; SSO Affected Private Property | White Lick Creek
10868 | 41818 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-11-13 13:45 | 2013-11-13 14:36 | 2013-11-13 14:01 | 0 |  | 62 N Edmondson Ave Manhole #320353 | Unknown Grease Blockage In Manhole Manhole | Removed Blockage See Report | SSO Reached Public Land; SSO Reached Receiving Water | South Creek
10868 | 42206 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-11-26 16:00 | 2013-11-26 23:00 | 2013-11-26 19:01 | 0 |  | 3765 W 21st St Manhole #811828 | Stone and other debris. | Removed Blockage See Report | SSO Reached Public Land; SSO Affected Private Property
10868 | 42240 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-11-27 13:34 | 2013-11-27 18:30 | 2013-11-27 15:28 | 0 |  | 1001 Broad Ripple Ave Sanitary Main #696998-696999 | Unknown Heavy Grease | Removed Blockage See Report | SSO Basement Backup
10868 | 42307 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-04 10:14 | 2013-12-04 13:45 | 2013-12-04 14:39 | 0 |  | 6800 E 32nd St L?S 523-SMH 331085 | Unknown Hole in Force Main | Repaired Pipe See Report | SSO Reached Public Land
10868 | 42846 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-21 06:18 | 2013-12-22 18:00 | 2013-12-22 01:42 | 1465 | gallons | Manhole 635034 3516 Woodcliff | Overflow occurred due to Rain Event system is on upper reaches of Combination Area | See Report | SSO Affected Private Property
10868 | 42847 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-21 09:23 | 2013-12-22 18:00 | 2013-12-21 10:43 | 1176 | gallons | Manhole 330941 3725 Payton | Overflow due to rain event. | See Report | SSO Basement Backup
10868 | 43777 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-21 18:18 | 2013-12-22 | 2013-12-22 01:42 | 6740 | gallons | Manhole 635035 2440 Beechcrest | Rain 3.02 inches System returned to normal after rain event ended. | See Report | SSO Basement Backup
10868 | 42844 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-21 18:18 | 2013-12-22 | 2013-12-22 01:42 | 0 |  | Manhole 635035 | System return to normal after rain event ended. | See Report | SSO Basement Backup
10868 | 43776 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-21 18:18 | 2013-12-22 | 2013-12-22 01:42 | 6740 | gallons | Manhole 635035 2440 Beechcrest | Rain 3.02 inches system returned to normal after rain event ended | See Report | SSO Basement Backup
10868 | 42842 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-21 19:50 | 2013-12-22 | 2013-12-21 23:07 | 0 |  | Manhole 510923 1736 Colt | Rain 3.02 inches System was surcharged due to rain event. | Removed Blockage | SSO Basement Backup; SSO Affected Private Property
10868 | 42845 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-22 11:00 | 2013-12-22 | 2013-12-22 11:34 | 0 |  | Manhole 635004 3125 Bradbury | Overflow was due to system overflow during rain event system is at upper end of combination area. | See Report | SSO Basement Backup; SSO Affected Private Property
10868 | 43093 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-22 12:30 | 2013-12-22 14:10 | 2013-12-26 | 537 | gallons | MH 906168 7153 W 86th ST | Equipment Failure Rain 3.02 inches | See Report | SSO Affected Private Property
10868 | 42849 | IN0023183 | CWA Authority Incorporated Belmont Advanced Waste Water Treatment | Marion | 2013-12-22 16:05 | 2013-12-22 18:00 | 2013-12-22 19:05 | 0 |  | 3739 Decamp 3947 Esquire | Rain 3.02 inches system surcharged due to rain event no overflow was seen in basement. | See Report | SSO Basement Backup; SSO Affected Private Property
12903 | 36629 | IN0023574 - Terminated | LAWRENCE UTILITIES | Marion | 2013-04-24 07:15 | 2013-04-24 14:30 | 2013-04-25 08:23 | 5625 | gallons | 5013 Kitley Avenue | Precipitation event caused untreated release from manholes to storm sewer | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent future SSOs. | SSO Reached Public Land
12903 | 36631 | IN0023574 - Terminated | LAWRENCE UTILITIES | Marion | 2013-04-24 07:35 | 2013-04-24 12:35 | 2013-04-25 08:23 | 1500 | gallons | 5453 David Street | Precipitation event cause overflow of untreated release from a manhole to storm sewer. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent future SSOs. | SSO Reached Public Land
12903 | 36628 | IN0023574 - Terminated | LAWRENCE UTILITIES | Marion | 2013-04-24 08:00 | 2013-04-24 16:00 | 2013-04-25 08:23 | 14400 | gallons | 46th and Post Road | Precipitation event caused untreated release from manholes to storm sewer. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent future SSOs. | SSO Reached Public Land; Storm Sewer
12903 | 36626 | IN0023574 - Terminated | LAWRENCE UTILITIES | Marion | 2013-04-24 10:44 | 2013-04-24 15:00 | 2013-04-25 08:23 | 14200 | gallons | 7103 Oaklandon Road | Precipitation event triggered overflow of untreated matter from manhole to receiving water. | City of Lawrence is in the process of completing a SSES to determine the best solution to prevent future SSOs. | SSO Reached Receiving Water | North Branch
12903 | 36709 | IN0023574 - Terminated | LAWRENCE UTILITIES | Marion | 2013-04-29 20:32 | 2013-04-29 21:52 | 2013-04-29 22:41 | 400 | gallons | 5840 Lawton Loop West Drive | Crack in an above ground pipe resulted in an untreated release to the surrounding ground. | SSO signs placed at discharge location. Jet rodded sewer and repaired crack in pipe. | SSO Reached Public Land
12903 | 36767 | IN0023574 - Terminated | LAWRENCE UTILITIES | Marion | 2013-05-03 10:00 | 2013-05-03 11:00 | 2013-05-03 15:54 | 120 | gallons | Manhole at 7644 Bay Ridge Drive | Manhole overflow in a non permitted location resulted in an untreated release that reached public land paved surface and storm sewer. | Untility crew dispatched with vactor truck and cleaned main sewer. No source of blockage was found. Affected area was washed down and limed. Warning signs posted for public.Will keep a close eye on the Manhole and main segment for a few weeks. this area has never experienced a problem like this before and we believe it to be anomolous.The are will continue to receive routine PM activities such as MH inspections and main cleaning per schedule. | SSO Reached Public Land; Storm Sewer
16166 | 35464 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-01-14 |  | 2013-01-14 10:01 | 1 | gallons | 2738 North Whitcomb | Precipitation event treiggered residential basement back up | Basement had drained by the time of notification. | SSO Basement Backup
16166 | 35468 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-01-14 |  | 2013-01-14 10:02 | 0 |  | 2706 Moller Road | Precipitation event caused residential basement back up | Water had drained by the time we were notified. | SSO Basement Backup
16166 | 35469 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-01-14 09:00 |  | 2013-01-14 09:00 | 0 |  | 6821 West 10th Street Chapel Hill Lift Station | Precipitation event caused untreated release from Chapel Hill Lift Station to the ground and storm sewer. | Water had stopped surcharging when area was checked 1/14/2013. No calls to town about problem. Cleaned up area of discharge and spread lime on complete area. | SSO Reached Public Land
16166 | 36267 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-15 | 2013-04-19 | 2013-04-19 08:52 | 0 |  | 6729 Doris Drive Manhole 3-43 | Precipitation event caused untreated release from manhole to surrounding ground and storm sewer | Will go down by end of day 4/19/13. | SSO Reached Public Land; Storm Sewer
16166 | 36270 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 08:29 | 0 |  | 5828 West 30th Street | Precipitation event caused an untreated release into a residential basement | Will go down by end of day 4/19/13. | SSO Basement Backup
16166 | 36250 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 07:19 | 0 |  | 7216 Halden Place | Precipitation event resulted in untreated release into a residential basement. | Will go down by end of day 4/19/13. | SSO Basement Backup
16166 | 36710 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 09:52 | 0 |  | 2228 Fisher Basement | Untreated Release Rain 3.33 inches Will go down by end of day 4/19/2013
16166 | 36155 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 |  | 2013-04-19 06:41 | 0 |  | 2224 Fisher | Precipitation event triggered an untreated release into a residential basement | Will go down by end of day 4/19/2013. | SSO Basement Backup
16166 | 36253 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 08:53 | 0 |  | Chapel Hill Lift Station 4-1 | Precipitation event caused untreated release from Lift Station to surrounding ground and storm sewer | Will go down by end of day 4/19/13. Clean up area of discharge spread lime on complete area. | SSO Reached Public Land
16166 | 36254 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 08:52 | 0 |  | thorndale and Carlsen 3-68 | Precipitation event untreated release from manhole to surrounding ground and storm sewer | Will go down by end of day 4/19/13. Clean up area of discharge spread lime on complete area. | SSO Reached Public Land; Storm Sewer
16166 | 36255 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 08:52 | 0 |  | 1625 Farley Manhole 3-37 | Precipitation event triggered untreated release from manhole to surrounding ground and storm sewer. | Will go down by end of day 4/19/13. Clean up area of discharge spread lime on complete area. | SSO Reached Public Land; Storm Sewer
16166 | 36266 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 08:52 | 0 |  | 6705 Doris Drive Manhole 3-42 | Precipitation event caused untreated release from manhole to surrounding ground and storm sewer. | Will go down by end of day 4/19/13. Clean up area of discharge spread lime on complete area. | SSO Reached Public Land; Storm Sewer
16166 | 36271 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 08:53 | 0 |  | 16th Street and Farley. Manhole 3-31 | Precipitation event caused an untreated release from manhole to surrounding ground and storm sewer. | Will go down by end of day 4/19/13. | SSO Reached Public Land; Storm Sewer
16166 | 36268 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 07:11 | 0 |  | 5249 West 15th Street | Precipitation event caused untreated release into residential basement. | Will go down by end of day 4/19/13. | SSO Basement Backup; SSO Affected Private Property
16166 | 36716 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 09:37 | 0 |  | 1908 North Auburn Basement | Untreated Release. Rain 3.33 inches Will go down by end of day 4/19/2013 |  | SSO Basement Backup
16166 | 36153 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 |  | 2013-04-19 06:39 | 0 |  | 5109 McCray | Precipitation event triggered an untreated release into a residential basement | Will go down by end of day 4/19/2013. | SSO Basement Backup
16166 | 36274 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 09:02 | 0 |  | 2211 Main Street | Precipitation event caused an untreated release into a residential basement | Will go down by end of day 4/19/13. | SSO Basement Backup
16166 | 36720 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 10:20 | 0 |  | 5047 McCray Basement | Untreated Release Rain 3.33 inches Will go down by end of day 4/19/13 |  | SSO Basement Backup
16166 | 36156 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 |  | 2013-04-19 06:41 | 0 |  | 7040 Buick | Precipitation event resulted in untreated release into a residential basement | Will go down by end of day 4/192013
16166 | 36251 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 08:53 | 0 |  | Doris and Farley Manhole 3-38 | Precipitation event caused untrteated release from manhole to surrounding ground and storm sewer. | Will go down by end of day 4/19/2013. Clean up area of discharge spread lime on complete area. | SSO Reached Public Land; SSO Affected Private Property; Paved Surface
16166 | 36608 | IN0032972 | SPEEDWAY WASTE WATER TREATMENT PLANT | Marion | 2013-04-18 | 2013-04-19 | 2013-04-19 13:42 | 0 |  | 5001 McCray Basement | Untreated Release Rain 3.33 rain Will go down by end of day 4/19/2013 |  | SSO Basement Backup
12903 | 36260 | Terminated Permit | LAWRENCE UTILITIES | Marion | 2013-04-24 07:15 |  | 2013-04-24 08:52 | 0 |  | 5013 Kitley Ave (2 mhs) Storm Sewer | Untreated Release Rain 1.64 inches. | City of Lawrence Utilities is in the process of completing a SSES to determine the best solution to prevent future SSO s | Storm Sewer
12903 | 36263 | Terminated Permit | LAWRENCE UTILITIES | Marion | 2013-04-24 07:35 |  | 2013-04-24 08:52 | 5000 | gallons | 5453 David St (1MH) Storm Sewer | Untreated Release Rain 1.64 inches | City of Lawrence utilities is in the process of completing a SSES to determine the best solution to prevent future SSO s | Storm Sewer
12903 | 36261 | Terminated Permit | LAWRENCE UTILITIES | Marion | 2013-04-24 08:00 |  | 2013-04-24 08:52 | 300000 | gallons | 46th and Post Rd (3MHS) Storm Sewer | Untreated Release 1.64 rain | City of Lawrence utilities is in the process of completing a SSES to determine the best solution to prevent future SSO s | Storm Sewer
12656 | 35340 | IN0020427 | Bremen Waste Water Treatment Plant | Marshall | 2013-03-11 | 2013-04-05 | 2013-03-11 12:51 | 0 | gallons | Town of Bremen WWTP Bremen IN | Chalking on bio towers being repladed on March 28th 2013 with alternate dates of 3/29/2013 or April 1 3 or 5 2013. Only one tower at a time will be out of service. Once one tower is complete it will be put back in service and media growth monitored before starting the second tower. There will be a bypass of a treatment process while each tower is down but the result will be blended with the final effluent and sampled. | No further actions needed. | SSO Occurred at Treatment Plant
12073 | 34908 | IN0020991 | Plymouth Waste Water Treatment Plant | Marshall | 2013-01-30 | 2013-01-30 18:15 | 2013-01-30 18:15 | 0 |  | CSO 005 007 and 002 Plymouth IN | CSO overflow due to 2.89 inches of rain snow melt and frozen ground. Untreated Release of effluent | tREATMENT PLANT MAXIMIZED | SSO Reached Receiving Water | Yellow River
12073 | 36556 | IN0020991 | Plymouth Waste Water Treatment Plant | Marshall | 2013-04-17 08:40 |  | 2013-04-18 06:30 | 1052890 | gallons | CSO 005 CSO 007 CSO 010 Yellow River | Untreated Release Rain 1.28 inches CSO due to rain storm that hit late at night on 4-17-13 and caused the CSO s to overflow. |  | SSO Reached Receiving Water | Yellow River
12073 | 38027 | IN0020991 | Plymouth Waste Water Treatment Plant | Marshall | 2013-06-12 09:20 |  | 2013-06-13 06:30 | 6600000 | gallons | CSO s 005007009010 | Rain This was do to heavy rain that hit around 7:15am the treatment plant was maximized at peak flow of 6.6 MGD. The rainfalls peak 15 minute intensity was 1.56 as for the volume it is still on going. |  | SSO Reached Receiving Water | Yellow River
12073 | 37587 | IN0020991 | Plymouth Waste Water Treatment Plant | Marshall | 2013-06-12 21:50 |  | 2013-06-13 06:30 | 3011000 | gallons | CSO s 005007009010 | Rain 1.92 inches CSO. This was do to heavy rain that hit around 7:30pm the treatment plant did not exceed it design flow do to the rain starting late in the evening. The peak 15 minute intensity was 1.92 inches. |  | SSO Reached Receiving Water | Yellow River
12073 | 38058 | IN0020991 | Plymouth Waste Water Treatment Plant | Marshall | 2013-06-26 09:20 |  | 2013-06-26 14:07 | 0 |  | CSO s 002004005007009010011 | Rain 2.78 inches |  | SSO Affected Private Property | Yellow River
11777 | 35785 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-01-12 19:30 | 2013-01-13 08:20 | 2013-01-14 11:41 | 31500 | gallons | Lift Station 17 and 34. | Precipitation event triggered untreated release from Lift Stations to Overflow Basin. | Overflow from Lift Stations 17 and 34 was diverted to the overflow basin at LS 17. Pumped back into collection system after flow returned to normal. Manned three lift stations to minimize overflow totals. Continue to use overflow basin as designed. | SSO Reached Public Land
11777 | 35144 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-03-29 02:00 |  | 2013-04-01 09:07 | 0 |  | Force Main coming from area of bachelers quarter. | Untreated Release Equipment Failure SSO is due to a suspected sewer line break. Event was noticed on Friday 3/29. Break is in a remote area that is heavily wooded. Further investigation will be completed on 4/1 and proper course of action developed to initiate repairs. Tree removal will be required and a permit is being sought by the Forestry Division. The main buildings on this line were virtually empty for the Easter weekend holiday so flows would have been a a low minimal. | It has been suggested to the Public Works Department that the lift station feeding the line with the break be shut down and the pumper trucks be utilized to shuttle flows to the gravity line further south of the break. | SSO Affected Private Property
11777 | 36106 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-04-19 03:30 | 2013-04-19 07:30 | 2013-04-19 10:59 | 0 |  | Dept Of Navy Crane Division NswcLift Station 17 - Overflow Basin | Precipitation event necessitated pumping water from lift station to overflow basin. Overflow basin reached capacity and overflowed to surrounding ground. Untreated release. | Area was inspecte operators are inspecting lift station until flow decreases. No evident environmental damage. Will continue using overflow basin as designed. | SSO Reached Public Land
11777 | 39060 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-06-26 04:00 | 2013-06-27 05:00 | 2013-06-27 07:00 | 0 |  | LS #6 Ground | Rain 5.25 inches Power Failure The base experienced 3 severe storms in 24 hours and received 5.25 inches of rain as recorded by the WWTP staff | See Report | SSO Affected Private Property
11777 | 38943 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-06-26 07:00 | 2013-06-27 02:00 | 2013-06-27 07:07 | 0 |  | LS2173436 see attached notes for details. LS17 excess flow (150000 gals) diverted to EQ basin and LS still overflowed after that; others to ground. | Rain 5.25 Power Failure. The base experienced 3 severe storms in 24 hours and received 5.25 inches of rain as recorded by the WWTP staff. The first 150.000 gallons from LS17 was diverted into the overflow basin and then approx 5000 gals overflowed from LS. there was wide spread power outages that affected the operation at LS2 and LS36. LS344 is directly downstream of LS17. While the Utility crews tried to manage the flow with the vac truck it was deemed unsafe to continue and were pulled back. I have attached an email report from the Utility Supervisor with all of the overflow information. | Overflows due to Force Majeaure and all normal procedures were tried. | SSO Affected Private Property
11777 | 39794 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-08-18 08:30 | 2013-08-18 09:30 | 2013-08-19 12:33 | 0 |  | Sludge Holding Tank | Equipment Failure Upper and lower digesters of WWTP were being cleaned and wastewater was transported to sludge holding tank. The tank was filled above pipe discharge and gravity fed out of the pipe because valve was not completely closed. | Repaired Pipe See Report | SSO Occurred at Treatment Plant
11777 | 39817 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-08-23 10:00 | 2013-08-24 02:00 | 2013-08-27 11:31 | 0 |  | LS21 wet well discharge pipe ground | Power Failure Equipment Failure | Pumps were shut off until repairs completed. No new actions are going to be taken but the current practice of lift station checks will be continued. | SSO Affected Private Property
11777 | 43518 | IN0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-12-21 02:45 | 2013-12-22 04:00 | 2013-12-23 10:05 | 150000 | gallons | Raw Bypass at WWTP | Rain 5.87 inches the base experienced torrential downpour of rain that lasted for approximately 30 hours. Attached to this report is a time line of events for this event. The estimated release vp;ie was 1.5MGD | See Attachment | SSO Occurred at Treatment Plant | Boggs Creek
11777 | 43457 | IN0021539 ( LS 17 excess flow (150000 gals) diverted to EQ basin and LS Still Overflowed after that for 20 hr 50 min) | Naval Surface Warfare Center Crane Division | Martin | 2013-12-21 09:30 | 2013-12-22 06:20 | 2013-12-23 10:05 | 150000 | gallons | LS 17 See Attachment | Rain 5.87 inches The base experienced torrential downpour of rain that lasted for approximately 30 hours. Attached to the report is a time line of events for this event. The estimated release volume was 1.5 MGD | See Report | SSO Affected Private Property
60851 | 43522 | IN0021539 Creek | WINCHESTER | Martin | 2013-12-21 07:00 | 2013-12-22 07:00 | 2013-12-23 14:35 | 0 |  | Ponds 002 003 008 overflows TSS result of 74/4 mgl | Rain 5.7 inches the base experienced torrential downpour of rain that lasted for approximately 30 hours. Attached to this report is a time line of event for this event. Th ponds were pumped down on Saturday 12/21 but with the continued heavy rains they could not contain the sheet flows coming off of the demolition range. | See Report
33101 | 43455 | IN0039241 | Loogootee Waste Water Treatment Plant | Martin | 2013-12-21 03:00 | 2013-12-22 08:00 | 2014-02-07 08:57 | 0 |  | MH #11 156 254 | Untreated Release Sanitary Sewer collection system surcharged due to excessive amount of rain fall (5.0 inches) in a short amount of time
30922 | 35243 | IN0040631 | SHOALS MUNICIPAL WASTE WATER TREATMENT PLANT | Martin | 2013-01-14 06:00 |  | 2013-01-14 11:21 | 0 |  | Manhole Shoals IN | Precipitation event resulted in Beaver Creek flooding manhole resulting in untreated release to Beaver Creek |  | SSO Reached Public Land; SSO Reached Receiving Water | Beaver Creek
30922 | 43464 | IN0040631 | SHOALS MUNICIPAL WASTE WATER TREATMENT PLANT | Martin | 2013-12-22 12:00 |  | 2013-12-23 09:15 | 0 |  | Manhole | Creek over Manhole |  | SSO Reached Receiving Water | Beaver Creek
11777 | 39595 | N0021539 | Naval Surface Warfare Center Crane Division | Martin | 2013-07-25 05:00 | 2013-07-25 06:30 | 2013-07-25 16:07 | 0 |  | WWTP | Unknown During renovation of the WWTP material from an old digester was removed and placed in the flock tank to pretreat prior to entering the WWTP system. The aerator was turned on and overtime it began to froth/foam. The foam spilled over the side of the tank. | See Report | SSO Occurred at Treatment Plant
10621 | 36538 | IN0024902 | Grissom Air Reserve Base | Miami | 2013-04-19 16:00 | 2013-04-20 03:30 | 2013-04-20 08:54 | 6900 | gallons | Manhole at Thule CourtManhole at Shaw | Precipitation event(s) flow exceeded collection system capacity creating a surcharge and untreated release from manholes to storm sewer. | Maximizing flow to plant to empty collection system. Continuing collection system maintenance and inspection activities where we have found and removed clear water sources already and will continue with those actions. | SSO Reached Public Land; Storm Sewer
10621 | 37859 | IN0024902 | Grissom Air Reserve Base | Miami | 2013-06-13 02:30 | 2013-06-13 05:30 | 2013-06-13 12:28 | 0 |  | Manhole at Thule Ct. Storm Drain | Power Failure Rain 1.69 inches. Heavy rains Pump Station 802 experienced a power failure. | Investigation found that a main fuse had blown. The fuse was replaces and the pump station power was checked for both operational amps and voltage. The pump station was brought back online after a second fuse failure. The equipment was checked and the station was returned to service. The pump station was monitored the rest of the night and no further incident occurred with the power. Maintenance activities will be performed to assure that no equipment in the station is faulty or damaged. | Storm Sewer
47279 | 36537 | IN0032328 | PERU CITY UTILITIES WASTE WATER TREATMENT PLANT | Miami | 2013-04-19 03:30 | 2013-04-19 06:40 | 2013-04-20 08:54 | 18200 | gallons | Manhole at Orchid Court | Precipitation event(s) caused sewer system surcharge and untreated release to storm sewer. | Maximizing flow to plant to empty collection system. Continuing collection system manintenance and inspection activities where we have found and removed clear water sources already and will continue with those actions. | SSO Reached Public Land
47279 | 37363 | IN0032328 | PERU CITY UTILITIES WASTE WATER TREATMENT PLANT | Miami | 2013-04-19 03:30 | 2013-04-19 06:40 | 2013-04-20 09:30 | 200000 | gallons | Manhole at Orchid Ct Storm Ditch | Untreated Release Rain 4.5 inches. Heavy rains-4.5 inches in less that 36 hours-caused sewer system to surcharge and release to storm sewer. | Maximizing flow to plant to empty collection system. Continuing collection system maintenance and inspection activities where we have found and removed clear water sources already and will continue with those actions. | SSO Affected Private Property
47279 | 39537 | IN0032328 | PERU CITY UTILITIES WASTE WATER TREATMENT PLANT | Miami | 2013-07-09 01:00 | 2013-07-09 01:30 | 2013-07-10 09:45 | 0 |  | CSO #104 Tippecanoe CSO Wabash River | Equipment Failure Level Sensor malfunction at Cass Street lift station causing it to stop pumping. Flow at the WWTP dropped from 5.5 MGD to 1.64MGD. Level sensor was reset fixing the problem. | See Report | SSO Reached Receiving Water | Wabash River
40091 | 36234 | IN0039888 | CONVERSE SEWER PLANT | Miami | 2013-04-19 09:00 |  | 2013-04-19 10:35 | 100000 | gallons | SSO# manhole B-17 4th Street and Wabash Street | Precipitation event caused flooding and untreated release to receiving waters. |  | SSO Reached Receiving Water | Little Pipe Creek
40091 | 36233 | IN0039888 | CONVERSE SEWER PLANT | Miami | 2013-04-19 09:30 |  | 2013-04-19 10:35 | 0 |  | Lift Station at Sycamore and Maple Streets | Precipitation event caused creek flooding resulting in lift station being submerged. Probable untreated release to receiving waters. | Waiting for flood waters to recede. Electrician and Pump Company on standby to repair lift station. | SSO Reached Public Land; SSO Reached Receiving Water | Little Pipe Creek
11892 | 35881 | IN0035718 | Dillman Road Waste Water Treatment Plant | Monroe | 2013-01-11 06:45 | 2013-01-11 12:30 | 2013-01-14 17:37 | 20797 | gallons | Manhole 6 near Micro Motors Grimes Rd. | Precipitation event triggered an untreated release from a manhole to receiving waters. | The area was cleaned of debris. We are under an agreed order and have a wet weather management program in progress to rctify these situations. | SSO Reached Receiving Water | Clear Creek
11892 | 35777 | IN0035718 | Dillman Road Waste Water Treatment Plant | Monroe | 2013-01-12 20:30 | 2013-01-13 12:45 | 2013-04-22 12:43 | 132300 | gallons | Manhole #6 Grimes Lane near Micro Motors9933 College Mall Road near Steele Chir3124 - 1500 South Rogers Crosby Warehouse | Precipitation event triggered untreated release from multiple locations to receiving waters. | The area was cleaned of debris. We are under an agreed order and have a wet weather management program in progress to rectify these situations. | SSO Reached Receiving Water | Clear Creek; Jackson Creek
11892 | 36493 | IN0035718 | Dillman Road Waste Water Treatment Plant | Monroe | 2013-04-19 02:00 | 2013-04-19 09:00 | 2013-04-19 14:13 | 132300 | gallons | MH# 6 - Grimes Lane (near Micro Motors) | Precipitation event triggered untreated release from manhole to receiving water. | The area was cleaned of debris. We are under an agreed order and have a wet weather management program in progress to rectify these situations. | SSO Reached Receiving Water | Clear Creek
11892 | 38212 | IN0035718 | Dillman Road Waste Water Treatment Plant | Monroe | 2013-06-29 16:30 | 2013-06-29 18:00 | 2013-07-02 | 0 |  | MH #6 Grimes lane (micro motors) | Rain 1.06 inches Manhole | The area was cleaned of debris. We are under an agreed order and have a wet weather management program in progress to rectify these situations.
11892 | 39279 | IN0035718 | Dillman Road Waste Water Treatment Plant | Monroe | 2013-07-22 01:20 | 2013-07-22 02:30 | 2013-07-22 10:42 | 0 |  | MH #6 Grimes Ln (micro motors) Manhole | Rain 1.25 inches
11892 | 38213 | IN0035718 - Dillman | Dillman Road Waste Water Treatment Plant | Monroe | 2013-06-30 15:00 | 2013-06-30 18:00 | 2013-07-02 | 0 |  | MH #^ Grimes Lane (micro motors) | Rain 0.20 inches | The area was cleaned of debris. We are under an agreed order and have a wet weather management program in progress to rectify these situations.
11892 | 42850 | IN0035718 Outfall 001 (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 07:00 | 2013-12-23 11:00 | 2013-12-24 13:20 | 5695119 | gallons | Grimes Ln Micro Motors MH6 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Clear Creek
11892 | 42873 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 10:45 | 2013-12-22 08:00 | 2013-12-24 13:20 | 5695119 | gallons | S Walnut St Herald Times MH 6134 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Clear Creek
11892 | 38056 | IN0035718 (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-06-26 18:30 | 2013-06-26 21:30 | 2013-06-27 10:15 | 0 |  | Discharge pipe near MH (Micro Motors) | Rain 1.96 inches MH #6 | The area was cleaned of debris. We are under an agreed order an have a wet weather management program in progress to rectify these situations. | SSO Affected Private Property
11892 | 39280 | IN0035718 (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-07-20 18:00 | 2013-07-23 11:00 | 2013-07-23 11:00 | 0 |  | Fieldstone Lift Station MH #11291 Pump Station Failure | Rain 2.05 inches Power Failure Equipment Failure Pump failure due to lightning strike.
11892 | 39281 | IN0035718 (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-07-23 15:00 | 2013-07-23 21:00 | 2013-07-24 11:08 | 0 |  | MH#6 Grimes Lane (micro motors) Manhole | Rain 0.35 inches
11892 | 43235 | IN0035718 (Dillman) Outfall 001 | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-30 10:00 | 2013-12-30 14:00 | 2013-12-31 14:15 | 1800 | gallons | 444 S Patterson MH #7028 | Equipment failure Blockage in sewer main due to build up of rocks/stone in the pipe itself. | See Report
11892 | 40761 | IN0035718 Bloomington- Dillman Rd Outfall 001 | Dillman Road Waste Water Treatment Plant | Monroe | 2013-10-06 03:42 | 2013-10-07 05:00 | 2013-10-07 10:23 | 0 |  | Grimes Lane - Micro Motors MH #6 | Rain 4.0 inches excessive amounts of rain for long periods of time. | See Report
11892 | 42851 | IN0035718 Outfall 001 (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 21:25 | 2013-12-22 12:00 | 2013-12-24 13:20 | 5695119 | gallons | Grimes Ln Micro Motors MH 6290 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Clear Creek
11892 | 42863 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 | 2013-01-21 15:00 | 2013-12-24 13:20 | 5695119 | gallons | College Mall Rd Bton Hardware MH 9942 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Jackson Creek
11892 | 42853 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 12:30 | 2013-12-22 10:00 | 2013-12-24 13:20 | 5695119 | gallons | College Mall Rd Steele Chiro MH 9933 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Jackson Creek
11892 | 42871 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 22:25 | 2013-12-22 11:00 | 2013-12-24 13:20 | 5695119 | gallons | Charlie Ave MH 4749 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Clear Creek
11892 | 42868 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 11:00 | 2013-12-22 06:00 | 2013-12-24 13:20 | 0 |  | 1500 S Rogers St Crosley Warehouse MH 3124 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Clear Creek
11892 | 42875 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 15:30 | 2013-12-22 09:15 | 2013-12-24 13:20 | 5695119 | gallons | Hunter & Easteside Dr MH 1095 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Jackson Creek
11892 | 42876 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 21:55 | 2013-12-22 07:30 | 2013-12-24 13:20 | 5695119 | gallons | 1st St & Walker St MH 1341 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Clear Creek
11892 | 42865 | IN0035718 Outfall 001A (Dillman) | Dillman Road Waste Water Treatment Plant | Monroe | 2013-12-21 22:10 | 2013-12-22 10:00 | 2013-12-24 13:20 | 5695119 | gallons | College Mall Rd Bton Hardware MH 9942 | Rain 4.38 inches | See Report | SSO Reached Receiving Water | Jackson Creek
12614 | 34339 | IN0035726 | Blucher Poole Waste Water Treatment Plant | Monroe | 2013-02-17 12:00 | 2013-02-20 14:00 | 2013-02-21 18:15 | 500 | gallons | Man hole 2116 2703 North Skyline Drive | Equipment Failure - Untreated Release - Sewage was seeping from a privately owned cleanout on a lateral just SW of ManHole 2116 because of roots in the system. | The area was cleaned of debris and the roots in the surrounding mains were cut. | SSO Affected Private Property; SSO Reached Receiving Water | Beanblossom Creek
12614 | 34835 | IN0035726 | Blucher Poole Waste Water Treatment Plant | Monroe | 2013-02-17 12:00 | 2013-02-20 14:00 | 2013-02-21 18:15 | 500 | gallons | Manhole 2116 2703 North Skyline Drive Bloomington IN | Untreated release seeping from a privately owned cleanout on a lateral jus Southwest of Manhole 2116 because of root infiltration. | The area was cleared of debris. roots in the surrounding mains were cut. | SSO Affected Private Property; SSO Reached Receiving Water; Surface Soil | Cascades Creek
12614 | 34836 | IN0035726 | Blucher Poole Waste Water Treatment Plant | Monroe | 2013-02-21 16:00 | 2013-02-21 18:00 | 2013-02-22 12:54 | 72000 | gallons | Manhole 2652 | Blocked Sewer triggered Untreated Release into Cascades Creek | The area was cleaned of debris. Used the Vactor to open blockage. | SSO Reached Receiving Water | Cascades Creek
12614 | 42877 | IN0035726 Outfall 001A (Blucher) | Blucher Poole Waste Water Treatment Plant | Monroe | 2013-12-22 12:00 | 2013-12-22 15:00 | 2013-12-24 13:20 | 10530 | gallons | Manhole 1506 - Brookdale & Woodburn | Rain 4.38 inches | See Report |  | Cascades Creek
42975 | 37918 | IN0045187 | MONROE COUNTY REGIONAL WASTE DISTRICT | Monroe | 2013-06-13 08:30 | 2013-06-13 10:00 | 2013-06-14 08:42 | 2000 | gallons | Lift station #3 Ground | Untreated Release No noticeable damage occurred. Loss of phase at the Lift Station. One alarm failed to make notification. | Had Todd s Septic Service pump the sewage out of the station until full power was restored (Approx 3 hours). Duke Energy Restored full power ordered new transformer (Replacement) for Portable Generator. | SSO Affected Private Property
42975 | 38868 | IN0045187 | MONROE COUNTY REGIONAL WASTE DISTRICT | Monroe | 2013-06-22 13:29 | 2013-06-22 12:30 | 2013-06-24 09:45 | 0 |  | Waters Edge #2 lift St Ground | Control float was unable to function to function due to grease build up. | Cleaned grease off of the floats and tank wall Contacted septic hauler to schedule tank cleaning. | SSO Affected Private Property
42975 | 41083 | IN0045187 Outfall 001 | MONROE COUNTY REGIONAL WASTE DISTRICT | Monroe | 2013-10-08 09:00 | 2013-10-08 09:30 | 2020-10-08 13:02 | 0 |  | Lift Station force main east of 9410 S Lake Ridge | Equipment failure Pipe Failure | Repaired Pipe | SSO Affected Private Property; SSO Reached Receiving Water
108728 | 35134 | No NPDES Permit | Eastern Richland Sewer Corporation | Monroe | 2013-01-12 |  | 2013-01-24 15:11 | 0 |  | Manholes 102 and 104 - Hartstralt Road Bloomington/ Elletsville. Eastern Richland Sewer Corporation | Precipitation event caused manhole overflows with untreated release | We are going to place solid sole manhole lids and reseal rings and risers of the manholes. We will monitor the issues closely during heavy rain fall. | SSO Reached Receiving Water | Jacks Defeat Creek
108728 | 35136 | No NPDES permit | Eastern Richland Sewer Corporation | Monroe | 2013-01-12 | 2013-01-13 | 2013-01-22 15:06 | 0 |  | Manhole 169 Eastern Richland Sewer Corp. Bloomington IN | Apparent vandalism and intentionalblockage of sewer main in Manhole 169 just off Hartstraight Road. Discovered concrete block blocking main with two logs holding it in place and miscellaneous blactop chunks as well. Caused untreated release into Jacks Defeat Creek | Removed debris and overflow was eliminated. We will monitor the manhole more closely against future vandalism. | SSO Reached Receiving Water | Jacks Defeat Creek
108728 | 35202 | No NPDES Permit | Eastern Richland Sewer Corporation | Monroe | 2013-01-30 | 2013-01-30 07:30 | 2013-01-30 12:20 | 0 |  | Manholes 169 and 104 on Hartstraight Road Bloomington IN | Precipitation event/flash flood resulted in minimal untreated release from manholes 169 and 104. | Sealing lids and reported to engineer for further advice. | SSO Reached Public Land; SSO Reached Receiving Water | Jacks Defeat Creek
| 34782 | No Permit found |  | Monroe | 2013-02-26 11:00 | 2013-02-26 12:00 | 2013-02-26 15:00 | 0 |  | Manhole 169 Hartstralt Road Bloomington IN | Release from Manhole 169 | We will be installing a sealed lid to this manhole. | SSO Reached Public Land; Surface Soil
| 36347 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-04-19 03:00 | 2013-04-19 07:00 | 2013-04-22 08:56 | 0 |  | Manhole 132 - West State Road 46 near Ellettsville | Precipitation event caused non permitted untreated release from manhole to surrounding ground. | Engineers are working on a plan/design to correct overflow problem. | SSO Reached Public Land
| 36348 | Non permitted | Eastern Richland Sewer Corporation | Monroe | 2013-04-19 03:00 | 2013-04-19 07:00 | 2013-04-22 08:57 | 0 |  | Manhole 169 - Hartstrait Road | Precipitation event caused an unpermitted untreated release from a manhole to surrounding ground. | Currently looking at the lines to determine source of infiltration so that it may be corrected. | SSO Reached Public Land
| 36349 | Non permitted | Eastern Richland Sewer Corporation | Monroe | 2013-04-19 03:00 | 2013-04-19 07:00 | 2013-04-22 08:57 | 0 |  | Manhole 112 - Highway 46 near the Linday Hayes Trailer Courts | Precipitation event triggered unpermitted untreated release from manhole to surrounding ground. | We are currently looking at the lines to determine source of infiltration so that it may be corrected. | SSO Reached Public Land
| 43516 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 06:00 | 2013-12-22 06:30 | 2013-12-23 11:14 | 0 |  | MH 129-1 Pullers Park 4747 West State Rd 46 | Rain 5 inches for both MH: The rainfall fell very heavy and hard and lasted for almost w solids days. the entire town was flooded and they lost power in most areas. | See Report
| 43513 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 06:00 | 2013-12-22 06:30 | 2014-12-23 11:15 | 0 |  | MH-1383 Hayes Trailer Park off Hwy 46 Ground | Rain 5 inches For both MH: the rainfall fell very heavy and hard and lasted for almost 2 solids days. The entire town was flooded and they lost power in most areas. | See Report
| 43514 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 06:00 | 2013-12-22 06:30 | 2013-12-23 11:15 | 0 |  | MH 128 Pullers park 4747 West State 46 ground | 5 inches for both MH; The rainfall fell very heavy and hard and lasted for almost 2 solid days. the entire town was flooded and they lost power areas. | See Report
| 43511 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 06:00 | 2013-12-22 06:30 | 2013-12-23 11:15 | 0 |  | MH 111- HayesTrailer Park off HWY 46 Ground | Rain 5 inches For both MH: the rainfall fell very heavy and hard and lasted for almost 2 solid says. The entire town was flooded and they lost power in most areas. | See Report
| 43478 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 06:00 | 2013-12-22 06:30 | 2013-12-23 11:15 | 0 |  | MH 129 - Putters park 4747 West State Rd 46 | Rain 5 inches for MH 129: The rainfall fell very heavy and hard-and lasted for almost 2 solid days. The entire town was flooded and they lost power in most areas. | See Report
| 43466 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 10:00 | 2013-12-21 11:00 | 2013-12-23 11:15 | 0 |  | MH 1666-4499 W State Rd 46 and Outback Road Ground | Rain 5 inches For MH 1666: The rainfall fell very heavy and hard-and lasted for almost 2 solid days. This manhole actually overflowed twice. early in the morning stopped an then again in the evening-only when rainfall was at it s heaviest. The entire town was flooded and they lost power in most areas. | Rain 5 inches | SSO Affected Private Property
| 43467 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 19:30 | 2013-12-22 06:00 | 2013-12-23 11:15 | 0 |  | MH 1666 4499 W State Rd 46 and Outback Road Ground | Rain 5 inches for MH 1666: the rainfall fell very heavy and hard-and for almost 2 solid days. this manhole actually overflowed twice. early in the morning stopped and then again in the evening- only when rainfall was at it s heaviest. The entire town was flooded and they lost power in most areas. | See Report
| 43469 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 19:30 | 2013-12-22 06:00 | 2013-12-23 11:15 | 0 |  | MH 1185-4499 W State Rd 46 and Outback Road Ground | Rain 5 inches for MH 1185: The rain fall fell very and hard -and lasted for almost 2 solids days. This manhole actually overflowed twice early in the morning stopped and then again in the evening - only when rainfall was at it s heaviest. the entire town was flooded and they lost power in most areas. | See Report
| 43468 | Non Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 22:00 | 2013-12-21 23:00 | 2013-12-23 11:15 | 0 |  | MH 1185 - 4499 W State Rd 46 and Outback Road Ground | Rain 5 inches for MH 1185: the rainfall fell very heavy and hard-and lasted for almost 2 solid days. this manhole actually overflowed twice early in the morning-only when rainfall was at it s heaviest. The entire town was flooded and they lost power in most areas. | See Report
| 43508 | Non-Permitted | Eastern Richland Sewer Corporation | Monroe | 2013-12-21 06:00 | 2013-12-22 06:30 | 2013-12-23 11:15 | 0 |  | MH 115 Hayes Trailer Park off Hwy 46 | Rain 5 inches For MH 115: The rainfall fell very heavy and hard- and lasted for almost 2 solid days. The entire town was flooded an they lost power in most areas. | See Report
42934 | 35229 | IN0020524 | WAYNETOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-01-13 10:15 | 2013-01-13 23:59 | 2013-01-14 08:42 | 1000 | gallons | Manhole #2 Waynetown IN | Relay failure in level control in Manhole #2 resulted in an Untreated Release to Receiving waters | Area of Spill will be cleaned | SSO Reached Receiving Water | East Fork Coal Creek
42934 | 36751 | IN0020524 | WAYNETOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-18 19:30 | 2013-04-19 19:00 | 2013-04-22 10:15 | 11500 | gallons | Manhole #2 Field in creek bottom. | Untreated Release Rain 4 inches Receiving area is hay field manhole #2 is along street approx 100yds from coal creek this is second page denoting end of relapse. | Will clean area when possible. | SSO Affected Private Property
42934 | 36292 | IN0020524 | WAYNETOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-18 19:30 |  | 2013-04-18 21:10 | 0 |  | Manhole #2 | Precipitation event triggered untreated release from manhole to surrounding ground and unnamed recieving waters. |  | SSO Reached Receiving Water
43120 | 42368 | IN0022721 | DARLINGTON MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-12-09 09:00 | 2013-12-09 15:15 | 2013-12-10 07:05 | 0 |  | Darlington WWTP Chlorine Contact Tank | Broken air diffuser in chlorine contact tank (Frozen Valve) | Moved valve on top of chlorine contact tank. |  | Honey Creek
43066 | 36081 | IN0023418 | LADOGA MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-18 | 2013-04-21 | 2013-04-23 10:34 | 0 |  | Manhole 48 Manhole 50 Manhole 72A Manhole 103 | Untreated release Rain 5.2 inches Rain causing heavy flooding in county. |  | SSO Affected Private Property
43066 | 36654 | IN0023418 | LADOGA MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-24 09:15 | 2013-04-25 | 2013-04-25 09:39 | 0 |  | Manhole 48 50 and 103 | Precipitation event(s) caused untreated release from multiple manholes to an unnamed stream. |  | SSO Reached Receiving Water
43066 | 37771 | IN0023418 | LADOGA MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-06-04 14:00 | 2013-06-05 | 2013-06-07 14:02 | 0 |  | No release cleaning secondary clarifier. | No Release Cleaning Secondary Clarifier. Employee cleaning secondary clarifier. running flow thru both rock and plastic filter. Operator contacts Vac Company to help clean tank and grit channels.
40084 | 36545 | IN0032964 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-19 01:36 | 2013-04-19 12:00 | 2013-04-20 10:46 | 1500 | gallons | Mill Street ManholeSoth Water Streeet ManholeIndustrial Boulevard ManholeWWTP | Precipitation event caused area flooding resulting in receiving water backing up into WWTP and backing up/flooding the sewer collection system. Untreated release from WWTP and collection system to surrounding grounds storm sewers and receiving waters. | No real action taken. Everything in flooded in collection system. Confirmed operation of all lift stations and maximized flow to and through WWTP. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water; Storm Sewer | Sugar Creek
40084 | 36546 | IN0032964 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-19 06:00 | 2013-04-19 15:00 | 2013-04-20 10:45 | 0 |  | Covington Street Plant Discharge Manhole | Precipitation event caused flooding and partially treated release from WWTP. Flooding cause creek to back up into plant where it blew off the discharge manhole lid. | Released effluent was blended with final effluent and sampled prior to release to receiving water. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Sugar Creek
40084 | 36074 | IN0032964 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-19 06:00 | 2013-04-20 07:00 | 2013-04-23 13:51 | 6000000 | gallons | Covington Street Plant Discharge Manhole Sugar Creek. | Partially Treated Release Blended with Final Effluent & Sampled Rain 3.84 inches. Sugar Creek exceeded flood stage and backed up into final effluent sewer main. | Limited access to area so that no one entered manhole/sewer. | SSO Reached Receiving Water | Sugar Creek
40084 | 36221 | IN0032964 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-19 07:00 |  | 2013-04-19 10:05 | 0 |  | Final effluent of treatment plant to Sugar Creek | Precipitation event(s) caused flooding fromvSugar Creek into the WWTP. The blower building has >1 of water near the blower and the UV disinfection system was flooded. Untreated release bypass of treatment process. Some partially treated release. | Have installed flood gates on plant blower system off to prevent electrical damage. UV off to address electrical issues. Working to get water levels down and electrical repairs completed. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Sugar Creek
40084 | 36044 | IN0032964 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-19 07:00 |  | 2013-04-23 13:50 | 6000000 | gallons | Final Effluent of Treatment Plant UV System Down Sugar Creek | Untreated Release Partially Treated Release Bypass of a Treatment Process Blended with final Effluent & Sampled Rain 3.84 inches. Heavy rains this week totaling >6 have resulted in the flooding of Sugar Creek into the treatment plant. Aeration and clarifier systems flooded and UV disinfection equipment flooded and damaged. | Repairing UV banks using chlorine tabs as a back up until equipment repaired. Hoping to have UV system working by 5/1/13 | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Sugar Creek
40084 | 40371 | IN0032964 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-09-25 07:15 | 2013-09-25 08:30 | 2013-09-25 09:29 | 0 |  | 900 & 904 Cottage Street | Lift Station went down sewage went into 900 & 904 Basements. 900 3 inches of sewage 904 12 inches of sewage. | Repaired Pump StationSee Report | SSO Basement Backup
40084 | 42334 | IN0032964 Outfall 005 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-12-05 14:00 | 2013-12-05 17:30 | 2013-12-06 10:30 | 0 |  | Manhole at junction of IN-47 & IN - 33 | Equipment Failure Grease Blockage | Removed Blockage See Report | SSO Reached Public Land
40084 | 40655 | IN0032964 Outfall 005 | CRAWFORDSVILLE WASTE WATER TREATMENT PLANT | Montgomery | 2013-10-01 14:45 | 2013-10-01 15:15 | 2013-10-01 11:30 | 0 |  | 801 North Street | Construction Rrelated Manhole 2.45pm called in 3:15pm open then we opened her lateral | Removed Blockage See Report | SSO Basement Backup
43081 | 35534 | IN0040274 | LINDEN MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-01-13 16:30 |  | 2013-01-14 15:02 | 130000 | gallons | Overflow pipe in EQ basin at WWTP. | Precipitation event and snow melt combined to cause and untreated release from an EQ Basin to receiving waters. | Will process total volume in EQ Basin following lessening of hydraulic surge. Facility awaiting funding to start plant upgrade. | SSO Reached Receiving Water | Stoddard Ditch
43081 | 36387 | IN0040274 | LINDEN MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-18 20:51 | 2013-04-21 16:00 | 2013-04-22 12:13 | 600000 | gallons | Town of Linden WWTP | Precipitation event caused an Equalization Tank overflow and a partially treated release to receiving waters | Equalization tank shuts of aeration prior to overflow allowing material to settle out.Facility waiting for funding for upgrade. | SSO Reached Receiving Water | Stoddard Ditch; Wabash River; Wea Creek
43081 | 36484 | IN0040274 | LINDEN MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-18 21:51 | 2013-04-19 04:30 | 2013-04-19 14:45 | 0 |  | Equaliztion tank overflow at WWTP | Inflow from precipitation event resulted in partially treated release from WWTP to receiving waters | Equalization tank shuts off aeration prior to overflow allowing material to settle out.facility waiting for funding for upgrade. | SSO Reached Receiving Water | Stoddard Ditch; Wabash River; Wea Creek
43084 | 37377 | IN0040711 | LITTLE RACCOON REGIONAL WASTE DISTRICT | Montgomery | 2013-06-01 20:00 | 2013-06-02 19:30 | 2013-06-04 08:16 | 50000 | gallons | Lift Station #4 upon land on Highway 59 stream next to LS #4 | Power Failure Equipment Failure I was not aware there was an over flow until Aaron Teeter called me at 4:00 pm 6-3-13. I called Kirk Rewurts sewer maintenance for Little Raccoon. He said he was having electrical maintenance done on one of the pumps controls. And only had one in operation. Storm and power outage tripped the other pump off. He forgot to call me. | Spray area with bleach. | SSO Affected Private Property
40053 | 35820 | IN0040771 | WINGATE MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-14 | 2013-04-15 | 2013-04-15 13:13 | 5000 | gallons | Force Main Ground | Untreated Release Equipment Failure Broken Force Main Pipe. | Fixed treated ground with lime | SSO Affected Private Property
40053 | 36127 | IN0040771 | WINGATE MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-18 12:00 | 2013-04-19 | 2013-04-19 12:29 | 10000 | gallons | West Lift Station | Precipitation and main break resulted in untreated release to surrounding ground. | Treated affected area with lime. | SSO Reached Public Land
40053 | 36273 | IN0040771 | WINGATE MUNICIPAL WASTE WATER TREATMENT PLANT | Montgomery | 2013-04-24 06:00 | 2013-04-25 | 2013-04-24 12:42 | 5000 | gallons | West Lift Station Ground | Untreated Release Rain 2-8 inches Two inches of rain on top of the other 6 this month. | Pumped water on ground at west Lift Station will Ag Lime ground | SSO Affected Private Property
42745 | 39816 | IN0020303 | MARTINSVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Morgan | 2013-08-27 07:00 | 2013-08-27 10:36 | 2013-08-27 13:31 | 0 |  | Grassy fork lane/Shipeman Est. Lift Station | Power Failure Pump Station Failure Power failure at Lift Station | Repaired Pump Station | SSO Affected Private Property; SSO Reached Receiving Water
40093 | 35861 | IN0036820 | MORGANTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-01-13 03:00 | 2013-01-14 15:00 | 2013-01-14 15:44 | 4320 | gallons | 1st manhole upstream from 252 Lift Station | Precipitation event exceeded the maximum capabilities of lift station pumps resulting in untreated release from lift station to receiving waters. | Lift station pumps were checked and operating at maximum capacity. | SSO Reached Receiving Water | Long Run
40093 | 35214 | IN0036820 | MORGANTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-01-30 19:30 | 2013-01-30 21:30 | 2013-01-31 14:11 | 4000 | gallons | State Road 252 Lift Station Morgantown IN | Pump failure following a precipitation event resulted in an untreated release to receiving waters | Reset pumps in control panel. only one pump restored. service rep repaired second pump 1/31/2013 9:00 A.M. Check Lift Stations on a regular basis and more frequently during storm events. | SSO Reached Receiving Water | Long Run
40093 | 36040 | IN0036820 | MORGANTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-04-22 19:05 |  | 2013-04-23 12:40 | 1000 | gallons | SR 135 Lift Station Indian Creek | Untreated Release Construction Related Midwest Underground Co. was boring underground near lift station on SR135. They struck the Force Main coming out of the lift station. | Line was repaired | SSO Reached Receiving Water | Indian Creek
40093 | 43538 | IN0036820 | MORGANTOWN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-12-21 08:34 | 2013-12-22 16:47 | 2013-12-23 15:20 | 0 |  | ST RD 252 Lift Station Manhole | Rain 4.25 inches During routine check of lift station during storm the water level in the manhole was at full capacity. Both pumps running at full capacity. | See Report |  | Long Run
41076 | 35856 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-01-15 06:30 | 2013-01-15 11:30 | 2013-01-16 10:56 | 0 |  | Manhole #32 | Pump failure resulted in untreated release from manhole to receiving waters. | Have pump repaired. Cleaned around manhole and put down lime. | SSO Reached Receiving Water | White Lick Creek
41076 | 35207 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-01-30 06:30 | 2013-01-30 11:00 | 2013-01-31 09:13 | 0 |  | Manhole #76 Brooklyn IN | Precipitation event resulted in untreated release from manhole #76 to White Lick Creek | Clean site lime down. | SSO Reached Receiving Water | White Lick Creek
41076 | 35209 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-01-30 07:15 | 2013-01-30 11:45 | 2013-01-31 09:14 | 0 |  | Manhole #32 Brooklyn IN | Precipitation event resulted in untreated release from Manhole #32. | Clean site lime down. | SSO Reached Receiving Water | White Lick Creek
41076 | 34807 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-02-24 10:00 | 2013-02-24 12:30 | 2013-02-26 15:37 | 0 |  | Manhole #32 Lift Station | Removal and installation of old manhole lines released debris that clogged the lift station pump. | Removed pump cleaned out debris from it and reinstalled. cleaned site and put down lime. | SSO Reached Receiving Water | White Lick Creek
41076 | 34804 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-02-26 07:30 | 2013-02-26 19:00 | 2013-02-27 10:02 | 0 |  | Manhole #32 Lift Station Brooklyn IN | Clogged pump at manhole #32 caused backup/overflow | Pulled pump from lift station. Was plugged up with pieces of wood socks baby wipes. Removed debris and reinstalled pump. Rake and put down lime. Untreated release bypassed to White Lick Creek. | SSO Reached Receiving Water | White Lick Creek
41076 | 34928 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-03-18 08:00 | 2013-03-18 10:00 | 2013-03-19 12:55 | 0 |  | #32 White Lick Creek | Equipment Failure | Pulled pump replaced with new one raked and put lime down. | SSO Reached Receiving Water | White Lick Creek
41076 | 35538 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-04-05 08:30 | 2013-04-05 09:50 | 2013-03-05 11:55 | 0 |  | Ditch to Whitelick Creek | Main plugged up manhole was seeping. | Used vac truck cleaned main. | SSO Affected Private Property
41076 | 38230 | IN0039772 | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-07-01 13:30 | 2013-07-01 14:30 | 2013-07-02 08:19 | 0 |  | Manhole #76 | Rain 1 inch. Spectro Tech rehab manholes. | Spectro Tech repaired manholes at Country Manor. Plastic pieces got stuck in pumps. Pulled and cleaned pumps. | SSO Affected Private Property | White Lick Creek
41076 | 43536 | IN0039772 Water Body- W Lick | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-12-21 01:00 | 2013-12-21 22:00 | 2013-12-23 09:26 | 0 |  | #147 | Rain 5.75 inches and melting snow | See Report
41076 | 43537 | IN0039772 Waterbody Effected - W Lick | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-12-21 06:00 | 2013-12-21 09:00 | 2013-12-23 09:26 | 0 |  | #76 | Rain 5.75 inches and snow melting. | See Report
41076 | 43535 | IN0039772 Waterbody Impacted - W Lick | BROOKLYN MUNICIPAL WASTE WATER TREATMENT PLANT | Morgan | 2013-12-21 03:00 | 2013-12-21 18:30 | 2013-12-23 09:26 | 0 |  | #32 | Rain 5.75 inches & Melting Snow | See Report
41881 | 42403 | IN0049361- White River | FOXCLIFF ESTATES SUBDIVISION | Morgan | 2013-12-09 09:00 | 2013-12-09 14:00 | 2013-12-11 10:45 | 0 |  | Manhole off of Ramsgate Rd | Homeowner notice sewage overflowing out of a manhole then called the utility. This event was reported to the utility at 9:03am on December 9th 2013 | Removed Blockage See Report | SSO Affected Private Property
| 39430 | Terminated Permit | HOLIDAY INN EXPRESS | Morgan | 2013-07-19 13:30 | 2013-07-19 13:45 | 2013-07-19 13:30 | 0 |  | Sewer Lift Station 2233 Buran Lane | Equipment Failure | See Report | SSO Affected Private Property
51150 | 36473 | IN0039764 | BROOK MUNICIPAL WASTE WATER TREATMENT PLANT | Newton | 2013-04-19 03:00 |  | 2013-04-19 14:20 | 0 |  | Manhole on Canal Street | Precipitation event triggered untreated release from manhole to receiving waters. | Water only coming out of holes on lid. Expect to be stopped by evening. | SSO Reached Receiving Water | Jones Ditch
51150 | 37394 | IN0039764 | BROOK MUNICIPAL WASTE WATER TREATMENT PLANT | Newton | 2013-05-31 21:00 |  | 2013-06-01 10:51 | 0 |  | Manhole on Canal St. | Rain 9 inches 3.5 on Friday night in about 2 hrs manhole is 10 ft from flooded ditch. |  | SSO Affected Private Property
42946 | 35578 | IN0020664 | AVILLA MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-04-11 05:00 | 2013-04-11 06:45 | 2013-04-11 11:12 | 2000 | gallons | Manhole West of 4th St Lift Station main Lift Station at WWTP | Untreated release Equipment Failure Rain 1.25 inches Precipitation Related Equipment Failure at main lift station at pump. | Pumps at WWTP turned on by hand debris form overflow vacuumed up and disposed onto drying bed. Sanitary sewers are being inspected to determine source of I&I sump pumps are contributing to excess flow in collection system. Expert will be called in to inspect and repair controls at main LS at WWTP | SSO Affected Private Property; SSO Reached Receiving Water
42946 | 36145 | IN0020664 | AVILLA MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-04-18 19:00 | 2013-04-19 10:30 | 2013-04-19 13:01 | 13950 | gallons | Manhole west of 4th Street Lift Station | Precipitation event and I & I contribution resulted in untreated release from a manhole to receiving waters. | verfified pumps in lift station are pumping. Sanitary sewers are being inspected to determine source of I & I. Plans are underway to develop sump pump inspection program to remove sump pumps from sanitary sewers. | SSO Reached Receiving Water | Eli Creek
42946 | 36165 | IN0020664 | AVILLA MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-04-24 | 2013-04-24 07:15 | 2013-04-24 12:36 | 15000000 | gallons | Manhole west of 4th St Lift Station Eley Creek | Untreated Release Rain 1.5 inches Heavy rains and sump pumps contributing to high flow in collection system. | Verified pumps in lift station are running properly. Sanitary sewer are being inspected to determine source of I&I. Plan are underway to develop sump pump inspection program to remove them from sanitary sewer. | SSO Reached Receiving Water
42946 | 36748 | IN0020664 | AVILLA MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-05-01 19:00 | 2013-05-01 22:30 | 2013-05-02 15:00 | 2100 | gallons | Manhole west of 4th Street Lift Station | Transformer went short and damaged pump controls not allowing the generator to operate the pumps. Result was an untreated release from a manhole to receiving water. | Parts replaced to bring lift station back online and normal operation. | SSO Reached Receiving Water | Eli Creek
42946 | 37603 | IN0020664 | AVILLA MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-06-01 03:00 | 2013-06-01 09:00 | 2013-06-03 09:59 | 20000 | gallons | Manhole West of 4th St. Lift Station | Rain 3.0 inches Manhole Heavy rains in short period contributed to overflow. Sump pumps contributing to excess flow. | Made sure Lift Station pumps were working to capacity. Studying system to indentify source s of I&I. | SSO Reached Receiving Water
42946 | 39921 | IN0020664 | AVILLA MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-11-17 21:40 | 2013-11-17 21:45 | 2013-11-18 10:56 | 0 |  | Manhole west of 4th St Lift Station | Power Failure Power failure at Lift Station | See Report | SSO Reached Receiving Water | Eley Ditch
42946 | 43539 | IN0020664 | AVILLA MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-12-21 21:00 | 2013-12-22 | 2013-12-22 21:29 | 0 |  | Man hole West of 4th st Lift Station | Rain 1.6 inches Heavy rains and snow melt contributed to overflow. | See Report | SSO Reached Receiving Water | Eley Ditch
43103 | 34569 | IN0021814 | CROMWELL MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-03-10 13:30 | 2013-03-10 15:30 | 2013-03-11 12:42 | 14583 | gallons | Cromwell WWTP Solomon Creek | Untreated Release Equipment Failure The loss of solids stopped within 15min of the discovery. | On Sunday March 10th the weekend operator discovered the west Clarifier was losing solids over 1/2 of it s effluent weir. The Enot Clarifier was okay. Flow was stopped and the return was increased slightly and sludge was washed. Flow was returned after completing wasting sludge. | SSO Reached Receiving Water | Solomon Creek
43103 | 36322 | IN0021814 | CROMWELL MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-04-19 21:00 | 2013-04-19 16:00 | 2013-04-20 11:48 | 60000 | gallons | C-1 Rail Road Spare | Rain 3 inches | Insured all the equipment was operating. | SSO Affected Private Property
43103 | 42456 | IN0021814 Outfall 001 | CROMWELL MUNICIPAL WASTE WATER TREATMENT PLANT | Noble | 2013-12-12 15:10 | 2013-12-12 15:30 | 2013-12-13 09:42 | 0 |  | 4525n 860W | Equipment Failure December 12 2013. On the morning of Dec 12th 2013 discovered the shear pin on the East Clarifier had broken. At this point some light gassing solids ere rising to the surface but was not causing any problems with the effluent. All the flow was then diverted to the West Clarifier and we began draining the East clarifier to inspect it and fix any issue. During the time period of 3:10pm and 3:30pm our flow was beyond the capacity of the West Clarifier. The sludge blanked was at 8 feet leaving about 3 to 4 feet of treated water on the top. i had left the clarifier at 3:10 the flow rate was creating turbulence and a mixture of treated water and biosolids were passing over the effluent weir. The flow was immediately stopped and the sludge blanket was allowed to go down thru the return sludge before we could begin to discharge again. The cause of the East clarifier failure is a large thrust bearing that carries the bottom screed equipment . | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Solomon Creek
42841 | 36341 | IN0022144 | Albion Municipal Waste Water Treatment Plant | Noble | 2013-04-19 | 2013-04-20 01:00 | 2013-04-22 08:43 | 0 |  | Town of Albion WWTP SSO #2 | Precipitation event triggered bypass of treatment process to receiving waters. |  | SSO Reached Receiving Water | Croft Ditch
42841 | 36655 | IN0022144 | Albion Municipal Waste Water Treatment Plant | Noble | 2013-04-24 00:30 | 2013-04-24 20:00 | 2013-04-25 10:05 | 0 |  | Overflow to SSO #2 at WWTP | Precipitation event(s) triggered WWTP overflow bypassing treatment process to receiving water. |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Croft Ditch
43363 | 35520 | IN0023582 | Ligonier City | Noble | 2013-03-31 09:05 | 2013-03-31 10:00 | 2013-04-04 07:54 | 0 |  | CSO #009 Cavin & Richmond Street Elkhart River | Untreated Release Sewer lines at the intersection of Cavin and Richmond Street are not of adequate size. | Back washing will be done at low flow periods to optimize pipe capacity. At this time a sewer separation project is under way. With the next 90 days (June 2013) CSO #009 will be closed. | SSO Reached Receiving Water | Elkhart River
43363 | 35516 | IN0023582 | Ligonier City | Noble | 2013-03-31 09:05 | 2013-03-31 10:00 | 2013-04-04 07:52 | 0 |  | CSO #9 Cavin & Richmond St. | Untreated Release Sewer lines at the intersection of Cavin and Richmond St are not of adequate size. | Back washing will be done at low flow periods to optimize pipe capacity. At this time a sewer separation project is under way. With the next 90 days (June2013) CSO #009 will be closed. | SSO Reached Receiving Water | Elkhart River
43363 | 36856 | IN0023582 | Ligonier City | Noble | 2013-05-12 03:00 | 2013-05-12 11:30 | 2013-05-14 07:02 | 0 |  | CSO #2 bypass vol. 7000 gallons Smith St Elkhart River | Untreated Release Sewer lines partially plugged due to dirt and grease. | Crew to clean line and schedule future preventative maintenance schedule future preventative maintenance. | SSO Reached Receiving Water | Elkhart River
43363 | 35512 | IN0023582 No visual observation will also be conducted on the receiving stream over the next 24 hours | Ligonier City | Noble | 2013-03-31 09:05 | 2013-03-31 10:00 | 2013-04-04 07:50 | 0 |  | CSO #9 Cavin & Richmond St Elkhart River | Untreated Release Sewer lines at the intersection of Cavin and Richmond Street are not of adequate size. | Back washing will be done at low flow periods to optimize pipe capacity. At this time a sewer separation project is under way. With the next 90 days (June 2013) CSO #009 will be closed. | SSO Reached Receiving Water | Elkhart River
44779 | 41767 | IN0038822 Outfall 001 | EAST SHORE CD BEAR LAKE SUB | Noble | 2013-11-05 09:30 | 2013-11-05 10:30 | 2013-11-12 16:00 | 0 |  | High Lake Vacuum Station #4 | Equipment Failure Vacuum pump seat failure caused vacuum station to be disabled. Alarm float switch was caught in debris and did not activate on-site emergency telemetry. For a brief period of time the lift station over-flow however spill did not leave the premises or reach High Lake. | Repaired Pump Station See Report
| 43540 | Terminated Permit | Turkey Creek Regional Sewer District | Noble | 2013-12-22 07:45 | 2013-12-22 07:45 | 2013-12-23 01:03 | 5000 | gallons | WWTP | 3 rain overnight. Flow up some light solids loss out of south clarifier only. Reajusted valve ok. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Cromwell Ditch
33179 | 37032 | IN0024431 | Rising Sun Municipal Utilities | Ohio | 2013-05-20 07:35 | 2013-05-20 07:50 | 2013-05-20 03:39 | 100 | gallons | MH #Y-1 grass field | Untreated Release Blockage in sewer line. | Jetted sewer main cleaned rags out of manhole. We will check line and manhole weekly. | SSO Affected Private Property
51171 | 37006 | IN0021601 | ORLEANS MUNICIPAL WASTE WATER TREATMENT PLANT | Orange | 2013-05-20 10:30 | 2013-05-21 02:15 | 2013-05-20 15:08 | 0 |  | Main Lift Station on McKinley St Transports Sewage to WWTP | Untreated release Equipment Failure At approximately 10:30am Orleans WWTP staff was doing daily tasks on computer SCADA and noticed the Mail Lift Station not pumping. staff drove to the Lift Station and it was non-responsive. | As it was decided the remaining pump in the Dry-Pit Main Lift Station was in failure Chris Simmons notified Town Superintendent Mike Dixon. ISI inc was contacted and began implementing a bypass procedure at 10:30am completed and online at 2:30pm. The town is awaiting shipment/completion for a new submersible pumping station to replace the current Lift Station. In the mean time the Town of Orleans had put a submersible pump into the main Lift Station wet well until construction can be completed. | SSO Affected Private Property
50376 | 35470 | IN0022951 | French Lick Municipal Waste Water Treatment Plant | Orange | 2013-01-14 13:00 | 2013-01-15 | 2013-01-15 06:07 | 50000 | gallons | Manhole at Sinclair Street next to CVS Pharmacy and the Storm Pond at the WWTP. | Precipitation event and snow melt combined to cause untreated release overflow from manhole and WWTP storm pond. | All lift station pumping at 100% capacity. Continue I/I and inflow study. | SSO Reached Public Land; SSO Occurred at Treatment Plant
50376 | 38913 | IN0022951 | French Lick Municipal Waste Water Treatment Plant | Orange | 2013-06-26 17:00 | 2013-06-26 23:00 | 2013-06-27 11:45 | 0 |  | Larry Bird Blvd (Manhole) | Liftstation was running at Max Capacity. Flash Flood Event. | Repairing manholes along Larry Bird Blvd that are receiving I/I. Continue ongoing I/I study. | SSO Reached Public Land
| 34784 | IN0024023 |  | Orange | 2013-03-16 07:00 |  | 2013-03-18 10:28 | 0 |  | Joseph Industry #004 Field app 1000 feet Lick Creek | Untreated Release Rain 2.07 inches Had .45 inches of rain on 3-16-13 followed by 1.62 inches of rain on 3-17-13 for a total of 2.07 inches in about 24 hours. | Will let site dry up and then clean up and apply lime to area. All pumps up an running. | SSO Affected Private Property; SSO Reached Receiving Water | Lick Creek
51141 | 34938 | IN0024023 | PAOLI MUNICIPAL WASTE WATER TREATMENT PLANT | Orange | 2013-03-18 07:00 | 2013-03-18 13:00 | 2013-03-19 10:22 | 0 |  | Joseph Industry #004 | Untreated Release Rain 2.07 inches Has .45 inches of rain on 3-16-13 followed by 1.62 inches of rain on 3-17-13 for total of 2.07 in about 24 hours. | Will let site dry up and then clean up and apply lime to area. All pumps up and running. | SSO Reached Receiving Water | Lick Creek
51141 | 38933 | IN0024023 | PAOLI MUNICIPAL WASTE WATER TREATMENT PLANT | Orange | 2013-06-26 18:00 | 2013-06-27 09:30 | 2013-06-27 10:08 | 0 |  | Joseph Industries Willowcreek Rd | Rain 3.35 inches Exceeded Max Capacity. 3.35 inches of rainfall pumps at sewer plant could not keep up. | See Report | SSO Reached Receiving Water | Lick Creek
51141 | 43543 | IN0024023 Outfall 004 | PAOLI MUNICIPAL WASTE WATER TREATMENT PLANT | Orange | 2013-12-21 09:00 | 2013-12-22 15:00 | 2013-12-23 11:44 | 50000 | gallons | Joseph Industries Willow Creek Road | Rain 3.75 inches 3.75 inches of rainfall last 24 hours. Plant can not keep with. | See Report | SSO Affected Private Property
50009 | 36287 | IN0024449 | ROCKVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Parke | 2013-04-18 16:29 | 2013-04-18 19:33 | 2013-04-19 06:10 | 3000 | gallons | Manhole #9. Highway 36 East ( East Ohio Street) | Partial obstruction of sewer main resulted in untreated release from manhole to surrounding ground and pave street. | No solids released. Jet truck used to open blockage and restore normal flow. Will check sewer main to make sure flow is normal. | SSO Reached Public Land; Paved Surface
50009 | 36784 | IN0024449 | ROCKVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Parke | 2013-04-19 08:00 | 2013-04-19 23:50 | 2013-04-20 09:56 | 1103 | gallons | Storm Basin Effluent outfall No# 101 to Outfall 001 to Williams Creek | Blended with Final Effluent & Sampled This is a follow up report to the 4-19-13 24 HR notice 1st report samples and tests were run as required. D.O. 9.2 / ammonia 0.53.PH 7.3/ E. Coli 120.7 TSS 8.3 CBOD not ready till 4-25-13 | All equipment was checked by staff for proper operation. When flow is down enough the storm pond will be returned through the plant to be treated. This will make room in basin for future flows. | SSO Affected Private Property; SSO Reached Receiving Water | Williams Creek
50009 | 36633 | IN0024449 | ROCKVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Parke | 2013-04-19 08:00 |  | 2013-04-19 13:37 | 616000 | gallons | Storm basin effluent outfall no 101 to outfall 001 to Williams Creek | Blended with Final Effluent & Sampled Rain 3.3 inches. Extremely wet conditions and heavy rainfall was the cause of the storm basin overflow to the plant effluent. Will send follow up report when overflow stops. | Plant staff made sure all pumps an equipment functioning properly. When plant flow reduces then the staff will return basin flow to plant and room in basin for future flow will be ready. | SSO Reached Receiving Water | Williams Creek
50009 | 36622 | IN0024449 | ROCKVILLE MUNICIPAL SEWAGE TREATMENT PLANT | Parke | 2013-04-24 15:00 | 2013-04-24 23:30 | 2013-04-25 09:58 | 810000 | gallons | Storm Basin to Receivin water Rockville WWTP | Flooding conditions caused by precipitation event(s) caused untreated release and release blended with final effluent from overflowing storm pond to outfall 101 to outfall 001 to receiving waters. | Plant staff made sure all pumps were functioning during the event. Full basin was returned 4/23/13. When plant flow reduces then the staff will return basin flow to the plant and room in basin for future flow will be ready. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Williams Creek
12067 | 35458 | IN0021016 | Tell City Sewage Treatment Plant | Perry | 2013-01-13 04:00 | 2013-01-13 09:00 | 2013-01-14 08:51 | 0 |  | basement at 131 Burglen Hills Drive | Precipitation event created excessive flows in collection system resulting in a residential basement untreated release. | Pumped down manhole to downstream manhole to clear the line. Rodded sewer line basement drained. No further action taken. | SSO Basement Backup
12067 | 34823 | IN0021016 | Tell City Sewage Treatment Plant | Perry | 2013-02-21 18:00 | 2013-02-22 07:00 | 2013-02-22 11:40 | 500000 | gallons | CSO outlet. Station at 5th and Mozart in Tell City IN | Station failure at 5th and Mozart in Tell City caused and Untreated Release and Treatment Bypass situation for about 500000 gallons of wastewater. | This is a brand new station and so far the plant electrician has found nothing to cause the failure nor has Evapar who services the switch gear. Continuing to monitor and test the station to assure proper continuing operation. | SSO Reached Receiving Water | Ohio River
12067 | 35540 | IN0021016 | Tell City Sewage Treatment Plant | Perry | 2013-04-03 19:00 | 2013-04-03 19:20 | 2013-04-04 08:15 | 500 | gallons | Manhole Unnamed ditch to Windy Creek | Untreated Release Equipment Failure Overflow was contained in a dry ditch and the entire overflow was cleaned up with the City s Vactor truck. A Blocked line was leaned and flow was restored quickly. | Spill was cleaned up right away and line was cleaned. Increase monitoring of this line to make sure flow is not restricted. | SSO Reached Receiving Water | Windy Creek
12067 | 35490 | IN0021016 | Tell City Sewage Treatment Plant | Perry | 2013-04-10 13:00 | 2013-04-10 13:20 | 2013-04-10 16:25 | 2000 | gallons | Air Release valve pit Ground | Untreated Release Construction Related Preventative maintenance was being conducted on the Branchville Force Main. Crews were replacing air release valves on the main. The valve broke off and flooded the manhole and surrounding area by the track field at Perry Central School. Opening was temporarily plugged until full repairs can be made. | We were in the process of making preventative repairs to keep this from happening in the first place. Crews are replacing all air release mains due to the age of the system. | SSO Affected Private Property
12067 | 41736 | IN0021016 | Tell City Sewage Treatment Plant | Perry | 2013-11-07 08:00 | 2013-11-07 10:00 | 2013-11-07 11:45 | 0 |  | On Branchville Correctional FacilityGrounds | Unknown Tell City crews discovered the overflow condition during routine pump checks this morning. The City s lift station had pumped its normal volume so the overflow must have just started around 8:00am when the station was being inspected. The City worked with Branchville Correctional Facility and restored flow using the City s jet rodding equipment. | Removed Blockage | SSO Affected Private Property
12067 | 42538 | IN0021016 | Tell City Sewage Treatment Plant | Perry | 2013-12-16 | 2013-12-16 20:00 | 2013-12-17 13:34 | 0 |  | 1800 Block alley between 12 & 13 | Pump station was accidently left off during routine maintenance. Station was powered back on and the alley was vacuumed clean and hosed down. | See Report | SSO Affected Private Property
59784 | 41699 | IN0024945 - Terminated | Branchville Correctional Facilities | Perry | 2013-11-07 08:15 | 2013-11-07 10:15 | 2013-11-07 11:15 | 0 |  | 21390 Old State Road 37 | Unknown Facility main sewer line was obstructed just prior to Tell City Lift Station. | Remove Blockage See Reports | SSO Reached Receiving Water | Oil Creek
61685 | 36798 | INM062901 | CANNELTON MUNICIPAL SEWAGE TREATMENT PLANT | Perry | 2013-03-11 13:30 |  | 2013-03-11 14:28 | 0 |  | Force Main on River Road in Tell City | Break in the force main carrying sewage from Cannelton to Tell City results in an untreated release to surrounding ground. | Called for emergency locates and contractor to make repairs asap. | SSO Reached Public Land
61685 | 34446 | INM062901 | CANNELTON MUNICIPAL SEWAGE TREATMENT PLANT | Perry | 2013-03-11 13:30 | 2013-03-13 10:30 | 2013-03-11 14:28 | 0 |  | Force Main on River Rad in Tell City IN | Untreated Release Equipment Failure | This is a follow up report to the one that I sent to you on 3-11-13. The force is ductile iron and the sewer gas is eating the top out of it. It took so long to make repairs this time because every time we thought we were done there would be another crack exposed after we turned on the pumps. We finally installed 32 feet of c900 and noticed no leakage.We are in the process of applying for a CFF Grant to change some of the force main with a polyethylene pipe but I was told that we won t here about the grant until this August. | SSO Affected Private Property
52122 | 34773 | IN0040789 | WINSLOW WATER TREATMENT PLANT | Pike | 2013-03-18 08:00 | 2013-03-21 | 2013-03-18 09:01 | 50 | gallons | Manhole 142 Winslow IN 467598 | Untreated Release 2 inches Rain | Will clean up to the best of our ability when flow stops. Seeking financial help to alleviate II problems | SSO Reached Receiving Water | Patoka River
50960 | 35649 | IN0020061 | HEBRON MUNICIPAL WASTE WATER TREATMENT PLANT | Porter | 2013-04-11 08:00 | 2013-04-11 10:00 | 2013-04-11 17:01 | 5000 | gallons | Notification Tower Box Stream via Swale | Partially Treated Release Rain 2.5 inches Observed boxes on towers overflowing immediately reduced recirculation flow to towers which stopped flow. Monitored area throughout day observed no other problems. Contacted Nick Ream va phone at 12:12pm to inform. | Water was treated and since it was mixing with rain/runoff did not further try to treat. We are looking into an alarm to notify us in case of high water in boxes. Will be investigating I&I | SSO Affected Private Property
50960 | 37858 | IN0020061 | HEBRON MUNICIPAL WASTE WATER TREATMENT PLANT | Porter | 2013-06-12 21:30 | 2013-06-12 23:30 | 2013-06-13 12:16 | 48000 | gallons | Monroe Lift Station Lift Station #3 | Untreated Release Power Failure Rain 1.75 inches | Installed portably generator. Need to install a bypass and transfer switch for generator. | SSO Affected Private Property
12069 | 41064 | IN0022578 | CHESTERTON UTILITIES WASTE WATER TREATMENT PLANT | Porter | 2013-10-15 06:00 | 2013-10-15 06:30 | 2013-10-15 14:20 | 0 |  | West side of 5th St at intersection with Pope-O Conner Ditch | A 2 PVC force main developed a longitudinal crack 4 under ground. | See Report | SSO Reached Receiving Water | O Conner Ditch
12069 | 39194 | IN0022578 - Info sent in of Noncompliace Notification Form | CHESTERTON UTILITIES WASTE WATER TREATMENT PLANT | Porter | 2013-06-26 08:00 | 2013-06-26 09:50 | 2013-06-26 15:54 | 0 |  | Bypass at Treatment Plant | There was not a non-compliance event. This fax is to notify you of a wet weather bypass at the WWTP. The flow was 11.4 MGD into the plant at the time of the bypass the plant is rated at 10MGD peak. The bypass was from 8:00am to 9:50am 1.59 of rain fell from 6:30 am to 8:30am. |  | SSO Occurred at Treatment Plant
12069 | 42229 | IN0022578 Outfall 001 | CHESTERTON UTILITIES WASTE WATER TREATMENT PLANT | Porter | 2013-12-01 14:00 | 2013-12-01 14:30 | 2013-12-02 12:10 | 0 |  | Manhole M7-10 on gravity sewer on Woodllawn Dr Street Surface | Obstructed Gravity Sewer Main | See Report | SSO Affected Private Property
12074 | 35776 | IN0024368 | Portage Waste Water Treatment Plant | Porter | 2013-01-17 19:30 | 2013-01-17 20:00 | 2013-01-18 12:48 | 10 | gallons | 6165 Lute road | Obstructed sewer main line resulted in untreated release into residential basement. | Jetted main line and removed blockage. Televised the main line and found some root infiltration. We will continue to monitor and root cut the 8 main. Slip line the 8 main in the future. | SSO Basement Backup
12074 | 34460 | IN0024368 | Portage Waste Water Treatment Plant | Porter | 2013-03-12 14:00 | 2013-03-12 14:30 | 2013-03-18 15:03 | 100 | gallons | Woodland Village Portage IN 46368 ground | Untreated Release Block w/grease and debris. | Open Clogged line by using combo jet truck notify residence of what not to put into out system also make this a bi-weekly trouble spot. | SSO Affected Private Property
12074 | 37007 | IN0024368 | Portage Waste Water Treatment Plant | Porter | 2013-04-19 17:15 | 2013-04-19 17:45 | 2013-04-20 02:27 | 0 |  | 2885 Bry and T Ground | Untreated Release Collapsed line due to a void over the 15 main line. | Begin bypass pumping to the nearest manhole to avoid any further SSO that may occur. Report attached. | SSO Affected Private Property
12074 | 36423 | IN0024368 | Portage Waste Water Treatment Plant | Porter | 2013-04-19 17:15 | 2013-04-19 17:45 | 2013-04-20 14:20 | 0 |  | 2885 Bryandt | Collapsed line due to a void over the 15 main line. Untreated release to surrounding ground | Begaun by-pass pumpint to the nearest mahole to avoid any further SSO that may occur. Contractor called to make repairs. Line monitored while repairs were completed. | SSO Affected Private Property
12074 | 40149 | IN0024368 | Portage Waste Water Treatment Plant | Porter | 2013-08-01 08:00 | 2013-08-01 09:30 | 2013-09-11 15:18 | 0 |  | House lateral 2111 Kennedy St Basement | Found a main line was blocked with grease and debris. | Removed Blockage See Report | SSO Basement Backup
12074 | 39660 | IN0024368 | Portage Waste Water Treatment Plant | Porter | 2013-08-01 08:00 | 2013-08-01 09:30 | 2013-08-26 13:17 | 0 |  | 2111 Kennedy St Basement | Found a main line was blocked with grease and debris. | Removed Blockage See Report | SSO Basement Backup
12074 | 42303 | IN0024368 Outfall 001 | Portage Waste Water Treatment Plant | Porter | 2013-12-02 14:48 | 2013-12-02 14:48 | 2013-12-04 14:07 | 0 |  | 1927 Jackson St | Unknown Clogged sewer main caused back-up in basement. We were not notified until 1.26pm on 12-03-2013 | Removed Blockage See Report | SSO Basement Backup
50989 | 35579 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-04 10:30 | 2013-01-04 11:45 | 2013-01-07 11:30 | 10 | gallons | 1652 Patoka Court | Residential sewer line blockage resulted in untreated release into residential basement. | Sewer Department cleaned main in front of residence and found no obstruction/blockage. Notified homeowner who will contact a plumber ASAP to clean the residential line. | SSO Basement Backup
50989 | 35680 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-08 06:45 | 2013-01-08 07:40 | 2013-01-15 15:55 | 10 | gallons | 658 Bond Avenue | Basement back up. Untreated release | Sewer Dept. cleaned main sewer line and found no blockage. Notified homeowner who will contact a plumber ASAP to clean out residence sewer line. | SSO Basement Backup
50989 | 35676 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-10 06:30 | 2013-01-10 08:00 | 2013-01-17 16:42 | 7 | gallons | 906 Jefferson Street | apparent blockage resulted in untreated release into residentil basement | Sewer Dept. cleaned main sewer line and found no blockage. Notified homeowner who woll call a plumber ASAP to clean residence sewer line. | SSO Basement Backup
50989 | 35674 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-11 14:30 | 2013-01-11 15:30 | 2013-01-15 16:30 | 10 | gallons | 805 Oak Street | Untreated release into residential basement | No obstruction in main sewer line. Notified homeowner. Homeowner will contact plumber ASAP to clean residence sewer line. | SSO Basement Backup
50989 | 35673 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-11 15:45 | 2013-01-11 16:46 | 2013-04-19 13:12 | 2 | gallons | 1306 Institute Street | Apparent blockage resulted in untreated release into residential basement. | Sewer Dept. cleaned 10 private sanitary sewer and found no obstructions/blockage. Notified homeowner who will call plumber ASAP to clean residence sewer line. | SSO Basement Backup
50989 | 35675 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-14 21:10 | 2013-01-14 22:15 | 2013-01-17 16:44 | 2 | gallons | Industrial Revolution Restaurant 1084 Linwood Avenue | Apparent blockage resulted in untreated release into restaurant | Sewer Dept. found no obstruction/blockage and reported findings to restaurant manager. Plumber had been on site earlier to clean the restaurant sewer lines. Manager will recall the plumber to try again. | SSO Basement Backup
50989 | 35677 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-15 12:47 | 2013-01-15 13:30 | 2013-01-17 16:50 | 10 | gallons | 213 Elmhurst Avenue | Untreated release into residence basement | Sewer Dept. cleaned main sewer and found no blockage. Notified homeowner who will call a plumber ASAP to clean residence sewer line. | SSO Basement Backup
50989 | 35678 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-16 07:00 | 2013-01-16 08:00 | 2013-01-17 16:53 | 25 | gallons | 804 Monroe Street | Apparent blockage resulted in an untreated release into a residential bath tub. | Sewer Dept. cleaned the main sewer and found no obstructions. Notified homeowner who will call a plumber ASAP to clean residence sewer line. | SSO Basement Backup
50989 | 35679 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-16 08:30 | 2013-01-16 09:00 | 2013-01-17 17:00 | 10 | gallons | 1652 Patoka Court | Apparent blockage resulted in untreated release into basement of residence | Sewer Dept. cleaned and televised main sewer line and found no blockages. Results reported to homeowner via telephone. Homeowner reported that a plumber had already been there to clean 60 feet of residence sewer but he was going to call him back to try again. | SSO Basement Backup
50989 | 35152 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-29 15:47 | 2013-01-30 07:30 | 2013-02-01 12:59 | 15 | gallons | 401 Academy Street Valparaiso IN | Residential basement backup | Cleaned sewer main and found no obstruction or blockage. Notified homeowner who has hired a plumber to clean the residence sewer line.. | SSO Basement Backup
50989 | 35150 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-29 20:00 | 2013-01-30 08:00 | 2013-02-01 13:14 | 0 |  | 507 Locust Street Valparaiso IN | Basement back upin residence. | Cleaned main sewer line and found no obstruction or blockage. Reported to homeowner who has called a plumber to clean sewer line for residence. | SSO Basement Backup
50989 | 35151 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-29 22:00 | 2013-01-30 06:30 | 2013-02-01 13:08 | 100 | gallons | 201 McKinley Street Valparaiso IN | Residential Basement Backup | Cleaned main sewer line and found no blockage or obstruction. Homeowner calling a plumber to have residence sewer line cleaned | SSO Basement Backup
50989 | 35112 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-30 | 2013-01-30 11:45 | 2013-02-01 13:25 | 0 |  | 1416 Del Vista Drive Valparaiso IN | Basement back up. | Cleaned city sewer in front of residence. Found no blockages. Notified homeowner who will call a plumber ASAP to resolve the back up. | SSO Basement Backup
50989 | 35148 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-30 14:00 | 2013-01-30 14:30 | 2013-02-01 13:18 | 10 | gallons | Ivy Boutique 23 Washington Street Valparaiso IN | Evidence of past basement back up. | Found evidence of previous back up. Cleaned main line and found no obstruction/blockage. Owner has contacted a plumber to clean the sanitary sewer line for the business. | SSO Basement Backup
50989 | 35006 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-31 11:30 | 2013-01-31 12:45 | 2013-02-04 09:40 | 10 | gallons | Basement floor drain at 405 Calumet Avenue | Residential basement back up. | No blockage/obstruction found in main sewer line. Advised homeowner. He will call a plumber to have resindence sanitary sewer line cleaned. | SSO Basement Backup
50989 | 35002 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-01-31 11:53 | 2013-01-31 11:53 | 2013-02-04 09:45 | 0 |  | Basement floor drain in residence 1418 Del Vista Drive. Valparaiso IN | Residential basement backup | Cleaned maain sewer line. No obstructions. Advised homeowner. He will contact plumber to have residential line cleaned ASAP. | SSO Basement Backup
50989 | 34929 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-02-11 18:10 | 2013-02-11 18:45 | 2013-02-13 14:51 | 1 | gallons | Basement backup of sanitary sewer at 2915 Lakepointe Drive in Valparaiso IN | Basement backup reported by homeowner | Homeowner cleaned up approximately 1 gallon of wastewater from around floor drain in basement. The sewer department cleaned the city sanitary sewer main within the road directly in front of the residence without finding any blockage or obstruction. Results reported to the homeowner who will call a plumber to clean the sanitary sewer line at the residence. | SSO Basement Backup
50989 | 34931 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-02-12 10:00 | 2013-02-12 11:30 | 2013-02-13 13:40 | 5 | gallons | 352 Marian Drive Valparaiso IN | Untreated release from residential sanitary sewer cleanout. | City sewer crew discovered that sanitary sewer clean out cap was not completely secured. Cleaned sanitary sewer main located in utility easement in the rear of the residential address and found no blockages or obstructions. Reported to homeowner who will call a plumber to clean the sanitary sewer service line. | SSO Affected Private Property
50989 | 34833 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-02-19 12:00 | 2013-02-19 12:45 | 2013-02-21 11:58 | 5 | gallons | 608 Indiana Avenue Valparaiso IN Bath tub. | Bathroom backup. Wastewater backing up in bath tub. | Cleaned city sewer main within the alley directly south of the residence located at 608 Indiana Ave. Did not find any blockage or obstruction. Homeowner is renting a rodding machine to clean the home sanitary sewer. | SSO Basement Backup
50989 | 34820 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-02-28 17:30 | 2013-02-28 19:00 | 2013-03-06 14:15 | 10 | gallons | 1607 McCord Drive Valparaiso IN | Basement backup at 1607 McCord Dr. | Homeowner contacting a plumber to clean the home s sanitary sewer line ASAP. No trouble found in municipal sewer lines. | SSO Basement Backup
50989 | 34822 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-02-28 19:30 | 2013-02-28 20:00 | 2013-03-06 14:25 | 2 | gallons | St. Theresa of Avila Church 1511 LaPorte Ave. Valparaiso IN. Lower Level floor drain. | Basement backup from lower level floor drain at St. Theresa of Avila Church 1511 LaPorte Avenue Valparaiso IN | No trouble found in city sewers. Office Manager at the church is calling a plumber to clean the church s sanitary sewer lines. | SSO Basement Backup
50989 | 35350 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-03-11 07:30 | 2013-03-11 09:00 | 2013-03-15 14:21 | 100 | gallons | The basement floor drain within the residence located at 405 Institute St. | Untreated release Private Sanitary Sewer Service Line The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 3-11-2013 at 8:15am that there I/was sanitary sewer wastewater coming through the basement floor drain within the home located at 405 Institute St. Upon arrival VCU_WRD Sewer Dept personnel observed approximately 100 gallon of sanitary sewer wastewater around the home s basement floor drain. The homeowner stated at this time to VCU-WRD Sewer Dept Staff that the homeowner had cleaned the sanitary sewer service line for the residence 3-12--13 | The VCU-WRD Sewer Dept cleaned the City sanitary/storm sewer combination main within the alley directly to the north of the residence locat4ed at 405 Institute St. The VCU-WRD Sewer Dept. personnel did not find any blockage/obstructions within the City sanitary/storm sewer combination main and reported these findings/observations directly to the homeowner. The homeowner stated to VCU-WRD Sewer Dept. Personnel that the homeowner will keep cleaning the sanitary sewer service line for the home located at 405 Institute St. | SSO Basement Backup
50989 | 35423 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-03-11 09:00 | 3/11/0013 11:00:00 | 2013-03-15 14:19 | 50 | gallons | The basement floor drain within the residence located at 1208 Campbell St. | Untreated Release Rain 0.01 The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer dept on 3-11-13 at 10:02am at there is/was sanitary sewer wastewater coming up through the basement floor drain within the residence located at 1208 Campbell St. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately fifty (50) gallons of sanitary sewer wastewater round the home s basement floor drain. | The VCU-WRD Sewer Dept. cleaned the City sanitary sewer main within the utility easement directly behind the residence located at 1208 Campbell St. The VCU-WRD Sewer Dept did not find any blockages/obstructions with the City sanitary sewer main and reported these findings/observation directly to the homeowner. The homeowner will contact a plumber to clean the sanitary service line for the residence located at 1208 Campbell St. | SSO Basement Backup
50989 | 35427 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-03-17 19:00 | 2013-03-17 21:00 | 2013-03-18 10:39 | 350 | gallons | The laundry room floor drain within the apartment building located at 1903 Chicago St | Untreated Released City Sanitary Sewer main Blockage/Obstruction. A tenant from the apartment building located at 1903 Chicago St stated in the original telephone sewer call to the VCU-WRD Sewer Dept. on the bottom floor of the apartment building. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately 350 gallons of sanitary sewer wastewater on the floor of the laundry room and the entrance to the apartment building. | The VCU-WRD Sewer Dept cleaned the City sanitary sewer main within the parking lot for an adjacent apartment building directly south of the apartment building located at 1903 Chicago St. VCU-WRD Sewer Dept. found a blockage/obstruction within the City sanitary sewer main and removed it. VCU-WRD Sewer Dept personnel further reported these findings/observations directly to the tenant who made the original telephone sewer call in the Department. The VCU-WRD Sewer Dept will televise the City sanitary sewer main that had the blockage/obstruction on 3-18-13 in order to confirm that the blockage/obstruction has been completely removed. if the blockage/obstruction has not been cleared from the City sanitary sewer main VCU-WRD Sewer Dept. personnel will clean sanitary sewer main ASAP until the main is cleared of debris. | SSO Basement Backup; SSO Affected Private Property
50989 | 35164 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-03-27 11:00 | 2013-03-27 12:15 | 2013-03-28 10:25 | 5 | gallons | The outside sanitary sewer service line cleanout for the residence located at 706 Parkside Ave. The ground around the outside sanitary sewer service line cleanout for the residence located at 706 Parkside Ave. | Untreated Release Private Sanitary Sewer Service Line Blockage/Obstruction The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 3/27/13 at 11:25AM that there is/was sanitary sewer wastewater pouring out of the outside sanitary sewer service line cleanout for the home located at 706 Parkside Ave. Upon arrival VCU-WRD Sewer Dept personnel observed approximately five (5) gallons of sanitary sewer wastewater around the home s outside sanitary sewer service line cleanout. Furthermore the homeowner was observed by VCU-WRD Sewer Dept. personnel trying to clean the home s sanitary sewer service line. | The VCU-WRD Sewer Dept cleaned and televised the City sanitary sewer main within the road directly in front of the residence located at 706 Parkside Ave. The VCU-WRD Sewer Dept. personnel did not find any blockage/obstructions within the City sanitary sewer main and reported these findings/observation directly to the homeowner. The homeowner will continue to clean the sanitary sewer line for at the residence located at 706 Parkside Ave. until the obstruction/blockage is removed from the home s sanitary sewer service line. | SSO Affected Private Property
50989 | 35542 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-01 10:30 | 2013-04-01 12:00 | 2013-04-04 10:27 | 50 | gallons | The basement floor drain within the residence located at 214 Roosevelt Rd. | Untreated Release Private Sanitary Sewer Service line Blockage/Obstruction The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 4-1-13 at 11:22am that there is/was sanitary wastewater backing up through the basement floor drain within the residence located at 214 Roosevelt Rd. Upon arrival VCU-WRD Sewer Dept. personnel observed the homeowner cleaning the homes sanitary sewer line. Furthermore the homeowner stated to VCU-WRD Sewer Dept personnel that there was approximately fifty (50) gallons of sanitary wastewater around the home s basement floor drain. | The VCU-WRD Sewer Dept cleaned the City sanitary sewer main within the road directly in front of the residence located at 214 Roosevelt Rd/ VCU-WRD Sewer Dept personnel did not find any blockages/obstruction within the City sanitary sewer main and reported these findings/observations directly to the homeowner. The homeowner will continue to clean the sanitary sewer service line for the home located at 214 Roosevelt Rd. until they have removed the blockage/obstruction form within the homes sanitary sewer service line. | SSO Basement Backup
50989 | 35666 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-05 19:33 | 2013-04-05 20:00 | 2013-04-10 09:22 | 0 |  | Unknown location within the basement for the residence located at 1303 Lafayette St | Untreated Release Private Sanitary Sewer Service Line Blockage/Obstruction The homeowner stated in the orginal email sewer call to the Utility Director of the VCU-WRD Sewer Dept on 4/5/2013 at 7:33pm that the basement floor is wet and the wetness appears to have com form the basement laundry room floor drain within the residence located at 131 Lafayette St. VCU-WRD personnel receive the call at 8:33am on 4-6-13. VCU-WRD didn t observe any wastewater around the basement floor drain. VCU-WRD did observe two wet spots on the basement floor carpet. Homeowner had no knowledge of the actual time and location from which the problem had occurred VCU-WRD personnel approximated that less then 5 gallons of wastewater had exited the home. |  | SSO Basement Backup
50989 | 35979 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-13 15:30 | 2013-04-13 17:00 | 2013-04-17 13:08 | 20 | gallons | 3351 Field Hawk Drive | Untreated release into residential basement. | Cleaned sewer in front of home. No obstruction or blockage found. Notified homeowner who will contact a plumber to clean residence sewer line. | SSO Basement Backup
50989 | 36070 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-16 11:00 | 2013-04-16 13:00 | 2013-04-18 15:44 | 500 | gallons | 158 Pine Street | Apparent private sanitary sewer service line blockage resulted in an untreated release into residential basement. Backup was clear water. | No obstructions or blockages found in main sewer line. Checked both upstream and downstream from residence. The homeowner will contact a plumber asap to check residence sewer line to determine source of clear discharge. | SSO Basement Backup
50989 | 36071 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-17 15:00 | 2013-04-17 14:15 | 2013-04-18 15:46 | 5 | gallons | 702 Albert Street | Untreated release into a residential basement. | No blockage or obstruction found in main sewer. Notified homeowner who will contact a plumber to have residence sewer line cleaned. | SSO Basement Backup
50989 | 36092 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-17 19:00 | 2013-04-17 21:00 | 2013-04-19 05:52 | 200 | gallons | 820 Jefferson Street | Basement backup. Clear water coming into residential basement through floor drain. | Found no blockages in sewer main. Notified customer who will contact plumber to get residential sewer line cleaned. | SSO Basement Backup
50989 | 36332 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-18 12:30 | 2013-04-18 14:00 | 2013-04-20 12:07 | 22600 | gallons | Three (3) basement floor drains within the residence located at 1508 Wood St. | Untreated Release Rain 0.7 inches The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 4-17-13 at 1:01 pm that there is/ was water coming up through every basement floor drain within the residence located at 1508 Wood St. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 110 gallons of clear water around three (3) basement floor drains within the residence. | The ACCU-WRD Sewer Dept cleaned the City sanitary sewer main within the road directly in front of the residence located at 1508 Wood St. VCVU-WRD Sewer Dept personnel did not find any blockages/obstructions within the City sanitary sewer main and reported these findings/observations directly to the homeowner. | SSO Basement Backup
50989 | 36328 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-18 20:45 | 2013-04-18 21:15 | 2013-04-20 11:54 | 20000 | gallons | The bathroom bathtub drain within the residence located at 1416 Del Vista Dr. | Untreated Release Rain 0.13 inches The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 4-18-13 are 9:06pm that there is/was sanitary wastewater coming up through the bathroom bathtub drain within the residence located at 1416 DelVista Dr. Upon arrival VCU-WRD Sewer Dept personnel did not observe any sanitary wastewater within the home s bathroom bathtub. The homeowner stated to VCU-WRD Sewer Dept. personnel that less than two (2) gallons of sanitary wastewater had come up through the bathroom bathtub and then flowed right back down the drain. | The VCU-WRD Sewer Dept. cleaned the City sanitary sewer main located within the road directly in from of the residence located at 1416 Del Vista Dr. VCU-WRD Sewer Dept personnel did not find any blockages/obstructions within the City sanitary sewer main and reported these findings/observations directly to the homeowner. The homeowner will contact a plumber ASAP in order to have the sanitary sewer service line cleaned for the residence located at 1416 Del Vista Dr. | SSO Affected Private Property
50989 | 36651 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-19 08:00 | 2013-04-19 17:00 | 2013-04-25 09:10 | 150 | gallons | 58 John Glenn Drive | Untreated release from an unknown source into a residential basement. | Cleaned combined sanitary/storm sewer in front of home. Found no blockage or obstruction. Notified homeowner who will contact a plumber to determine source of inflow and clean residence sewer line. | SSO Basement Backup
50989 | 36652 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-19 13:00 | 2013-04-19 13:45 | 2013-04-25 09:21 | 1000 | gallons | 604 Franklin Street | Untreated release into residential basement | Cleaned sanitary sewer main in front of home. No sign of blockage/obstruction. Notified homeowner who will contact a plumber to have residence sewer line cleaned. | SSO Basement Backup
50989 | 36653 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-04-20 10:30 | 2013-04-20 11:30 | 2013-04-25 09:25 | 0 |  | 353 Garfield Avenue | Untreated release into residential basement. | Cleaned sanitary sewer main in front of residence. Found no indication of blockage/obstruction. Notified homeowner who will contact a plumber to determine source of inflow and clean residential sewer. | SSO Basement Backup
50989 | 36877 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-05-13 07:45 | 2013-05-13 09:00 | 2013-05-15 14:53 | 6300000 | gallons | The basement cleanout within the residence located at 510 Franklin St. The basement floor drain within the residence located at 510 Franklin St. | Untreated Release The homeowner stated in the original telephone ewer call to the VCU-WRD Sewer Dept on 5-13-13 at 8:22am that there is/was sanitary wastewater coming out at wall where the pipe is a floor level and not at the floor drain Upon arrival VCU-WRD Sewer Dept personnel were unable to observe the amount or location of the back up within the residence due to the homeowner not being at home during the time of arrival. | The VCU-WRD Sewer Dept personnel cleaned the City sanitary sewer main within the road directly in front of the residence located at 510 Franklin St VCU-WRD Sewer Dept personnel did not find any blockages/obstructions within the City sanitary sewer main and reported these findings/observations directly to the homeowner through a telephone voicemail message. The homeowner did not return the telephone call back to the VCD-WRD Sewer Dept. | SSO Basement Backup
50989 | 36912 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-05-15 08:00 | 2013-05-15 09:00 | 2013-05-16 14:54 | 6250000 | gallons | The basement floor drain within the residence located at 510 Radle St. The basement floor drain within the residence located at 510 Randle St | Untreated Release Private Sanitary Sewer Blockage/Obstruction The owner of the Total Development Construction which is located at 510 Randle St stated in the original telephone sewer call to the VCU-WRD Sewer Dept on t5-15-13 at 8:16am that there is/was sanitary sewer wastewater coming up through the basement floor drain of the business (residential home). Upon arrival VCU-WRD Sewer Dept personnel observed less than one (1) gallon sanitary sewer wastewater around the home s basement floor drain. | The VCU-WRD Sewer Dept cleaned the City sanitary sewer main within the road directly in front of the residence located at 510 Randle St VCU-WRD Sewer Dept did not find any blockages/obstructions within the City sanitary sewer main and reported these findings/observations directly to the business owner. The owner of Total Development Construction will call a plumber ASAP in order to clean the sanitary sewer service line for the business located at 510 Randle St. | SSO Basement Backup
50989 | 37068 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-05-21 08:00 | 2013-05-21 09:45 | 2013-05-22 15:37 | 12200000 | gallons | The basement floor drain within the residence located at 2506 Shannon Dr. | Untreated Release The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 5-21-13 at 8:55am that there is/was sanitary sewer wastewater coming up through the basement floor drain within the residence located at 2506 Shannon Dr. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 200 gallons of clear water ground the floor drain within the home s basement. | The VCU-WRD Sewer Dept cleaned the City sanitary sewer main located within the road directly in front of the residence located at 2506 Shannon Dr. VCU-WRD Sewer Dept personnel did not find any blockages/obstructions within the City sanitary sewer main and reported these findings/observation directly to the homeowner. The homeowner has a plumber in route to clean the sanitary sewer service line for the residence located at 2506 Shannon Dr. | SSO Basement Backup
50989 | 37157 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-05-23 08:00 | 2013-05-23 09:00 | 2013-05-24 13:05 | 5500000 | gallons | Unknown location in the basement within the residence located at 906 Jefferson St. | Untreated Release Private Sanitary Sewer Service Line Blockage/Obstruction The homeowner stated in the original telephone sewer call out the VCU-WRD Sewer Dept on 5-23-13 at 8:14am that there is/was a sanitary wastewater back up occurring in the basement within the residence located at 906 Jefferson St. Upon arrival VCU-WRD Sewer Dept. personnel did not observe the sanitary wastewater due to the homeowner not being at home at this time. Furthermore the homeowner did not state the location or the amount of the sanitary wastewater back up within the home during their telephone sewer call message. | The VCU-WRD Sewer Dept cleaned the City Sanitary Sewer main within the utility easement directly behind the residence located at 906 Jefferson St. VCU-WRD Sewer Dept personnel did not observe a sanitary sewer wastewater backup or an obstruction/blockage within the City sanitary sewer main and reported these findings/observation directly in the homeowner via a telephone voice message. | SSO Basement Backup
50989 | 37514 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-05-29 18:30 | 2013-05-29 19:30 | 2013-05-31 10:17 | 5 | gallons | 805 Oak Street | Untreated release into residence basement | No obstruction found in city sewer. Notified homeowner who will contact a plumber ASAP to have residence sewer line cleaned. | SSO Basement Backup
50989 | 37508 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-04 16:30 | 2013-06-04 18:00 | 2013-06-07 15:39 | 5 | gallons | 607 Center Street | Untreated release into a residential basement. | Cleaned city sanitary sewer in front of residence. No obstruction or blockage found. Notified homeowner who will contact a plumber ASAP to have residence sewer line cleaned. | SSO Basement Backup
50989 | 38391 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-12 | 2013-06-14 13:00 | 2013-06-18 09:33 | 0 |  | 304 Morgan Blvd. House Lateral Basment Backup | The owner of the rental home located at 304 Morgan Blvd. Contacted the VCU-WRD Sewer Dept on 6-14-13 at 1:00pm and stated that there had been a sanitary wastewater backup in the basement within the rental home located at 304 organ Blvd. The owner further stated to VCU-WRD Sewer Dept. that the sanitary wastewater backup had occurred sometime during the night of 6-12-13. They were unsure of the exact time the sanitary wastewater backup had started or stopped or the origin of the wastewater backup with the basement. Upon arrival VCU-WRD Sewer Dept. personnel were unable to enter the home due to the tenant not being at home at the time. | On 6-14-13 the VCU-WRD Sewer Dept. cleaned the City sanitary/storm sewer combination main within the road directly in front of the residence located at 304 Morgan Blvd. VCU-WRD Sewer Dept personnel did not observe any blockages/obstructions within the City sanitary/storm sewer combination main on 6-14-13 and reported these findings/observations directly to the owner of the rental home via a telephone call. The VCU-WRD Sewer Dept personnel stated to the owner of the rental home to call the VCU-WRD Sewer Dept. immediately if there is another backup occurrence. | SSO Basement Backup
50989 | 38383 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-12 | 2013-06-14 13:00 | 2013-06-18 09:39 | 0 |  | 304 Morgan Blvd House Lateral Basement Backup | House Lateral The owner of the rental home located at 304 Morgan Blvd. contacted the VCU-WRD Sewer Dept o 6-14-2013 at 1:00pm and stated that there had been a sanitary wastewater backup in the basement within the rental home located at 304 Morgan Blvd. The owner further stated to VCU_WRD Sewer Dept that the sanitary wastewater backup had occurred sometime during the night of 6-12-2013. They were unsure of the exact time the sanitary wastewater backup had started or stopped or the origin of the wastewater backup within the basement. Upon arrival VCU-WRD Sewer Dept. personnel were unable to enter the home due to the tenant not being at home at this time. | On 6-14-2013 the VCU-WRD Sewer Dept cleaned the City sanitary/storm sewer combination main within the road directly in front of the residence located at 304 Morgan Blvd. VCU-WRD Sewer Dept. personnel did not observe any blockages/obstructions within the City sanitary/storm sewer combination main on 6-14-2013 and reported these findings/observations directly to the owner of the rental home via a telephone call. The VCU-WRD Sewer Dept. personnel stated to the owner of the rental home to call the VCU-WRD Sewer Dept. immediately if there is another backup occurrence. | SSO Basement Backup
50989 | 38388 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-12 | 2013-06-14 08:00 | 2013-06-18 09:36 | 0 |  | 303 Burlington Beach Rd House Lateral | The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-14-2013 at 9:10am that there was clear water coming up through the basement floor drain within the residence located at 303 Burlington Beach Rd. The homeowner stated to VCU-WRD Sewer Dept. staff that the clear water started coming up on 6-12-2013. The homeowner was unsure unsure as to the time the wastewater backup started or ended and decided to wait until 6-14-13 at 9:10am to contact the VCU- Sewer Dept. Upon arrival VCU-WRD Sewer Dept. personnel did not observe a backup within the home. | On 6-14-13 the VCU-WRD Sewer Dept. cleaned the City sewer main within the road directly in front of the residence located at 303 Burlington Beach Rd. The VCU-WRD Sewer Dept. personnel did not observe any blockages/obstructions within the City sanitary sewer main and reported these findings/observations directly to the homeowner. The homeowner had a plumber on site to clean the sanitary sewer service line for the residence located at 303 Burlington Beach Rd. The contracted plumber will continue to investigate the source of the clear water coming up through the home s basement floor drain. | SSO Basement Backup
50989 | 38385 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-12 | 2013-06-14 22:00 | 2013-06-18 09:38 | 0 |  | 605 McCord Rd House Lateral | The owner of the building located at 605 McCord Rd. stated in the original telephone sewer call to the VCU-WRD Sewer Dept. on 6-14-13 at 9:00pm that there is/was sanitary sewer wastewater coming up into the craw space underneath a business located within the building. The business owner stated that the back up started sometime in the night (pm) on 6-12-13. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately (8) inches of water in the entire crawl space area. Further VCU-WRD Sewer Dept. personnel observed that water would back up even more into the building s crawl space when the sup pump would run. | The VCU-WRD Sewer Dept checked the City sanitary sewer manholes within the road directly upstream and downstream of the business located at 605 McCord Rd. VCU-WRD Sewer Dept personnel did not find any blockages/obstructions within the City sanitary sewer manholes and reported these findings/observations directly to the building owner. The building owner will disconnect the sump pump and contact a plumber ASAP to have the sanitary sewer service line cleaned for the business located at 605 McCord Rd. | SSO Affected Private Property
50989 | 38482 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-12 20:00 | 2013-06-12 21:30 | 2013-06-13 13:22 | 500 | gallons | 606 Brown St. | Rain 1.15 inches. The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-12-13 at 8:08pm that there is/was sanitary wastewater coming up through the basement floor drain within the residence located at 606 Brown St. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 500 gallons of sanitary wastewater within the home s entire basement. | The VCU-WRD Sewer Dept cleaned the City sanitary sewer main within the alley directly west of the residence located at 606 Brown St. VCU_WRD Sewer Dept personnel found a blockage/obstruction within the City sanitary sewer main and promptly removed the blockage. VCU-WRD Sewer Dept personnel reported these findings/observations directly to the homeowner. The VCU-WRD Sewer Dept returned to televise and clean the City sanitary sewer main in order to remove any remaining residual blockage/obstruction from within the City sanitary sewer main in the alley directly west of the residence located at 606 Brown St. This work was completed at 7:00am on 6/13/13. | SSO Basement Backup
50989 | 38390 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-12 22:00 | 2013-06-13 06:00 | 2013-06-18 09:30 | 0 |  | 2205 Dorsett Dr House Lateral | Rain 1.19 inches The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept 6-13-13 at 3:50am that there is/was sanitary wastewater coming up through the basement floor drain within the residence located at 2205 Dorsett Dr. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately 100 gallons of clear water around the floor drain with the home s basement. | The VCU-WRD Sewer Dept cleaned and televised the City sewer main within the utility easement directly to the west of the residence located at 2205 Dorsett Dr. VCU-WRD Sewer Dept. personnel did not find any blockage/obstructions within the City sanitary sewer main and directly notified the homeowner of these findings/observations. | SSO Basement Backup
50989 | 38615 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-18 16:00 | 2013-06-18 17:00 | 2013-06-19 14:23 | 20 | gallons | 1302 Carrsbrooke Dr House Lateral | House Lateral The maintenance supervisor for the apartment building located at 1302 Carrsbrooke Dr stated in the original telephone sewer call to the VCU_WRD Sewer Sept on 6-18-13 at 4:30pm. that here is/was sanitary sewer wastewater coming up through the first floor bathroom toilet. Upon arrival VCU-WRD Sewer Dept. personnel did not observe any sanitary wastewater backing up within the apartment because the building s maintenance supervisor had already cleaned up the spilled wastewater. | The VCU-WRD Sewer Dept. cleaned the city sanitary sewer main within the utility easement directly behind the apartment building located at 1302 carrsbroke Dr. VCU-WRD Sewer Dept personnel did not find any blockages/obstructions within the City sanitary sewer main and reported these finding /observations directly to the maintenance supervisor of the apartment building. The maintenance supervisor will contact a plumber ASAP to have the sanitary sewer service line cleaned for the apartment building at 1302 Carrsbrooke Dr. | SSO Affected Private Property
50989 | 38375 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 07:45 | 2013-06-26 09:00 | 2013-06-27 11:03 | 0 |  | Two (2) Sanitary Sewer Manholes EKPCF Wastewater Treatment Plt. | Rain 1.19 inches Manhole Treatment Plant (See attachment ) | The VCU-WRD Sewer Dept cleaned up the minimal debris that remained on the ground next to the two (2) manholes after the overflow ended from both structures with the use of a vactor truck. The size of the debris field was minimal at about 20 feet by 20 feet and contained an small amount of paper plastic products and grit. (See Attached Report) | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Salt Creek
50989 | 39102 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 08:30 | 2013-06-26 10:00 | 2013-06-27 16:08 | 0 |  | 602 Hastings Terrace | The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept 6-26-13 at 8:43am that there is/was sanitary sewer wastewater backing up through the basement floor drain within the residence located at 602 Hastings Terrace. Upon arrival VCU-WRD Sewer Dept. personnel could not determine the amount of sanitary wastewater around the drain due to the homeowner not being at home. The homeowner stated at this time they were unsure of the amount of sanitary wastewater with the home s basement and uncure of the exact time that the overflow stopped via a telephone conversation between the VCU-WRD Sewer Dept. staff and the homeowner. | See Report | SSO Basement Backup
50989 | 39088 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 08:30 | 2013-06-26 10:00 | 2013-06-27 15:50 | 0 |  | 466 Bond Ave | Rain 1.31 inches. The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6/26/13 at 10:00am that there is/was sanitary wastewater coming up through the basement cleanout cap within the residence located a 466 Bond Ave. VCU-WRD Sewer Dept. personnel observed approximately 500 gallons of sanitary wastewater within the home s private plumbing contractor had broken the original brass cleanout cap and replace it with a rubber screw plug. The contractor did not install the replacement cap properly. | See Report | SSO Basement Backup
50989 | 38273 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 09:00 | 2013-06-26 10:00 | 2013-06-28 15:08 | 5 | gallons | 1503 Washington St | Rain 1.19 inches House Lateral The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept. on 6/27/13 at 3:41pm. that there was a sanitary wastewater backup that had occurred on 6/26/13 through a basement floor drain within the residence located at 1503 Washington St. Upon arrival the homeowner stated to VCU-WRD Sewer Dept. personnel the backup actually occurred at around 9:00am and stopped at 10:00 am on 6/26/2013. There was about five (5) gallons of sanitary wastewater within the home s basement at the time. The homeowner further stated hew waited to call the Department because he decided to contract with a plumber in order to clean and televise the home s sanitary sewer service line. The plumber did not find any problems within the home s sanitary sewer service line and proceeded to tell the homeowner to contract the VCU-WRD Sewer Dept. to check the City sewer main. | VCU-WRD Sewer Dept. cleaned the City sanitary/storm sewer combination main within the utility easement directly behind the residence located at 1503 Washington St. this cleaning occurred on 6/27/13 at 5:00pm. The VCU-WRD Sewer Dept did not find any blockages/obstructions within the City Sanitary/storm sewer combination main. The VCU-WRD Sewer Dept televised the City sanitary/storm sewer combination main on 6/28-13 at 8:00am in order to verify that there were no blockages/obstructions within the City sanitary/storm sewer combination main. | SSO Basement Backup
50989 | 39104 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 09:00 | 2013-06-26 11:00 | 2013-06-27 16:10 | 0 |  | 1005 Kentucky St | Rain 1.31 inches. The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-26-13 at 9:18am that there is/was sanitary wastewater backing up through the basement floor drain within the residence located at 1005 Kentucky St. Upon arrival VCU_WRD Sewer Dept. personnel observed approximately 750 gallons of sanitary wastewater within the home s basement. | See Report | SSO Basement Backup
50989 | 39090 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 09:15 | 2013-06-26 10:30 | 2013-06-27 14:52 | 0 |  | 1509 Washington St | Rain 1.31 inches. The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-26-13 at 9:15am there is/was sanitary wastewater coming up through the basement bathroom shower drain within the residence located at 1509 Washington St. It was raining very hard at the time of the resident s telephone call. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 200 gallons of sanitary sewer wastewater within the home s basement. | See Report | SSO Basement Backup
50989 | 39092 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 09:15 | 2013-06-26 10:30 | 2013-06-27 16:02 | 0 |  | 1509 Washington St. | Rain 1.31 inches the homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-26-13 at 9:15am there is/was sanitary wastewater coming up through the basement bathroom shower drain within the residence located at 1509 Washington St. It was raining very hard at the time of the resident s telephone call. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 200 gallons of sanitary sewer wastewater within the home s basement. | See Report | SSO Basement Backup
50989 | 39119 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 11:00 | 2013-06-26 13:30 | 2013-06-27 16:17 | 0 |  | House Lateral 804 Brown St. | The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-26-13 at 11:43am that there is/was sanitary wastewater backing up through the basement floor drain within VCU-WRD Sewer Dept personnel observed approximately 500 gallons of sanitary sewer wastewater within the home s basement. | See Reports | SSO Basement Backup
50989 | 39120 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 12:15 | 2013-06-26 13:00 | 2013-06-27 16:19 | 0 |  | 1502 Wood st house Lateral | The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-26-13 at 12:15pm that there is/was sanitary wastewater coming up through the basement floor drain within the residence located at 1502 Wood St. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately 100 gallons of sanitary wastewater within the home s basement. | See Report | SSO Basement Backup
50989 | 39108 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 13:00 | 2013-06-26 14:30 | 2013-06-27 16:13 | 0 |  | House Lateral | House Lateral the homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-26-13 at 1:14pm that there is/was sanitary wastewater coming up through the basement floor drain within the residence located at 702 Chicago St. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 50 gallons of sanitary wastewater around the home s basement floor drain. | See Report | SSO Basement Backup
50989 | 39100 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 16:00 | 2013-06-26 17:00 | 2013-06-27 16:04 | 0 |  | 1007 Elmhurst Ave | The homeowner stated in the original telephone ewer call to the VCU-WRD Sewer Dept on 6-26-13 at 4:41pm that there is/was sanitary wastewater backing up through the basement floor drain within the residence located at 1007 Elmhurst Ave. The homeowner was not home upon VCU-WRD Sewer Dept arrival but stated in a telephone call with VCU-WRD Sewer Dept personnel that approximately 25 gallons of sanitary sewer wastewater was around the floor drain within the home basement. | See Report | SSO Basement Backup
50989 | 39509 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-07-02 11:00 | 2013-07-02 17:30 | 2013-07-03 14:54 | 0 |  | Restaurant Oil & Grease Interceptor 1805 Lincolnway | The manager of the Dynasty Buffet restaurant stated in the original telephone sewer call to the VCU_WRD Sewer Dept. on 7-2-13 at 3:25pm that the manhole to the restaurant s outside oil and grease interceptor is/was overflowing into a gravel parking lot directly behind the restaurant at 1805 Lincoln way. Upon arrival VCU_WRD Sewer Dept personnel observed approximately 300 gallons of sanitary wastewater around the manhole connected to the restaurant s interceptor. Furthermore the restaurant s manager stated to VCU-WRD Sewer Dept. personnel that the overflow had been occurring all day - the restaurant opens at 11:00am | See Report | SSO Affected Private Property
50989 | 39530 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-07-04 19:00 | 2013-07-04 21:00 | 2013-07-09 09:48 | 0 |  | 104 Garfield Ave | Unknown The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 7-4-13 at 8:08pm that there is/was sanitary wastewater coming up out of the outside sanitary sewer service line cleanout cap at the home located at 104 Garfield Ave. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately ton (10) gallons of sanitary wastewater around the home s outside sanitary sewer service line cleanout. | See Report | SSO Affected Private Property
50989 | 39550 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-07-09 10:30 | 2013-07-09 11:30 | 2013-07-11 08:08 | 0 |  | 4202 Hemlock Dr | Unknown The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 7-9-13 at 11:10am that there is/was sanitary wastewater backing up through the basement floor drain within the residence located at 42021 Hemlock Dr. upon arrival VCU-WRD Sewer Dept personnel observed approximately five (5) gallons of sanitary wastewater around the home s basement floor drain. The homeowner further stated to VCU_WRD Sewer Dept personnel that they had a plumber clean the home s sanitary sewer service line approximately four (4) months ago. | wSee Report | SSO Basement Backup
50989 | 39551 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-07-09 10:30 | 2013-07-09 11:30 | 2013-07-10 08:45 | 0 |  | 4202 Hemlock Dr | Unknown The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 7-9-13 at 11:10am that there is/was sanitary wastewater backing up through the basement floor drain. The homeowner further stated to VCU-WRD Sewer Dept personnel that they had a plumber clean the home s sanitary sewer service line approximately four (4) months ago. | See Report | SSO Basement Backup
50989 | 39616 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-07-20 14:19 | 2013-07-28 14:19 | 2013-07-30 14:12 | 0 |  | 3300 Churchview Dr | The homeowner called VCU-WRD Sewer Dept on 7-29-13 at 7:16am and reported that sanitary wastewater backed up through the basement bathroom toilet and bathtub at 3300 Churchview Dr. Upon arrival VCU-WRD was told by the homeowner that the backup occurred on 7-28-13 but wasn t sure of when it started or ended. The homeowner returned on 7-28-13 about 10:00pm this is when they observed a wastewater back up within the home s basement. The homeowner stated to staff that about 200 gallons of sanitary wastewater was within the home s basement. | Remove Blockage See Report | SSO Basement Backup
50989 | 39615 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-07-28 14:00 | 2013-07-28 18:00 | 2013-07-30 14:15 | 0 |  | 3207 Churchview Dr. | The homeowner called VCU-WRD Sewer Dept. on 7/28/13 at 4.40pm. There is/was sanitary wstewater coming up through the basement floor drain within the residence located at 3207 Churchview Dr. VCU-WRD Sewer Dept didn t observe the wastewater back up as the homeowner was not home at the time. It was suspected but not verified that the backup was due to a blockage within the City s sanitary sewer main. There was a attempt to contact the homeowner by phone but the homeowner s phone was out of order. | Removed Blockage See Report | SSO Basement Backup
50989 | 39662 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-08-02 08:00 | 2013-08-02 09:00 | 2013-08-02 14:30 | 0 |  | 2001 McCord Rd | House Lateral The homeowner told VCU- WRD Sewer Dept on 8-2-13 @ 8:45am that there is/was sanitary sewer wastewater coming up through the basement floor drain at 2001 McCord Rd. VCU-WRD Sewer Dept personnel observed approximately less than 10 gallons of sanitary sewer wastewater around the basement floor drain. | See Report | SSO Basement Backup
50989 | 39749 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-08-02 11:21 | 2013-08-02 11:21 | 2013-08-06 15:20 | 0 |  | 104 Greenwich St | Homeowner stated that there was 5 inches of sanitary wastewater in the basement within the residence located at 104 Greenwich St. The backup occurred during a rain storm on 8-2-13 but didn t state the time of the actual backup. VCU-WRD personnel didn t observe the backup because the homeowner wasn t home at the time. | See Report | SSO Basement Backup
50989 | 39747 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-08-02 14:58 | 2013-08-02 15:30 | 2013-08-05 13:55 | 0 |  | 1900 Beech St | The maintenance supervisor stated to VCU-WRD Sewer Dept 8-2-13 at 2:58pm that sanitary wastewater was coming up through the laundry room floor drain within the apartment building located at 1900 Beech St. Upon arrival VCU-WRD personnel observed approximately 5 gallons of sanitary wastewater around the laundry room floor drain. | Removed blockage See Report | SSO Basement Backup
50989 | 39788 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-08-15 10:00 | 2013-08-15 11:30 | 2013-08-16 11:08 | 0 |  | 1601 Valparaiso St | The homeowner called VCU-WRD Sewer Dept on 8-15-13 at 1-:47am to report sanitary wastewater backing up in the homes s bathroom toilet within the residence located at 1601 Valparaiso St. Personnel observed approximately 10 gallons of sanitary wastewater around the bathroom toilet. | See Report | SSO Affected Private Property
50989 | 40005 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-09-04 16:00 | 2013-09-04 18:00 | 2013-09-06 11:51 | 0 |  | 605 Parkside Ave | The homeowner stated to VCU-WRD Sewer Dept. 9-5-13 at 7:50am that there was/is sanitary wastewater coming up through the bathroom s bathtub drain at 605 Parkside Ave. Upon arrival the homeowner told VCU-WRD Sewer staff that the actual wastewater backup occurred on 9-4-13 at 4:00pm and that 2 gallons of sanitary sewer wastewater backed up within the home s bathroom bathtub. | See Report | SSO Affected Private Property
50989 | 41152 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-10-02 12:30 | 2013-10-02 14:00 | 2013-10-04 10:01 | 0 |  | 551 Woodlawn Dr. | The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 10-02-13 at 1:14pm that there is/was sanitary wastewater coming up in the yard at the residence located at 551 Woodlawn Dr. Upon arrival VCU-WRD Sewer Dept personnel observed approximately five (5) gallons of sanitary wastewater and waste paper around what appeared to be an old outside stormwater downspout drain for the next door home. | See Report
50989 | 41141 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-10-18 12:00 | 2013-10-19 11:00 | 2013-10-21 13:10 | 0 |  | Sanitary sewer force main failure at US Hwy and Axe Avenue | Equipment Failure See Report | Repaired Pipe See Report | SSO Reached Receiving Water
50989 | 41212 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-10-22 06:30 | 2013-10-22 07:30 | 2013-10-23 08:30 | 0 |  | 2206 Roosevelt Rd Manhole | The office manager of the Digestive Healthcare Associates Clinic located at 2206 Roosevelt Road stated in the original telephone sewer call to the VCU-WRD Sewer Dept. on 10-22-13 at 6:30am that there is/was sanitary sewer wastewater coming up from a sanitary sewer manhole located within the business s parking lot. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 25 gallons of sanitary wastewater around the sanitary sewer manhole within the business s parking lot. | Removed Blockage See Report | SSO Affected Private Property
50989 | 41515 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-10-29 10:00 | 2013-10-29 11:00 | 2013-11-01 06:19 | 0 |  | 902 Eastbrook Dr | See Attached | See Report | SSO Basement Backup
50989 | 41518 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-10-31 14:09 | 2013-10-31 01:00 | 2013-11-01 09:20 | 0 |  | 1404 Peachtree Dr | Unknown The homeowner stated in the original telephone call to the VCU-WRD Sewer Dept at 12:13am on 10-31-13 that there is/was sanitary wastewater coming up through the basement floor drain within the residence located at 1404 Peachtree Dr. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately ten (10) gallons of sanitary wastewater around the homes s basement floor drain. | See Report | SSO Basement Backup
50989 | 41519 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-10-31 14:09 | 2013-10-31 17:00 | 2013-11-01 10:13 | 0 |  | 305 Erie St | The homeowner stated in the original telephone call to the VCU-WRD Sewer Dept at 4:04pm on 10-31-2013 that there is/was sanitary wastewater within the basement of the residence located at 305 Erie St. Upon arrival VCU-WRD Sewer Dept observed approximately 500 gallons of sanitary wastewater within the home s basement. The homeowner was unsure of the time that the actual wastewater backup started due to being at work when the wastewater backup started due to being at work when the wastewater backup started. The homeowner lift for work the same day at 8:00am | See Report | SSO Basement Backup
50989 | 41940 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-11-14 11:45 | 2013-11-14 12:45 | 2013-11-15 11:39 | 0 |  | 362 Locust St | Unknown The owner of the home located at 360 Locust St stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 11-14-13 at 12:19pm that there is/was sanitary wastewater around the outside sanitary sewer service line cleanout for the residence located at 362 Locust St. Upon arrival VCU_WRD Sewer Dept. personnel observed approximately three (3) gallons of sanitary wastewater around the outside sanitary sewer cleanout for the home located at 362 Locust St. | See Report | SSO Affected Private Property
50989 | 42243 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-11-19 08:45 | 2013-11-19 10:00 | 2013-11-20 14:58 | 0 |  | 360 Locust St | Unknown The homeowner stated in the original telephone call to the VCU-WRD Sewer Dept at 9:20am on 11-19-13 that there is/was sanitary sewer coming up through the basement floor drain within the residence located at 360 Locust St. Upon arrival VCU-WRD Sewer Dept personnel observed approximately (10) gallons of sanitary wastewater around the home s basement floor drain. | See Report | SSO Basement Backup
50989 | 42241 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-11-23 09:18 | 2013-11-23 09:18 | 2013-11-27 10:10 | 0 |  | 3507 Hemlock Dr | Unknown the homeowner stated in the original telephone sewer call on 11-25-13 at 10:35am to the VCU-Sewer Dept that there is/was sanitary wastewater back in garage form a garage floor drain within the home located at 3507 Hemlock Dr. Upon arrival VCU-WRD Sewer Dept personnel did not observe any wastewater back up. At this time the homeowner stated to VCU-WRD Sewer Dept personnel that the actual back up occurred on 11-23-13 and they were unsure of the actual time. Furthermore about two (2) gallons of sanitary wastewater had come up through the home s garage floor drain. | See Report | SSO Affected Private Property
50989 | 42566 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-12-13 08:30 | 2013-12-13 17:00 | 2013-12-17 14:10 | 0 |  | 2106 Yortowne Dr | The homeowner stated in the original telephone sewer call to the VCU_WRD Sewer Dept on 12-13-13 at 4:06pm that there is/was sanitary wastewater backing up through the basement floor drain with arrival VCU_WRD Sewr Dept personnel observed approximately 500 gallons of sanitary watewater within the the home s basement. | Removed Blockage See Report | SSO Basement Backup
50989 | 42548 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-12-13 08:30 | 2013-12-13 17:00 | 2013-12-16 09:05 | 0 |  | 2106 Yorktowne Dr. | The homeowner stated in the original telephone sewer call at 4:06pm on 12-13-2013 to the VCU-WRD sewer Dept. that there is/was sanitary wastewater backing up through the basement floor drain within the residence located at 21086 Yorktowne Dr. Upon arrival VCU-WRD Sewer Dept personnel observed approximately 500 gallons of sanitary sewer within the home s basement. | Removed Blockage See Report | SSO Basement Backup
50989 | 43555 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-12-20 12:00 | 2013-12-20 14:00 | 2013-12-23 12:00 | 5 | gallons | 485 Ridgeland Ave | Unknown the tenant stated in the original telephone sewer call to the VCU_WRD Sewer Dept on 12/20/2013 at 1:30pm that there is sanitary wastewater coming up through the bathroom bathtub drain within the residence located at 485 Ridgeland. Upon arrival VCU_WRD Sewer Dept. personnel did not observe any wastewater back up due to the tenant not being home at this time. The tent stated in the original telephone call that there was approximately five (50 gallons of sanitary wastewater within the home s bathtub | See Report | SSO Affected Private Property
50989 | 43557 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-12-21 21:00 | 2013-12-21 23:45 | 2013-12-23 16:02 | 200 | gallons | 2204 Campbell St | See Report | See Report | SSO Basement Backup
50989 | 43556 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-12-27 09:05 | 2013-12-27 09:30 | 2013-12-27 16:36 | 100 | gallons | 205 Oxbow Court | See Report | See Report | SSO Basement Backup
52450 | 35411 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-04-11 | 2013-04-11 | 2013-04-12 08:41 | 0 |  | Manhole M-0823 located at the South Haven WWTP 305 West 700 North South Haven IN | Precipitation event triggered overflow from influent manhole at the Aqua Indiana - South Haven WWTP. Overflow affected grass area near manhole. No estimation of the amount of Untreated Release. | Area affected was inspected and all solids cleaned up. Manhole is a leak tight typ manhole but the seal had been removed for the installation of flow monitoring meters. The seal will be replaced. Rehabilitation work in the collection system will continue as well as flow metering and evaluation work. | SSO Occurred at Treatment Plant; Surface Soil
52450 | 36587 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-04-11 01:30 | 2013-04-12 15:00 | 2013-04-12 14:58 | 0 |  | Aqua Indiana - South Haven Sewer Works | Precipitation event triggered the need to remove the Fine Screen Headworks form service. No release just temporary bypass of a treatment process. | Fine screen headworks brought back into service. | SSO Occurred at Treatment Plant
52450 | 35398 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-04-11 17:20 | 2013-04-12 02:00 | 2013-04-12 12:34 | 281128 | gallons | Aqua Indiana - South Haven IN Manhole M-0823 at 305 West 700 North. | A precipitation event triggered an Untreated Release from the treatment plant manhole M-0823. Untreated Release was passed into a storm ditch. No record of receiving waters. | Area affected by overflow ws inspected and all solids were cleaned up. The seal on the manhole at the treatment plant had been removed to install flow meters. Seal will be replaced. Rehabilitation work in the collection system will continue as well as flow metering and evaluation work. | SSO Occurred at Treatment Plant
52450 | 38050 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-06-26 09:12 | 2013-06-26 10:23 | 2013-06-26 16:00 | 0 |  | MH# m-0246 in the road on Timberline Dr. Manhole | Rain 3.0 inches 3.0 inches of rain in an hour and a half. | Overflows ceased soon after rain stopped and the volume in the collection system decreased. The minimal debris was removed. The entire collection system is being systematically cleaned and video inspected annually and significant sources of the inflow and infiltration are being sealed when identified. | SSO Reached Public Land
52450 | 39034 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-06-26 09:12 | 2013-06-26 09:20 | 2013-06-26 16:00 | 0 |  | MH# M-0246 in the road on Timberline Dr. MH# M-0407 in front yard of 403-1 Portland Dr. | Rain 3.0 inches Manhole. 3.0 inches |  | SSO Reached Public Land
52450 | 38047 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-06-26 09:15 | 2013-06-26 10:25 | 2013-06-26 16:00 | 0 |  | MH in road between Governor and Lahonda Roads. Manhole | Rain 3.0 inches. 3.0 inches of rain in a hour and a half | Overflows ceased soon after rain stopped an the volume in the collection system decreased. The minimal debris was removed. The entire collection system is being systematically cleaned and video inspected annually and significant sources of the inflow and infiltration are being sealed when indentified. | SSO Reached Public Land
52450 | 39045 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-06-26 09:15 | 2013-06-26 10:25 | 2013-06-26 16:00 | 0 |  | MH in road between Govenor and Lahanda Roads. | Rain 3.0 inches 3.0 inches of rain in a hour and a half. | See Report | SSO Reached Public Land
52450 | 38051 | IN0030651 | SOUTH HAVEN WATER WORKS INCORPORATED | Porter | 2013-06-26 09:20 | 2013-06-26 10:18 | 2013-06-26 16:00 | 0 |  | MH# m-0407 in front yard of 403-1 Portland Dr Manhole | Rain 3.0 inches. 3.0 inches of rain in an hour and a half. | Overflows ceased soon after rain stopped and the volume in the collection decreased. The minimal debris was removed. The entire collection system is being systematically cleaned and video inspected annually and significant sources of inflow and infiltration are being sealed when indentified. | SSO Reached Public Land
51101 | 34814 | IN0031119 | SHOREWOOD FOREST UTILITIES | Porter | 2013-02-26 10:30 | 2013-02-26 10:45 | 2013-02-26 13:34 | 500 | gallons | Force Main at 396 Devon Road Valparaiso IN | NIPSCO was digging to replace underground power cables and hit Force Main | Shut down Lift Station and called out our Honey Dipper to maintain lift station and called Metz Sewer to repair the force main. | SSO Reached Receiving Water | Lake Louise
51101 | 35439 | IN0031119 | SHOREWOOD FOREST UTILITIES | Porter | 2013-03-26 09:30 | 2013-03-26 10:00 | 2013-03-27 07:28 | 500 | gallons | Force Main at 475 Wexford Road | Other utility contractor working and damaged the force main. Result was an untreated release to the surrounding ground. | Shut off lift station and called honey dipper to maintain lift station while force main was repaired. | SSO Reached Public Land
51101 | 38253 | IN0031119 | SHOREWOOD FOREST UTILITIES | Porter | 2013-07-01 09:00 | 2013-07-01 12:00 | 2013-07-01 09:00 | 0 |  | 388 Deer Ridge Rd 2 Force main | Equipment Failure Pipe Failure. 2 Forced main had a stress crack. | We had Midwest Excavation out to suck up water we had Metz out to repair the pipe. | SSO Affected Private Property; SSO Reached Receiving Water | Lake Louise
50989 | 39109 | IN024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 23:30 | 2013-06-26 12:30 | 2013-06-27 16:15 | 0 |  | 1302 Fairlane Dr | The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept on 6-26-13 at 11:57am that there is/was sanitary wastewater coming up through the basement floor drain within the residence located at 1302 Fairlane Dr. Upon arrival VCU-WRD Sewer Dept. personnel observed approximately 100 gallons of sanitary wastewater around the home s basement floor drain. | See Report | SSO Basement Backup
52129 | 35195 | INJ046949 | PORTER CITY | Porter | 2013-01-29 21:15 | 2013-01-30 09:30 | 2013-01-30 12:36 | 12349 | gallons | Porter Avenue Lift Station Porter IN | Extreme precipitation event resulted in pumps running continuously main breaker failure and back up generator failure causing an untreated release into the Little Calument River | Vac truck on site and hauled 22 loads to help relieve the pumps at the station. The Town of Porter is in the process of building a new Lif Station and installing a new force main to the Chesterton Treatment Plant. | SSO Reached Receiving Water | Little Calumet River
52129 | 36235 | INJ046949 | PORTER CITY | Porter | 2013-04-18 00:15 | 2013-04-18 12:30 | 2013-04-19 09:33 | 1500 | gallons | Triangle Trail | Precipitation event triggered SSO untreated release to the street. | Had vac truck on site to help lift station to keep up. Pumped 1200 gallons and stopped SSO. We are working on the I & I in this area and in process of engineering the new lift station. | SSO Reached Public Land; Paved Surface
52129 | 38957 | INJ046949 | PORTER CITY | Porter | 2013-06-26 07:00 | 2013-06-26 10:30 | 2013-06-26 16:30 | 0 |  | Porter Ave. Lift Station | Rain 2.53 inches Exceeded Max Capacity. 2.53 inches of rain flash flooding in Porter County | See Report | SSO Reached Receiving Water | Little Calumet River
52129 | 38963 | INJ046949 Overflow reached Unnamed Ditch | PORTER CITY | Porter | 2013-06-26 07:00 | 2013-06-26 10:30 | 2013-06-26 17:39 | 0 |  | Triangel Lift Station Manhole | Rain 2.53 inches. 2.53 inches of rain Flash flooding in Porter County | See Report | SSO Reached Public Land
52123 | 39054 | INJ060801 | BURNS HARBOR & ARCELORMITTAL BURNS HARBOR LLC | Porter | 2013-06-26 13:37 |  | 2013-06-26 16:25 | 0 |  | Sanitary Plant Influent | Rain. Due to precipitation the Sanitary Plant influent was overflowing directly into the clarifiers bypassing a portion of the treatment plant. The actual flow is unknown at this time. The effluent from this plant mixes with industrial wastewaters of NPDES Permit No IN0000175 flow into polishing lagoons and is discharged trough Outfall 011 to Outfall 001 and subsequently to the East Branch of the Little Calumet River. | TBD | SSO Occurred at Treatment Plant | Grand Calumet River
52123 | 39564 | INJ060801 | BURNS HARBOR & ARCELORMITTAL BURNS HARBOR LLC | Porter | 2013-07-16 22:00 | 2013-07-17 01:15 | 2013-07-17 10:09 | 0 |  | Overflow from Equalization Basins to Clarifiers | The upset occurred as a result of pump and control issues at the Sanitary Plant. While operating one pump in manual mode the incoming flow increased just enough to overwhelm the pump and allow the equalization basin to overflow into the clarifiers bypassing the aeration portion of the plant. The wastewater was treated with chlorine prior to discharge to Outfall 031 and subsequently to the polishing lagoons and Outfall 011 permitted under NPDES permit IN0000175 | See Report | SSO Reached Receiving Water | Little Calumet River
52123 | 39666 | INJ060801 | BURNS HARBOR & ARCELORMITTAL BURNS HARBOR LLC | Porter | 2013-08-02 20:10 | 2013-08-03 10:11 | 2013-08-05 09:34 | 0 |  | Overflow from Equalization Basins to Clarfiers | Rain The upset occurred as a result of heavy rains experienced on 8/2/13. The surges in flow overwhelmed the influent chamber which overflowed into the clarifiers bypassing a portion of the plant. Thew wastewater was treated with chlorine prior to discharge to Outfall 031 and subsequently to the polishing lagoons and Outfall 011 permitted under NPDES permit IN0000175. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Little Calumet River
52123 | 38945 | INJ060801 (Town of Burns Harbor and Arcelor Mitial Burns Harbor | BURNS HARBOR & ARCELORMITTAL BURNS HARBOR LLC | Porter | 2013-06-26 11:03 |  | 2013-06-26 16:25 | 0 |  | Sanitary Plant Influent | Due to precipitation the Sanitary Plant influent was overflowing directly into the clarifiers bypassing a portion of the treatment plant. The actual flow is unkown at this time. The effluent from this plant mixes with industrial wastewater of NPDES Permit No IN0000175 flows into polishing lagoons and is discharged through Outfall 011 to Outfall 001 and subsequently to the East Branch of the Little Calumet River. | See Report | SSO Occurred at Treatment Plant
52123 | 41102 | INJ060801 Outfall 001 011 | BURNS HARBOR & ARCELORMITTAL BURNS HARBOR LLC | Porter | 2013-10-11 08:40 | 2013-10-11 08:41 | 2013-10-11 15:07 | 0 |  | manhole #131 SWTP secondary mixers | As a result of switching of the waste water pump station #1 pump controls from automatic to manual control for a planned outage of the automatic control system. The first incident was a bypass of the SWTP Clarifiers and lagoons when approximately 100 gallons of untreated wastewater was diverted at upstream manhole #131 to the storm ditch which feeds outfall 001. The second incident was a bypass at the secondary mixers. When approximately 5000 gallons of untreated wastewater were diverted to the SWTP clarifier effluent. | See Report | SSO Reached Receiving Water | Little Calumet River
50989 | 39121 | N0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-06-26 12:11 | 2013-06-26 12:45 | 2013-06-27 16:21 | 0 |  | 1408 Wood St House Lateral | The homeowner stated in the original telephone sewer call to the VCU-WRD Sewer Dept to the VCU-WRD Sewer Dept. on 6-26-13 at 12:11pm that there is/was sanitary wastewater coming up through the basement floor drain within the residence located at 1406 Wood St. upon arrival VCU-WRD Sewer Dept. personnel did not observe any wastewater back up within the residence due to the homeowner already had cleaned up the wastewater. The homeowner stated that there was approximately 100 gallons of sanitary wastewater within the home s basement. | See Report | SSO Basement Backup
50989 | 40243 | N0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | Porter | 2013-09-18 22:11 | 2013-09-19 01:32 | 2013-09-19 12:08 | 0 |  | Two (2) Sanitary Sewer Manholes @ ELPCF Wastewater Treatment Plt. | See Attached Report | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Salt Creek
| 42399 | Terminated Permit | Damon Run Conservancy District Liftstation | Porter | 2013-12-11 08:30 | 2013-12-11 12:30 | 2013-12-11 08:30 | 0 |  | The Embridge easement 600ft south of Watson Rd (Watson Rd/ Meridian Rd is closest cross street) also entrance to Timberland Estates. | Surcharge was caused by excavation for pipeline install being conducted by Precision Pipeline (contractor damaged sewer pipe). Incident occurred at (8:25am ) lift station pumps feeding break in sewer line (surcharge) were manually controlled to limit flow as much as possible and were turned off at (12:30pm). | See Report | SSO Affected Private Property
50022 | 35957 | IN0035696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-01-12 | 2012-01-12 04:00 | 2013-01-13 10:11 | 100000 | gallons | Mill Creek Lift Station | A break in the force main leaving lift station resulted in an untreated relase to surrounding ground. | Shut down lift station and opened valve to divert waste to the wet weather pump station and to the treatment plant. Contractor will excavate and repair force main. | SSO Reached Public Land
50022 | 35956 | IN0035696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-01-12 18:00 | 2013-01-12 20:00 | 2013-01-13 10:12 | 50000 | gallons | E & S Housing Lift Station | Precipitation event and I & I contribution resulted in an untreated release from lift station to receiving waters. | We are currently video taping the lines to determine how I & I is entering the lift station so that we can determine what needs to be fixed to prevent hydraulic overload entering the lift station. | SSO Reached Receiving Water | McFadden Creek
50022 | 34361 | IN0035696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-01-12 18:00 | 2013-01-12 20:00 | 2013-01-13 10:00 | 50000 | gallons | E&S Housing Lift Station | Untreated release. 6 inches of precipitation. | currently video taping the lines to determine how INI is entering the lift station so that we can determine what needs to be fixed to prevent hydraulic overload entering the lift station. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | McFadden Creek
50022 | 35858 | IN0035696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-01-12 23:38 | 2013-01-13 18:15 | 2013-01-14 15:11 | 950000 | gallons | E & S Housing Lift Station | Precipitation event and I & I to lift station resulted in untreated release from Lift Station to receiving waters | Wea re currently video taping the lines to determine how the I & I is entering the Lift Station so that we can determine what needs to be fixed to prevent hydraulic over load entering the lift station. | SSO Reached Receiving Water | McFadden Creek
50022 | 34934 | IN0035696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-03-17 21:30 | 2013-03-17 | 2013-03-19 20:18 | 108317 | gallons | E&S Housing McFadins Creek | Untreated Release Rain 1.82 inches | We are currently investigating the neighborhood to see where all the I&I are coming from. | SSO Reached Receiving Water
50022 | 36474 | IN0035696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-04-18 23:20 | 2013-04-19 | 2013-04-19 12:41 | 7046 | gallons | E & S Lift Station | Precipitation event flow exceeded capacity of lift station resulting in untreated release from lift station to receiving waters. |  | SSO Reached Receiving Water | McFadden Creek; Ohio River
50022 | 36079 | IN0035696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-04-19 | 2013-04-19 04:55 | 2013-04-23 16:42 | 41709 | gallons | E&S Lift Station McFadden Creek Ohio River | Untreated Release Rain 1.54 inches The overflow is still going over from the day before we had 1.54 of precipitation. |  | SSO Reached Receiving Water | McFadden Creek; Ohio River
50022 | 43566 | IN0035696 Outfall 006 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-12-21 08:30 | 2013-12-22 05:30 | 2013-12-23 11:10 | 32826 | gallons | E&S Housing | Rain 5.62 inches | See Report | SSO Reached Receiving Water | McFadden Creek
50022 | 43567 | IN0035696 Outfall 006 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-12-22 | 2013-12-22 05:30 | 2013-12-23 11:12 | 549640 | gallons | E&S Housing | Rain .01 inches | See Report | SSO Reached Receiving Water | McFadden Creek
50022 | 34932 | IN00359696 | MOUNT VERNON WASTE WATER TREATMENT PLANT | Posey | 2013-03-18 | 2013-03-18 10:25 | 2013-03-19 20:20 | 88736 | gallons | E & S Housing McFadins Creek | Untreated Release Rain .83 inches | We are currently investigating the neighborhood to see where all the I&I are coming from. | SSO Reached Receiving Water
51147 | 35804 | IN0040517 | POSEYVILLE MUNICIPAL WASTE WATER PLANT | Posey | 2013-01-12 17:00 | 2013-01-13 23:00 | 2013-01-13 12:50 | 126000 | gallons | Main Lift Station at WWTP | Precipitation event coupled with saturated ground and flash flooding resulted in the necessity for untreated release and treatment plant bypass in order to prevent major property damage and public health concerns. Bypass was pumped to receiving waters. | Pumped out wet well to keep sewage from entering residences. system working at 100% capacity. Treatment only bypassed long enough to avoid property loss and avoid public health concerns. Revisit smoke testing plans and continue to work on I & I in the town s collection system. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Black River
58956 | 37589 |  | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-12 |  | 2013-06-13 09:39 | 0 |  | Lift Station #4 | Sonia Morrison of Cloverdale states that lift station #4 continues to overflow after rain events resulting in sewage and all over. She knows the town is under an agreed order. | I am familiar with this complainant and have spoken with her previously regarding SSO s in Cloverdale. I went by the facility today and they have no record of an overflow occurring at that location in the past two months. They have records showing the overflows that have occurred and they are reporting them as required. We went to the lift station and I did not see any evidence of recent overflows. I also checked the two manholes that are up and down stream of the lift station and did not see any evidence of an overflow. I have made several attempts to contact the complainant and have not gotten an answer. There is also no machine or voicemail on the line so I cannot leave a message. The plant monitors the locations daily and seems to be doing what is required for reporting so I do not believe this is an ongoing issue. I would suggest closing the complaint at this time as the plant is meeting reporting requirements and the complainant is not reachable by the phone number given.
59601 | 35640 | IN0021032 | GREENCASTLE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-12 23:45 | 2013-01-13 04:50 | 2013-01-07 06:43 | 10500 | gallons | Cornstalk Lift Station and Manhole #98-2A | Precipitation event overwhelmed lift station resulting in untreated release to unnamed receiving waters. Surcharge in manhole caused short term overflow to storm sewer. High temp alarm on pumps. | Picked up debris and applied a bleach solution to affected area. Determined that wire connection in panel were loose causing the erroneous high temp alarm. | SSO Reached Receiving Water; Storm Sewer
59601 | 36116 | IN0021032 | GREENCASTLE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 22:25 | 2013-04-19 07:45 | 2013-04-19 09:58 | 30000 | gallons | Manhole 32Manhole 37Manhole 56 | Precipitation event caused untreated release from manholes to storm drain and unnamed receiving waters. | system ran normally after rain stopped. Cleaned up any debris adn applied bleach solution to area. | SSO Reached Public Land; SSO Reached Receiving Water
59601 | 36113 | IN0021032 | GREENCASTLE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 22:45 | 2013-04-19 04:30 | 2013-04-19 09:58 | 22000 | gallons | Sherwood Lift StationCornstalk Lift Station | Precipitation event and power outage resulted in lift stations being overwhelmed with overflow reaching surrounding ground and unnamed receiving waters. | Applied bleach solution to affected areas and cleaned up debris. | SSO Reached Public Land; SSO Reached Receiving Water
59601 | 36115 | IN0021032 | GREENCASTLE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 22:52 | 2013-04-19 08:15 | 2013-04-19 09:58 | 10000 | gallons | Manhole 134Manhole 98-2A | Precipitation event caused untreated release from manholes to unnamed receiving waters. | System opened up and ran normally following rain event. We applied a bleach solution and picked up any debris. | SSO Reached Receiving Water
59601 | 43568 | IN0021032 Outfall 001 (Reached creek beside station name of creek unknown) | GREENCASTLE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-12-22 02:00 | 2013-12-22 03:00 | 2013-12-22 05:40 | 2500 | gallons | Sherwood Lift Station (N Houck Rd) | Power Failure Power failure a 100 amp breaker switch went bad on power pole. | Repaired pump Station | SSO Reached Receiving Water
58956 | 35947 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-11 | 2013-01-11 | 2013-01-12 10:38 | 0 |  | Manhole D-2 at Lift Station #4 | While doing daily checks discovered evidence of untreated release from lift station manhole apparently resulting from precipitation and snow melt. Unknown start and stop times. Release apparently reached receiving waters. | New lift station under construction. | SSO Reached Receiving Water | Doe Creek
58956 | 34359 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-11 |  | 2013-01-12 10:37 | 1658 | gallons | Manhole D-2 at Lift Station #4 | Untreated Release - Precipitation Event - While doing daily lift station check found evidence of overflow. Had 1.4 of rain and melting snow. | New lift station under construction. | SSO Reached Receiving Water | Doe Creek
58956 | 35946 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-11 | 2013-01-11 | 2013-01-12 09:33 | 0 |  | Manhole B-1 at Lift Station #2 | Power outage caused by precipitation event resulted in untreated release from manhole at lift station to ground surrounding manhole. | Raked debris and limed area around the manhole. Informed town board that a backup generator is needed to avoid these failures. | SSO Reached Public Land
58956 | 35945 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-11 05:00 | 2013-01-11 11:15 | 2013-01-12 09:29 | 150000 | gallons | W-3 Manhole | Clogged pump in the main lift station could not keep up with flow from I & I and snow melt resulting in untreated release to receiving waters. | Quality Repair Service pulled pump and cleaned out debris. Raked and limed area around manhole. | SSO Reached Receiving Water | Rabbit Run
58956 | 35767 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-12 | 2013-01-14 12:45 | 2013-01-15 07:48 | 0 |  | Manhole W-53 off Highway 231 across from Dollar Store. | Found evidence of untreated release from manhole overflow triggered by precipitation event. | Utility Manager will have affected area cleaned and limed today. Informed Utility Manager that I & I needs to be addressed in this area. | SSO Reached Public Land; SSO Reached Receiving Water | Rabbit Run
58956 | 35803 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-13 07:49 | 2013-01-13 10:30 | 2013-01-13 12:10 | 13000 | gallons | Manhole D-2 at Lift Station #4 | Precipitation event triggered untreated release from lift station manhole to receiving waters. | New Lift Station under construction. | SSO Reached Receiving Water | Doe Creek
58956 | 35959 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-13 10:00 | 2013-01-13 16:25 | 2013-01-14 08:52 | 0 |  | Manhole B-2-A at Lift Station #2 off Stardust Way | Precipitation event and I & I contribution exceeded capacity of manhole feeding lift station and resulted in an untreated release to an unnamed receiving water. | Will inform Utility Manager about working on I & I issues. | SSO Reached Receiving Water
58956 | 35659 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-18 16:00 | 2013-01-19 09:00 | 2013-01-21 07:44 | 25500 | gallons | Manhole D-2 at Lift station #4 Doe Creek Drive | Air locked lift station pumps resulted in untreated release from lift station to receiving waters | Flushed check valves and pumps cleared overflow. New lift station under construction. | SSO Reached Receiving Water | Doe Creek
58956 | 35110 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-01-30 07:50 | 2013-01-30 13:15 | 2013-01-30 13:51 | 5000 | gallons | manhole B-1 at Lift Station #2. Cloverdale IN | Manhole overflowing after heavy rain. Unteated Release. | Jet out gravity line with root cutter as soon as vac truck can get to the location. | SSO Reached Receiving Water; Surface Soil
58956 | 35033 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-01 19:30 | 2013-02-02 14:30 | 2013-02-13 15:09 | 150 | gallons | Force main at Small Fry and Stardust Way Cloverdale IN | 6 pvc force main has gash in bottom of pipe causing untreated release. |  | SSO Reached Public Land
58956 | 35034 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-02 07:12 | 2013-02-02 07:50 | 2013-02-13 10:22 | 200 | gallons | Manhole D-2 at Lift Station #4 Cloverdale IN | Daily check on Lift Station revealed that both pumps were running when they shouldn t be. Turned them off and manhole started to overflow. Contacted additional personnel so we could go down in the dry pit and flush check valves. Turned pump on and manhole stopped overflow immediately. Pumps were airlocked again. | New Lift Station under construction. | SSO Reached Receiving Water | Doe Creek
58956 | 35036 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-03 | 2013-02-03 08:40 | 2013-02-03 09:02 | 0 |  | Manhole D-2 Doe Creek Lift Station Coloverdale IN | Lift Station overflowing. Flushed check valves and pumps started pumping. | Going to call Quality Pump Repair. New Lift Station under construction. | SSO Reached Receiving Water | Doe Creek
58956 | 35035 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-04 07:40 | 2013-02-04 07:55 | 2013-02-05 07:38 | 100 | gallons | Manhole D-2 At Lift Station #4 Cloverdale IN | Flushed check valves again and pumps started pumping. | Quality Pump Repair was here first thing this morning to trouble shoot problem. They raised the floats so the influent going into the wet well would not surcharge the pumps. I have checked the Lift Station 3 additional times today and the problem appears to be solved. Graves Plumbing is working on new lift station today! | SSO Reached Receiving Water | Doe Creek
58956 | 34349 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-12 |  | 2013-02-13 10:50 | 0 |  | 154 West Water St | Untreated Release - Ultility worker noticed a residence had an open sewer lateral draining into a hole that was previously dug to repair the sewer. Hole has been open for sometime and was repaired sometime ago. | Appears that the repair didn t get the problem fixed the first time and have just cut the lateral leaving it to drain into the hole. I knocked on the door and no one is home. Left my card with phone number to call me. Checked again this morning and card is still in the door and no one home. I will contact the utility manager and advise him to send a Town Ordinance Violation Letter to the resident to repair ASAP. Does not appear sewer was used overnight. | SSO Affected Private Property
58956 | 34899 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-12 13:30 |  | 2013-02-13 10:50 | 0 |  | 154 West Water Street Cloverdale IN 46120 | Resident at 154 W. Water St. had an open sewer lateral draining into hole that was previously dug to repair sewer. Hole has been open for some time and was repaired some time ago. It appears that the problem was not fixed and they have just cut the lateral leaving it to drain in the hole. | All attempts to contact the resident have so far failed. Notifying Utility Manager to advise him to send Town Ordinance Violation Letter to resident requiring repair ASAP. | SSO Affected Private Property; Subsurface Soil (> 6 inches deep)
58956 | 34767 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-26 09:52 | 2013-02-26 13:20 | 2013-02-27 06:45 | 10000 | gallons | Release occurred at Manhole D-1 @ L.S. #4 | 1.7 Inch heavy rain triggered and untreated release from manhole D-2 @ L.S. #4 | No action taken to minimize or mitigate. There is a manhole at theAmerican Legion off US 231 in Cloverdale that has an I&I issue. Hoping the Utility Manager can get approval from the Board at the March meeting to have it contracted out for repair. | SSO Reached Receiving Water | Doe Creek
58956 | 34774 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-26 10:06 | 2013-02-26 00:10 | 2013-02-26 15:55 | 1500 | gallons | Release occurred at Manhole W-53 off US 231 across from Dollar General Store | 1.7 inch rain event triggered untreated release from Manhole W-53 off Us 231 across from Dollar General Store | Identified some possible I & I problem areas this morning to help eliminate the heavy flow on this gravity main. | SSO Reached Receiving Water | Rabbit Run
58956 | 34770 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-02-26 10:08 | 2013-02-26 13:30 | 2013-02-27 07:00 | 5000 | gallons | Manhole west of lift station #1 on Stardust Road | 1.7 inch rain triggered flooding around Lift Station and an untreated release from the manhole west of Lift Station #1 on Stardust Road | Heavy rain causes flooding around this Lift Station. Going to try to come up with a solution to divert water past the LS and into Doe Creek. | SSO Reached Receiving Water | Doe Creek
58956 | 34880 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-03-17 19:30 | 2013-03-17 21:30 | 2013-03-18 14:40 | 5 | gallons | Clean out uncapped on empty lot. | Untreated release Construction Related 8 Clay Tile sewer main had clog in line and overflowed from a sewer lateral on a empty lot. Installed new clean-out cap. | Cleaned up area and limed. Add this line to do routine sewer cleaning. | SSO Affected Private Property
58956 | 35362 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-12 10:00 | 2013-04-12 10:10 | 2013-04-12 14:30 | 500 | gallons | manhole D-2 at Lift Station #4 | Untreated Release - Construction Related - While Dashiell was digging to tie into new lift station they hit float wires to wet well. Turned pump on hand and pumped down right away. | Repaired float wires lift station is working correctly now. New lift station should be started up early next week if not sooner. | SSO Reached Public Land; SSO Reached Receiving Water | Doe Creek
58956 | 36017 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-17 01:10 | 2013-04-17 03:00 | 2013-04-17 05:22 | 1750 | gallons | Manhole W-53 across form Dollar General Store Rabbit Run Creek | Untreated Release Rain 2.2 inches Received 2 periods of heavy rain totaling 2.2 since yesterday afternoon. Flow from I&I on this line reached capacity and overflowed. | Will clean area when other employees report for work this morning. Waiting on Town to hire additional help to work on areas indentified with I&I problems. | SSO Reached Receiving Water | Rabbit Run
58956 | 36024 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-17 01:10 | 2013-04-17 05:41 | 2013-04-17 06:05 | 10000 | gallons | Manhole west of lift station #1 on Stardust Road Creek | Untreated Release Rain 2.2 inches. Received 2 periods of heavy rain totaling 2.2 since yesterday afternoon. Flow from I&I and flooding around lift station caused overflow at this L.S. | None apply at this time. Waiting on Town to hire additional help to work on areas identified with I&I problems. | SSO Reached Receiving Water
58956 | 36026 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-17 02:05 | 2013-04-17 04:00 | 2013-04-17 08:26 | 115920 | gallons | Cloverdale WWTP Outfall 001 Rabbit Run | Bypass of a Treatment Process Rain 2.2 inches. Received 2 periods of heavy rain since yesterday afternoon totaling 2.2 of rain. Had to bypass 1.3 of flow to UV system to prevent UV s from flooding out. | Working under agreed order at this time for I&I issues. | SSO Reached Receiving Water | Rabbit Run
58956 | 36279 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 | 2013-04-18 23:59 | 2013-04-18 15:20 | 0 |  | Manhole W-101 that flows to Manhole W-53 across from Dollar Store off Highway 231. 515 North Main Street. | Precipitation event(s) caused untreated release from manholes to surrounding ground and receiving waters. Complaint and photo evidenced previously unknown overflows following precipitation. | Following complaint and photo of the area cleaned up debris around manhole. Advised Untility Manager of problem. | SSO Reached Public Land; SSO Reached Receiving Water | Rabbit Run
58956 | 36681 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 20:10 | 2013-04-19 14:50 | 2013-04-26 07:48 | 1127840 | gallons | WWTP Outfall 001 | Precipitation event(s) necessitated bypass of 1/3 of flow to UV system to prevent UVs from flooding out. | Town continues to work under agreed order. | SSO Reached Receiving Water | Doe Creek
58956 | 36459 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 20:10 | 2013-04-19 14:50 | 2013-04-19 15:18 | 403200 | gallons | Cloverdale WWTP Outfall 001 Doe Creek | Rain 3.8 inches Has heavy rain all night totaling 3.8 inches addition to the 2.2 yesterday. Had to bypass 1/3 of flow to UV system to prevent UV s from flooding out. | Town continues to work under agreed order. | SSO Reached Receiving Water | Doe Creek
58956 | 36715 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 20:20 | 2013-04-19 09:18 | 2013-04-19 10:45 | 32000 | gallons | Manhole west of Lift Station #1 on Stardust Road Creek | Untreated Release rain 3.8 inches Had heavy all night totaling 3.8 addition to the 2.2 yesterday. Flooding in area caused lift station to reached capacity and overflow. | Town continues to work under agreed order. | SSO Reached Receiving Water
58956 | 36282 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 20:47 | 2013-04-19 06:10 | 2013-04-19 10:17 | 50000 | gallons | Manhole W-3 located at 2653 East County Road 1000S | Precipitation event(s) caused headworks back up at WWTP resulting in an untreated release from manhole to receiving waters. | Town continues to work under Agreed Order. | SSO Reached Receiving Water | Rabbit Run
58956 | 36280 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-18 21:30 | 2013-04-19 05:23 | 2013-04-19 09:20 | 0 |  | Manhole W-53 across from Dollar General Store | Precipitation event(s) caused untreated release from manhole to receiving waters. | Town continues to work under Agreed Order. | SSO Reached Receiving Water | Rabbit Run
58956 | 36285 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-19 07:00 | 2013-04-19 08:30 | 2013-04-19 11:17 | 10000 | gallons | Manhole D-49 across Highway 231 to east of lift station #4. | Precipitation event(s) caused untreated release from manhole to receiving waters. Construction at lift station #4 continues and the heavy rain caught contractor in middle of tying in new line. Some construction contribution to overflow. | Construction at Lift Station #4 continues. Town continues to work under Agreed Order. | SSO Reached Receiving Water | Doe Creek
58956 | 36212 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-24 00:15 | 2013-04-24 13:50 | 2013-04-24 14:16 | 423555 | gallons | Cloverdale WWTP Outfall #001 Doe Creek | Untreated release rain 2.1 inches |  | SSO Reached Receiving Water | Doe Creek
58956 | 36214 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-24 02:25 | 2013-04-24 10:00 | 2013-04-24 13:14 | 25000 | gallons | Manhole west of Lift Station #1 on Stardust Rd Creek | Untreated release Rain 2.1 inches. Received 2.1 of rain on top of already saturated ground. |  | SSO Reached Receiving Water
58956 | 36714 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-04-28 23:00 | 2013-04-29 11:20 | 2013-04-29 15:48 | 300000 | gallons | Manhole D-49 - Lift Station #4 | Failure of both pumps at a lift station resulted in an untreated release from the manhole to receiving water. | Pulled both pumps removed debris. Adjusted ramp start on both pumps. Will contact neighbors around Lift Station and ask them to call in if they see a red light on at the Lift Station. Will clean and lime the affected area. | SSO Reached Public Land; SSO Reached Receiving Water | Doe Creek
58956 | 37633 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-05-31 09:27 | 2013-05-31 10:35 | 2013-06-01 09:16 | 50 | gallons | M.H.-2-A@L.S. #2 off Stardust Way | Exceeded Max Capacity Rain 1.4 inches Manhole | Continuing to work on I&I issues in Stardust Hills. Clean up debris and lime area. | SSO Affected Private Property; SSO Reached Receiving Water
58956 | 37631 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-01 03:55 | 2013-06-01 05:57 | 2013-06-01 10:06 | 117282 | gallons | Cloverdale WWTP Outfall 001 Doe Creek | Rain 3.0 inches. Had a total of 3 of the Bypass/Overflow Event. Had a total of 3 of rain in the last two days. Had to bypass 1.3 of flow this morning to prevent UV S from flooding out. | Working under Agreed Order at this time for I&I issues. | SSO Reached Receiving Water | Doe Creek
58956 | 37630 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-01 04:20 | 2013-06-01 05:27 | 2013-06-01 10:26 | 2010 | gallons | Manhole west of lift station #1 on Stardust Road | Equipment Failure Rain 1.6 inches. Had alarm a L.S. #1 Pump had failure on soft start. Reset breaker and pumped LS down. | Repair Pump Station. Will have Quality Repair Service look at Lift Station. | SSO Affected Private Property | Ferguson Branch
58956 | 37500 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-10 02:22 | 2013-06-10 07:00 | 2013-06-10 10:18 | 280224 | gallons | Town of Cloverdale Wastewater Treatment Plant154 South Main StreetCloverdale IN | Heavy precipitation event necessitated the bypass of approximately 1/3 of the flow around the WWTP to prevent flooding of the UV array. | Bypassed approximately 1/3 of plant flow to receiving waters.Working under Agreed Order at this time for I & I issues. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Rabbit Run
58956 | 37502 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-10 02:43 | 2013-06-10 09:13 | 2013-06-10 10:45 | 19500 | gallons | Manhole B-2-A at Lift Station #2 off Stardust Way | Heavy precipitation event triggered untreated release as a result of a manhole overflow which affected private property and reached unnamed receiving waters. | Going to jet gravity main to ensure there are no blockages.Working under Agreed Order at this time for I & I issues. | SSO Affected Private Property; SSO Reached Receiving Water
58956 | 37505 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-10 03:15 | 2013-06-10 06:00 | 2013-06-10 11:32 | 16500 | gallons | Manhole W-53 across from Dollar General Store | Heavy precipitation event along with I & I influence caused untreated release from manhole to private property and receiving waters. | Town is under Agreed Order at this time and continues to work on I & I issues. | SSO Affected Private Property; SSO Reached Receiving Water | Rabbit Run
58956 | 37504 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-13 03:02 | 2013-06-10 05:50 | 2013-06-10 11:19 | 4450 | gallons | Manhole west of Lift Station #1 on Stardust Road | Heavy precipitation event along with I & I involvement caused flooding and overflow of untreated release at manhole that reached receiving waters. | Town is under Agreed Order at this time and continues to work on I & I issues. | SSO Reached Receiving Water | Ferguson Branch
58956 | 38381 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-24 08:40 | 2013-06-24 10:45 | 2013-06-25 07:54 | 0 |  | MH B2-A @ L.S. #2 Manhole Pipe Failure | Unknown Manhole Pipe Failure Town employees have been hauling dirt to make a rod to this MH for the past couple of weeks. This morning they found the overflow. We had jetted it after the last rain event and overflow on 6/10/2013 and found little or no blockage. Employees jetted line 4 time and opened line stopping the overflow. Roots appear to be the problem. Employees are working to clear woods to have access to sewer line and repair drop manhole on 6/25 | Removed Blockage Repaired Pipe | SSO Affected Private Property; SSO Reached Receiving Water
58956 | 39499 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-07-07 11:40 | 2013-07-07 17:15 | 2013-07-08 08:23 | 0 |  | Force Main Small Fry & Stardust | 6 inch pvc force main had split in bottom of pipe | Repaired Pipe | SSO Reached Public Land
58956 | 39771 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-08-12 12:35 | 2013-08-12 13:10 | 2013-08-13 09:43 | 0 |  | Manhole D-49 | Town employee heard alarm on LS coming back from his lunch. Both pumps were on auto but failed to com on? Turned pumps on hand and pumped wet well down. Called Chris with S&K Equipment. He suggest checking and cleaning transducer which we did. Lift Station up and running again. Will put cleaning of transducer on weekly Lift Station maintenance schedule. | Repaired Pump Station | SSO Reached Receiving Water | Doe Creek
58956 | 40658 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-09-30 10:45 | 2013-09-30 12:45 | 2013-09-30 16:38 | 0 |  | M H A-74 | Manhole * main had grease and roots in it. | Removed Blockage See Report | SSO Affected Private Property
58956 | 41938 | IN0022616 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-11-15 11:45 | 2013-11-15 04:30 | 2013-11-18 08:00 | 0 |  | 270 Down Boy Way Force Main | Pipe Failure 6 PVC force main had 3 split in pipe. Spikers Excavating was call in to repair leak. | Repaired Pipe | SSO Reached Public Land
58956 | 37619 | IN0022616 Affected Waterbody name given is Creek | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-06-01 05:00 | 2013-06-01 06:15 | 2013-06-01 11:30 | 1275 | gallons | M.H. B-2-A @ L.S. #2 off Stardust Way | Exceeded Max Capacity Rain 1.6 inches. Had additional 1.6 of rain in short period of time early this morning. This caused MH to exceed capacity. Will camera line if we can push our camera that far when flow goes down to check for any restrictions in line. | Continuing to work on I&I issues in Stardust Hills. | SSO Affected Private Property; SSO Reached Receiving Water
58956 | 43569 | IN0022616 Outfall 001 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-12-21 07:03 | 2013-12-21 14:30 | 2013-12-21 15:15 | 11200 | gallons | MH W-3 Clarence Sharder Prop. 2653 E Co Rd 1000S | Rain 2.3 inches Exceeded Max Capacity have had 6 of snow melting for last 3 days. then received 2.3 of rain that continues to fall. Plant LS unable to keep up. | See Report | SSO Affected Private Property; SSO Reached Receiving Water | Rabbit Run
58956 | 43571 | IN0022616 Outfall 001 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-12-21 09:28 | 2013-12-21 14:30 | 2013-12-21 15:38 | 1490 | gallons | Mh W-25 North of MH W-3 on Co Rd 1000 S | Exceeded Max Capacity rain 2.3 inches Have had 6 of snow melting for last 3 days. Then received 2.3 of rain that continues to fall. Plant L.S. unable to keep up. | See Report | SSO Reached Receiving Water | Rabbit Run
58956 | 41632 | IN0022616 Outfall 001 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-10-31 16:30 | 2013-11-02 13:49 | 2013-11-04 14:30 | 0 |  | Branneman Residence 307 E Logan St. Cloverdale In | Unknown Rain 2.7 inches Homeowner has sewer backup and running out of the lateral. Town employees jetted sewer line from MH D-47 east 420ft. Homeowners lateral is only 300ft from MH D-47 so Towns main is open and flowing. Advise homeowner to hire a plumber. |  | SSO Affected Private Property
58956 | 41633 | IN0022616 Outfall 001 | CLOVERDALE MUNICIPAL WASTE WATER TREATMENT PLANT | Putnam | 2013-10-31 18:45 | 2013-11-01 13:59 | 2013-11-01 13:38 | 0 |  | Outfall 001 | Exceeded Max Capacity Rain 2.7 inches Received 2.7 of rain. Had to bypass 1/3 of flow so UV lights would not flood out. | See Report | SSO Reached Receiving Water | Rabbit Run
59738 | 34971 | IN0039624 | VAN BIBBER LAKE CONSERVANCY DISTRICT | Putnam | 2013-02-07 13:00 | 2013-02-07 14:00 | 2013-02-07 16:38 | 2000 | gallons | manhole at Lot 5190 Van Bibber Lake | 8 main stopped up with clothing resulting back up and overflow from manhole. | Roto rootered main and removed obstruction. Clear water came out of the manhole. Sprayed area with bleach. | SSO Reached Public Land; SSO Reached Receiving Water | Glenn Flint Lake
58541 | 36448 | IN0045527 | CLEAR CREEK CONSERVANCY DISTRICT | Putnam | 2013-04-19 20:00 | 2013-04-19 | 2013-04-21 12:08 | 30000 | gallons | Manhole G41 | Precipitation event triggered untreated release from manhole to a ditch to receiving waters. | Raked up paper spayed with bleach. Wer are going to camera more sewer lines. | SSO Reached Public Land; SSO Reached Receiving Water | Heritage Lake
58541 | 36358 | IN0045527 | CLEAR CREEK CONSERVANCY DISTRICT | Putnam | 2013-04-22 | 2013-04-22 09:30 | 2013-04-22 13:11 | 0 |  | MH 621 A Ground to Heritage Lake | Equipment Failure At first we thought the main was plugged up. But then found out the Lift Station was not running. | Dripped chlorine bleach in over flow stream. Lowered high alarm float in Lift Station | SSO Affected Private Property; SSO Reached Receiving Water | Heritage Lake
58841 | 43574 | IN0020001 | RIDGEVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Randolph | 2013-12-21 10:00 | 2013-12-22 10:00 | 2013-12-23 07:34 | 0 |  | 002 Vine St Lift Station | Rain CSO 004 also released started 12-21-2013 @ 3:30pm will test and record actual amounts stopped 12-23-2013 @ 7:30am | See Report | SSO Reached Receiving Water | Ridge Run
58841 | 43576 | IN0020001 | RIDGEVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Randolph | 2013-12-21 10:30 | 2013-12-22 15:00 | 2013-12-23 07:34 | 0 |  | 101 WWTP Lift Station | Rain CSO 004 also released started 12-21-2013 @ 3:30pm will test and record actual amounts. Stopped 12-23-2013 @ 7:30am | See Report | SSO Reached Receiving Water | Mississinewa River
59574 | 35562 | IN0020729 | PARKER CITY MUNICIPAL WASTE WATER TREATMENT PLANT | Randolph | 2013-01-10 15:00 | 2013-01-15 16:30 | 2013-01-16 17:26 | 600000 | gallons | Parker City WWTP Outfall 002 to Arbogast Ditch | Precipitation event and snow melt resulted in untreated release from WWTP Outfall 002 to receivng waters Arbogast Ditch. Inflow exceeded plant capacity. | Ran plant at maximum flow to help catch up. Town was denied a grant to repair our I/I problem. The town is borrowing $900000 to make proper repairs to system. Bids are being accepted now. | SSO Occurred at Treatment Plant
59574 | 35944 | IN0020729 | PARKER CITY MUNICIPAL WASTE WATER TREATMENT PLANT | Randolph | 2013-01-10 15:00 |  | 2013-01-11 18:06 | 0 |  | Outfall 002 to Arbogast Ditch | Precipitation event and snow melt caused an untreated release from WWTP outfall to receiving waters. | Town was denied a grant to repair our I & I problems. The town is going to borrow $900000 to make proper repairs to the the system. Bids are being accepted now on that project. | SSO Reached Receiving Water
59574 | 43577 | IN0020729 | PARKER CITY MUNICIPAL WASTE WATER TREATMENT PLANT | Randolph | 2013-12-21 | 2013-12-23 16:00 | 2013-12-24 11:57 | 250000 | gallons | Outfall #002 | Rain 4.17 inches 4.17 inches of rain plus 5 snow melt. | See Report | SSO Reached Receiving Water
59606 | 34392 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-01-11 08:00 | 2013-01-11 13:00 | 2013-01-11 15:22 | 50000 | gallons | Jackson Pike Lift Station to Little Mississinawa | Combination of snow melt & rainfall pumps couldn t keep up. All three pumps running. Notified Scott Thompson in person. | Continue to monitor to minimize bypass. | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35943 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-01-11 08:00 | 2013-01-11 13:00 | 2013-01-11 15:22 | 50000 | gallons | Jackson Pike Lift Station | Precipitation event and snow melt exceeded capacity of lift station pumps resulting in untreated release/bypass from the lift station to receiving waters. | All three pumps running at capacity. Notified Scott Thompson in person. Continue to monitor to minimize bypass | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35228 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-01-13 04:30 | 2013-01-13 05:20 | 2013-01-14 11:47 | 0 |  | Manhole at Sterling and Glyn Ellen Drive Union City IN | Precipitation event and Pond Pump station failure resulted in an Untreated Bypass to the Little Mississenawa River | Reset and restarted pumps. Continued to monitor pump station. | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35225 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-01-13 05:30 | 2013-01-13 07:15 | 2013-01-14 11:46 | 4489000 | gallons | Union City Municipal WWTP Union City IN | Pump failure during/following precipitation event resulted in Untreated Bypass from the headworks of the treatment plant to the Little Mississenawa River. | Reset pumps/started and continued to monitor to minimize bypass. | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35227 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-01-13 06:00 | 2013-01-14 01:00 | 2013-01-14 11:47 | 50000 | gallons | Jackson Lift Station Union City IN | Precipitation event resulted in untreated bypass from Jackson Lift Station to the Little Mississenawa River | Lift Station could not keep up with flow. Continued to monitor pumps to minimize bypass. | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35222 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-01-13 20:30 | 2013-01-14 10:30 | 2013-01-14 11:47 | 4489000 | gallons | Union City Municipal WWTP Union City IN | Untreate Release from Headworks to Little Mississenawa River. | Storage full/ pond & EQ. Monitor and wait for flow to decrease. | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35432 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-04-10 19:55 | 2013-04-11 18:10 | 2013-04-12 07:11 | 50000 | gallons | Jackson Lift Station Union City WWTP | Precipitation event created excess flow to WWTP and necessitated untreated release from Hackson Lift Station to receiving waters. | Diverted exess flow from North Plant inlet to detention pond. Diverted excess flow from Headworks & Primaries to equalizer tank until that tank was full. | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35434 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-04-11 21:25 | 2013-04-12 06:55 | 2013-04-12 07:20 | 50000 | gallons | Jackson Lift Station at Union City WWTP | Precipitation event caused excess flow to the WWTP and necessitated flow diversion from North Inlet to detention pond until pond was full. Untreated release to receiving waters. | At 7:30 pm 4/12/13 flow was diverted back to plant headworks | SSO Reached Receiving Water | Little Mississinewa River
59606 | 35395 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-04-12 08:10 | 2013-04-12 13:30 | 2013-04-12 15:36 | 2457000 | gallons | Union City Municipal WWTP Union City IN | A major precipitation event triggered the need for an Untreated Release of effluent from the Union City WWTP. Bypass from the headworks to the Little Mississenawa River. All retention ponds and tanks were full. Influent overwhelmed the plant capacity. | Plant personnel monitored the flow to minimize impact on the river. | SSO Reached Receiving Water | Little Mississinewa River
59606 | 36059 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-04-15 18:15 | 2013-04-16 13:00 | 2013-04-18 10:10 | 150000 | gallons | Jackson Lift Station | Precipitation event exceeded capacityof holding tanks and ponds. All pumps running at maximum. Untreated release from Lift Station to receiving waters. |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Little Mississinewa River
59606 | 38371 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-06-13 02:00 | 2013-06-13 12:00 | 2013-06-13 14:04 | 0 |  | Jackson Lift Station Little Missisinawa | Rain 2.66 inches Plant personnel monitored plant to insure all equipment was working properly. | Diverted to north end of pond. | SSO Affected Private Property | Little Mississinewa River
59606 | 43573 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-12-21 07:35 | 2013-12-23 03:00 | 2013-12-23 10:09 | 540000 | gallons | Jackson Lift Station | rain 3.25 inches Influent flow exceeded pump station. Capacity all detention pond and tank wee full. | See Report | SSO Affected Private Property | Little Mississinewa River
59606 | 43572 | IN0020982 | UNION CITY MUNICIPAL SEWAGE TREATMENT PLANT | Randolph | 2013-12-21 21:15 | 2013-12-23 08:00 | 2013-12-23 10:09 | 4489000 | gallons | Headworks | Rain 3.25 inches Excessive rain and snow melt. Plant was operating at 100% of disign all detention pond and tank were full. | See Report | SSO Reached Receiving Water | Little Mississinewa River
59624 | 36726 | IN0021024 | WINCHESTER WASTE WATER TREATMENT PLANT | Randolph | 2013-04-30 11:00 |  | 2013-04-30 10:58 | 1200000 | gallons | Coty of Winchester WWTP | Plant headworks construction coupled with precipitation event(s) exceeded capacity of headworks bypass pumping resulting in the bypass of a treatment process and essentially a partially treated release. Unable to get lagoons empty due to rain and snow melt in spring. | Flow will be blended with plant effluent and will be chlorinated and all plant permit required tests will be done. Could possibly high E.coli numbers. Have never attempted blend during E.coli season. We have installed two new Raw Sewage pumps to increase plant pumping capacity during project when plant was down along with new screening unit in headworks. | SSO Occurred at Treatment Plant
59802 | 41683 | IN0021512 | FARMLAND FIRE DEPARTMENT | Randolph | 2013-10-31 22:00 | 2013-11-01 05:00 | 2013-11-06 11:45 | 0 |  | Wastewater Lagoon | Exceeded Max Capacity Exceeded influent vault s capacity. Diverted sewage flowed south out of the vault to a low laying area used to carry rainwater. Water flowed path north to ditch line and west to stream. Reported to operator 11-5-13 @ 4:00pm | See Report | SSO Occurred at Treatment Plant
59802 | 41997 | IN0021512 | FARMLAND FIRE DEPARTMENT | Randolph | 2013-11-17 18:00 | 2013-11-18 09:00 | 2013-11-18 11:39 | 0 |  | Wastetater Lagoon | Rain 2.5 inches 2 1/2 rainfall exceeded volts capacity causing overflow | See Report | SSO Occurred at Treatment Plant
59802 | 43578 | IN0021512 | FARMLAND FIRE DEPARTMENT | Randolph | 2013-12-21 22:00 | 2013-12-22 10:00 | 2013-12-26 07:44 | 0 |  | Manhole #114 409 S Plum St | Rain 4.25 inches 12-21-13 at 10:00pm manhole # 114 was spotted overflowing around the bolted down lid. Water from the overflow was running to an empty vacant lot on East side of Plum St. | See Report | SSO Affected Private Property
100087 | 37493 | IN0063177 | Cardinal Ethanol LLC | Randolph | 2013-06-09 |  | 2013-06-10 | 0 |  | Manhole outside of Water Treatment. Dry soil Gravel | Untreated Release Equipment Failure There are two discharge lines that drain settling pond 1 into settling pond 2. It was believed that both lines were open however on 6/9/13 the manhole outside of water treatment began to overflow. At that time investigation began and it was believed that both discharge lines had become plugged. Upon further investigation the morning of 6/10/13 it was discovered that the valve for one of the drain lines was completely closed. Once the valve was opened flow began into settling pond #2 again. | When it was discovered that a manhole was overflowing investigation began into the cause. At the start of the investigation it was believed that both discharge lines from settling pond #1 to Settling pond #2 were plugged. When the floating suction tube on one of the discharge lines was pulled to shore and investigated it was found to be clean. Employees then attempted to determine if the valve for that line was closed but were unable to open/close that valves for the discharges lines so it was believed that both were open and a contractor would have to be called in to remove the plug in the lines. On 6/10/13 a maintenance employee was able to open the valve for the second discharge line from settling pond #1 to settling #2. allowing flow into settling pond #2 again. Settling ponds will be emptied and cleaned of biological growth during facility shutdown scheduled for the week of July 29 2013. | SSO Affected Private Property
100087 | 38565 | IN0063177 | Cardinal Ethanol LLC | Randolph | 2013-06-25 23:00 | 2013-06-28 13:00 | 2013-06-26 13:30 | 1556000 | gallons | Manholes east of RO Building | Equipment Failure Manhole The discharge lines that drain settling pond #1 into settling pond #2 both became plugged. This caused settling pond #1 to back up and overflow at the manholes of the lines that feed settling pond #1 | Removed Blockage employees pulled the floating suction tube on one of the discharge lines of settling pond #1 to shore and discovered that it was covered in biological plant growth which is believed to have been blocking flow. The plant growth was removed and water began to flow again. The line plugged again on 6/28/13. At that time pumps were placed at pond #1 to assist in moving water from pond #1 to pond #2 stop overflow of manholes. Mechanical pumps were set up to pump water from pond #1 to pond #2. From 6/28/13 - 7/3/13 mechanical means were used to drain pond#1. On 7/2/13 approval was given by IDEM to bypass the ponds and on 7/3/13 pond #1 was completely emptied and cleaned out. Settling pond #2 will be emptied and cleaned of biological growth during facility shut down scheduled for the week of July 29 2013. Regular visual observations of the ponds and /or manway flow between ponds will occur to ensure that levels are not rising in settling pond #1 or decreasing too much in settling pond #2 indicating that there is another plug.
100087 | 39314 | IN0063177 | Cardinal Ethanol LLC | Randolph | 2013-07-24 12:30 | 2013-07-31 14:00 | 2013-07-24 11:30 | 0 |  | Outfall 001 (bypass of settling ponds) | Equipment Failure The system has a bypass to allow cleaning of the 2 setting ponds which have been plugging up (see June report). In order to lower the water level enough to clean pond #2 authorization to bypass the ponds was obtain from IDEM via email. The standard outfall was used to discharge effluent and samples taken to verity compliance with water permit limits. | See Report | SSO Reached Receiving Water
100087 | 38033 | IN0063177 The water that was released due to the overflow of the manhole did not reach any aquatic life or receiving stream. The overflow was the release of non-contact utility water without it traveling to the two on-site facility settling ponds. | Cardinal Ethanol LLC | Randolph | 2013-06-25 23:00 |  | 2013-06-26 13:30 | 0 |  | Manholes East of RO Building | Equipment failure Pipe Failure Manhole The discharge lines that drain settling pond #1 into settling pond #2 both became plugged. This caused settling pond #1 to back up and overflow at the manholes of the lines that feed settling pond #1. | Employee pulled the floating suction tube on one of the discharge lines of settling pond #1 to shore and discovered that it was covered in biological plant growth which is believed to have been blocking flow. The plant growth was removed and water began to flow again. Settling ponds will be emptied and cleaned of biological growth during facility shutdown scheduled for the week of July 29 2013. Regular visual observations of the ponds and/or manway flow between ponds will occur to ensure that levels are not rising in settling pond #1 or decreasing too much in settling pond #2 indicating that there is another plug. | SSO Occurred at Treatment Plant
100087 | 38028 | IN0063177: The water that was released due to the overflow of the manhole did not reach any aquatic life or receiving stream. The overflow was the release of non-contact utility water without it traveling to the two on-site facility settling ponds. | Cardinal Ethanol LLC | Randolph | 2013-06-09 13:00 | 2013-06-10 20:00 | 2013-06-10 13:00 | 0 |  | Manholes East of RO Building | Equipment failure Manhole Pipe Failure There are two discharge lines that drain settling pond 1 into settling pond 2. It was believed that both lines were open however on 6/9/13 the manhole outside of water treatment began to overflow. At that time investigation began and it was believed that both discharge lines had become plugged. Upon further investigation the morning of 6/10/13 it was discovered that the valve for one of the drain lines was completely closed. Once the valve was opened flow began into settling pond #2 again. | When it was discovered that a manhole was overflowing investigation began into the cause. At the start of the investigation it was believed that both discharge lines from settling pond #1 to settling pond #2 were plugged. When the floating suction tube on one of the discharge lines was pulled to shore and investigated it was found to be clean. Employees then attempted to determine if the valve for that line was closed but were unable to open/close the valves for the discharge lines so it was believed that both were open and a contractor would have to be called in to remove the plug in the lines. On 6/10/13 a Maintenance employee was able to open the valve for the second discharge line from settling pond #1 to settling pond #2 allowing flow into settling pond #2 again. Settling ponds will be emptied and cleaned of biological growth during facility shutdown scheduled for the week of July 29th 2013. | SSO Occurred at Treatment Plant
59655 | 43579 | IN0023779 | MILAN WASTE WATER TREATMENT PLANT | Ripley | 2013-12-22 | 2013-12-22 09:00 | 2013-12-23 08:02 | 30800 | gallons | See Report | Rain 3.3 inches To much rain at once the EQ Basin filled up to 100000 gal. No often place to pump to. | See Report | SSO Reached Receiving Water
1592 | 36739 | IN0052523 | BROWNING RECREATION CAMP | Ripley | 2013-05-01 | 2013-05-01 | 2013-05-01 10:18 | 0 |  | Brownings Camp | Ammonia too High. BOD too Low. | Keep sludge | SSO Affected Private Property
1592 | 39521 | IN0052523 | BROWNING RECREATION CAMP | Ripley | 2013-07-05 | 2013-07-05 23:59 | 2013-07-05 11:56 | 0 |  | Ammonia 45 E-Coli 1011.9 | I just move sludge from one tank to mixed lic so it may get better I hope. | See Report
60701 | 43580 | IN0061531 | WESTERN RUSH COUNTY REGIONAL SEWAGE DISTRICT WASTE WATER TREATMENT PLANT | Rush | 2013-12-21 15:00 | 2013-12-24 03:00 | 2013-12-24 10:43 | 617000 | gallons | Treatment plant | Rain 5 inches Rain fell in 24hrs period | See Report | SSO Reached Receiving Water | Goddard Ditch
59628 | 35485 | IN0109746 | ANDERSON TOWNSHIP REGIONAL SEWAGE DISTRICT | Rush | 2013-01-13 18:00 | 2013-01-13 23:00 | 2013-01-14 12:54 | 3000 | gallons | Woods Lift Station | Precipitation event combined with snow melt necessitated shutting down the Woods lift station to prevent overflow in more populated area. Untreated release bypassed from Lift Station to surrounding ground. | Shut down lift station to prevent overflow in more poplulated area. | SSO Reached Public Land
12541 | 43621 | IN0021911 Outfall 001 | Morgan Foods Incorporated | Scott | 2013-12-21 |  | 2013-12-23 15:30 | 1500000 | gallons | Wastewater Lagoon Outfall | Rain 2.5 inches Heavy rain fall occurred on Dec 21 & 22. Today it was discovered that the Lagoon was overflowing. It is unknown what time the overflow began but the heaviest rain fell during the night on Dec 21. The WW Plant was not staffed on Dec 22 so the overflow was not discovered until today. | See Report | SSO Reached Receiving Water | Muscatatuck River
50990 | 35511 | IN0025135 | AUSTIN MUNICIPAL SEWAGE TREATMENT PLANT | Scott | 2013-01-13 13:00 | 2013-01-14 07:00 | 2013-01-14 08:20 | 500 | gallons | Manhole 97A 112 105 | Precipitation event exceeded capacity of lift station resulting in and untreated release to the surrounding ground and stick ditch. | Working on grant to put in anothr force main on main lift station. | SSO Reached Public Land; SSO Affected Private Property | Stick Run
50990 | 35210 | IN0025135 | AUSTIN MUNICIPAL SEWAGE TREATMENT PLANT | Scott | 2013-01-30 07:00 | 2013-01-30 16:00 | 2013-01-31 08:08 | 600 | gallons | Manhole 460 97a City of Austing IN | Precipitation event resulted in untreated release from manhole 460 97a. | Too much rain lift station can t handle the volume. Working on grant to install another force main on main lift station | SSO Reached Public Land; SSO Reached Receiving Water | Stick Run
50990 | 34714 | IN0025135 | AUSTIN MUNICIPAL SEWAGE TREATMENT PLANT | Scott | 2013-02-26 07:00 | 2013-02-26 16:00 | 2013-02-27 07:50 | 1000 | gallons | 97 104 460 112 | unknown | Working on grant for collection system | SSO Reached Receiving Water
50990 | 40981 | IN0025135 | AUSTIN MUNICIPAL SEWAGE TREATMENT PLANT | Scott | 2013-10-06 08:00 | 2013-10-06 20:00 | 2013-10-07 07:57 | 0 |  | Manhole 112102103460 | 3.7 inches of rain pumps could not keep up. | Received grant to update Lift Station
50990 | 43614 | IN0025135 | AUSTIN MUNICIPAL SEWAGE TREATMENT PLANT | Scott | 2013-12-22 03:00 | 2013-12-22 16:00 | 2013-12-23 11:38 | 5000 | gallons | 45697a8451 | 3 of rain pumps would not handle the flow | See Report | SSO Reached Receiving Water
50001 | 38891 | IN0032867 | SHELBYVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Shelby | 2013-06-20 14:00 | 2013-06-25 08:30 | 2013-06-26 08:42 | 0 |  | Fairland Road Lift Station 1736 W 400 N Hankins Ditch | Untreated Release Equipment Failure. Plant O&M Team leader viewed Guard Dog and found no pumps running. Went to pump station and round controller locked up and turned pumps on manual. | Used City vactor sewer trucks to clean up spillage and wash down ditch. Hired Fluid Waste Services to clean 200 of Hankins Ditch. Employees rewired station and added additional float controls that will override controller and call plant for high level. Operators ordered to visit lift station at least once a day every day from now on. | SSO Reached Receiving Water | Hankins Ditch
50001 | 43624 | IN0032867 | SHELBYVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Shelby | 2013-12-21 21:40 | 2013-12-22 15:10 | 2013-12-23 11:46 | 2793000 | gallons | Conrey Street Lift Station 390 Conrey St Shelbyville In 46176 | Rain 4.73 inches Over 473 of rain came down during Saturday & Sunday with a saturated ground already. this on top of 5 of melted snow. | See Report | SSO Reached Receiving Water | Big Blue River
50963 | 43626 | IN0038431 | CREEKSIDE MOBILE HOME PARK | Shelby | 2013-12-21 16:00 | 2013-12-23 21:00 | 2013-12-24 15:16 | 318000 | gallons | Effluent pumping Structure | Rain 5.10 inches See Report | See Report | SSO Reached Receiving Water | Sugar Creek
107212 | 39815 |  | Luce Township Regional Sewer District | Spencer | 2013-08-27 11:00 |  | 2013-08-27 20:23 | 0 |  | Force main highway 161 | Unknown as soon as break was finally located steps were taken to do emergency repair. Break is in soybean field. |  | SSO Affected Private Property
59687 | 39590 | IN0020605 | SANTA CLAUS SEWAGE TREATMENT PLANT | Spencer | 2013-07-09 15:30 | 2013-07-09 16:00 | 2013-07-10 12:52 | 0 |  | #4 Lift Station Force Main | Force main leak was called in by farmer once leak was found lift station was shut down and locates were called in. Wet well had enough reserve capacity to hold wastewater until line was repaired. The force main had a hole in the bottom of the line and it was a cast line. Line was repaired and station put back in operation. | See Report | SSO Affected Private Property
13904 | 35794 | IN0021067 | Rockport Sewage Treatment Plant | Spencer | 2013-01-11 | 2013-01-11 12:00 | 2013-01-11 15:45 | 5000 | gallons | Manhole on Center and First | An as yet unidentified pipe that may be a force main from a nearby lift station was reported as broken causing an untreated release to the surrounding ground. | Crews doing dye testing to determine source of the leak. Crews dispatched and on site to perform repairs. | SSO Reached Public Land
13904 | 35661 | IN0021067 | Rockport Sewage Treatment Plant | Spencer | 2013-01-20 13:30 | 2013-01-20 13:45 | 2013-01-21 10:11 | 500 | gallons | Manhole at North and Center Streets | Main sewer blockage resulted in untreated release from manhole to ground surrounding the manhole. | Jet rodded sewer line blockage removed flow restored. | SSO Reached Public Land
12105 | 40975 | IN0051845 Outfall 002 | Indiana Michigan Power Rockport Plant | Spencer | 2013-10-06 11:30 | 2013-10-06 23:00 | 2013-10-07 08:05 | 0 |  | AEP Rockport Plant Flyash Landfill | Rain >6 inches | See Report | SSO Reached Receiving Water | Honey Creek; Ohio River
107212 | 36864 | No NPDES Permit | Luce Township Regional Sewer District | Spencer | 2013-05-14 08:00 | 2013-05-14 09:30 | 2013-05-15 10:20 | 50 | gallons | Main lift station 2002 N 550W | Equipment Failure Standing overflow around lift station wet well. Slow release thru manhole covers neutralized with lime. | Repaired Pump Station. Replaced damaged part manually pumped down wet well. Rebooted system normal operation. Neutralized by spraying area with lime continue to monitor lift station daily. | SSO Affected Private Property
107212 | 37013 | No NPDES Permit | Luce Township Regional Sewer District | Spencer | 2013-05-16 13:00 | 2013-05-16 15:00 | 2013-05-17 16:05 | 100 | gallons | Intersection of CR 850W & 400 Eureka IN | Equipment Failure Pipe Failure Air release valve broke flooding manhole. Slow release into field. Neutralized with lime. | Repaired Pipe Replace a valve release valve next day. Shut off flow to damaged valve by closing ball valve. Replaced broken air release valve. Continuous monitoring of pipes lines and valve boxes/ manholes. | SSO Affected Private Property
15848 | 39174 | IN0021661 | ROCHESTER WASTE WATER TREATMENT PLANT | St Joseph | 2013-06-29 15:30 | 2013-06-29 16:00 | 2013-06-30 12:43 | 0 |  | 418 Pontiac St Rochester In | Sewer line plugged with disinfection wipes. | See Report | SSO Basement Backup
11983 | 35591 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-01-09 18:55 | 2013-01-09 20:15 | 2013-01-10 11:57 | 0 |  | 5023 Kirkshire Drive | Main line blockage resulted in untreated release into residential basement. | Jetrodder number 488 opened main line. Will CCTV the main line to find problem. | SSO Basement Backup; SSO Affected Private Property
11983 | 35122 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-01-28 06:15 | 2013-01-28 08:15 | 2013-01-28 16:03 | 19900 | gallons | City of South Bend South Bend IN. | 8 abandoned in place pipe on old Primary CL2 tank rusted through and fell into the Primary CL2 tank causing water to pour in from the #1 Primary Clarifier causing a partially treated release to the St. Joseph River. | Leak discovered withing 2 hours. Dammed the drain to the tank. the pipe elbow has been replaced with a blind flange and the outfall drain valve has been dammed up temporarily. We will permanently close off the tank drain to the St. Joseph River. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
11983 | 35204 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-01-29 11:22 |  | 2013-01-30 11:30 | 0 |  | Basement at 1706 West Ewing Avenue(?) South Bend IN | Precipitation event resulted in basement back up | Untreated Release. Information turned over to engineering for review. Capacity issue. | SSO Basement Backup; SSO Affected Private Property
11983 | 35203 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-01-29 15:05 |  | 2013-01-30 11:30 | 0 |  | Basement at 1206 Lawrence Street South Bend IN | Precipitation event resulted in basement backup | Information turned over to engineering for review. Capacity issue. | SSO Basement Backup; SSO Affected Private Property
11983 | 34852 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-02-15 09:10 | 2013-02-15 10:30 | 2013-02-15 12:40 | 0 |  | Main Line South Bend IN | Unknown Untreated Release | Jet Rodder Number 466 opened the blockage. We will CCTV our main line to find the problem. | SSO Basement Backup; SSO Reached Public Land; Surface Soil
11983 | 37758 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-09 16:36 | 2013-06-09 17:25 | 2013-06-11 23:28 | 0 |  | Main line at 17295 Farmington Sq Rd 17313 Farmington Sq Rd | Untreated Release | Jet rodder number 461 opened the blockage. We will CCTV our main line on 6-10-13 to find the problem. | SSO Affected Private Property
11983 | 38235 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 | 2013-06-29 | 2013-07-02 07:34 | 0 |  | 1602 Bowman St | Rain 5 inches Heavy Rain on 6-29-13 | Heavy rain on 6-29-13 Resident called on 7-1-13 Basement being cleaned at this time. Turn over to engineering for review. | SSO Basement Backup
11983 | 38234 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 | 2013-06-29 | 2013-07-02 07:34 | 0 |  | 1608 Leer St | Rain 5 inches Heavy rain on 6-29-13 | Heavy rain on 6-29-13. resident called on 7-1-13 basement being cleaned at this time. Turn over to engineering for review. | SSO Basement Backup
11983 | 38233 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 | 2013-06-29 | 2013-07-01 09:32 | 0 |  | 1302 E Woodside St | Rain 5 inches Heavy rain 5 inches. | Heavy rain on 6-29-13. Resident called on 6-30-13 at 10:55am. Basement being cleaned at this time. Turn over to engineering for review. | SSO Basement Backup
11983 | 39170 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:05 | 2013-06-29 17:30 | 2013-06-30 10:10 | 0 |  | 128 Jenning St | Rain 5 inches heavy rain | See Report | SSO Basement Backup
11983 | 39168 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:08 | 2013-06-29 17:30 | 2013-06-30 10:10 | 0 |  | 3814 St Joseph St | Rain 5 inches heavy rain. | See Report | SSO Basement Backup
11983 | 39166 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:10 | 2013-06-29 17:30 | 2013-06-30 10:10 | 0 |  | 3522 Addison S | Rain 5 inches heavy rain. | See Report | SSO Basement Backup
11983 | 39165 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:11 | 2013-06-29 17:30 | 2013-06-30 10:10 | 0 |  | Rain 5 inches heavy rain | Rain 5 inches heavy rain | See Report | SSO Basement Backup
11983 | 39164 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:12 | 2013-06-29 17:30 | 2013-06-30 10:10 | 0 |  | 1125 Altgeld St | Rain 5 inches Heavy rain. | See Report | SSO Basement Backup
11983 | 39171 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:14 | 2013-06-29 17:30 | 2013-06-30 10:10 | 0 |  | 3730 S St Joseph SP | Rain 5 inches heavy rain | See Report | SSO Basement Backup
11983 | 39161 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:14 | 2013-06-29 17:30 | 2013-06-30 15:08 | 0 |  | 1142 Altgeld St | Rain 5 inches heavy rain | See Report | SSO Basement Backup
11983 | 39159 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-06-29 17:14 | 2013-06-29 17:30 | 2013-06-30 14:57 | 0 |  | 1142 Altgeld St | Rain 5 inches Heavy Rain | See Report | SSO Basement Backup
11983 | 39520 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-07-06 13:21 | 2013-07-06 15:34 | 2013-07-07 10:45 | 0 |  | 3301 Portage Ave South Bend IN | Directional drilling at this location could be the cause. | Removed Blockage
11983 | 39519 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-07-06 13:21 | 2013-07-06 15:34 | 2013-07-07 10:45 | 0 |  | 3301 Portage Ave South Bend In | Directional drilling at this location could be the cause. | Removed Blockage
11983 | 39427 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-07-18 17:45 | 2013-07-18 18:00 | 2013-07-19 08:48 | 0 |  | Riverside Dr (Cushing Extended) | Pipe blockage wastewater came out of the top of manhole. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Saint Joseph River
11983 | 39593 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-07-26 10:45 | 2013-07-26 13:45 | 2013-07-27 08:12 | 0 |  | CSO 039 (27th St) | Construction Related Sewer cleaning (jetting) of sewer line resulted in total sewer flows slightly exceeding capacity of both downstream lift station pumps. | See Report | SSO Reached Receiving Water | Saint Joseph River
11983 | 39594 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-07-26 13:40 | 2013-07-26 13:45 | 2013-07-27 08:19 | 0 |  | CSO 039 (27th St) | Construction Related Sewer cleaning (jetting) of sewer line resulted in total sewer flows slightly exceeding capacity of both downstream lift station pumps | See Report | SSO Reached Receiving Water | Saint Joseph River
11983 | 40443 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-19 12:30 | 2013-09-19 15:15 | 2013-09-26 15:20 | 0 |  | Intersection of Michigan St and Park | Rain 2.26 inchesExceeded Max Capacity Rainfall exceeded lift station pumping capacity and surcharge overflowed out the top of two manholes just before wet well. | See Report | SSO Reached Receiving Water | Saint Joseph River
11983 | 40401 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-19 12:30 | 2013-09-19 15:15 | 2013-09-26 15:30 | 0 |  | Intersection of Michigan St and Park | Rain 2.26 inch Exceeded Max Capacity Rainfall exceeded lit station pumping capacity and surcharge overflowed out the top of two manholes just before lift station wet well. | See Report | SSO Reached Receiving Water
11983 | 40252 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-19 12:44 |  | 2013-09-20 08:23 | 0 |  | Basement at 921 E Irvington Ave | Heavy rain over 3 inches | Forwarded to engineering for review of possible sewer line capacity issur. | SSO Basement Backup
11983 | 40251 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-19 12:55 | 2013-09-19 14:33 | 2013-09-20 08:23 | 0 |  | Basement at 2025 S William St | Rain 3 inches Heavy rain over 3 inches | Forward to engineering for review of possible sewer line line capacity issue | SSO Basement Backup
11983 | 40253 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-19 13:16 | 2013-09-19 14:48 | 2013-09-20 08:23 | 0 |  | Basement at 1721 Vernon St | Heavy rain on 9-19-13 over 3 inches. | Forwarded to engineering for review of possible sewer line capacity issue. | SSO Basement Backup
11983 | 40254 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-19 15:18 | 2013-09-19 14:53 | 2013-09-20 08:23 | 0 |  | Basement | Heavy rain on 9-19-2013 over 3 inches. | Forwarded to engineering for review of possible sewer line capacity issue. | SSO Basement Backup
11983 | 40277 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-20 09:15 | 2013-09-20 10:41 | 2013-09-21 08:12 | 0 |  | Basement at 1608 Leer ST | Rain 5 inches Heavy rain on 9-19-13 over 5 inches. | Turned over to engineering for review of possible sewer line cap issue. | SSO Basement Backup
11983 | 40303 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-23 10:00 | 2013-09-23 10:55 | 2013-09-23 15:45 | 0 |  | CSO 048 (river crossing #1) | Kensington stormwater basin were all full due to last weeks 4 rain event. Basin were being drain to provide for available storage capacity for next storm event. Weir gate was lowered too far down and excess water went out the overflow. Once discovered by SCADA alarm the gate was raise to reduce the amount of discharge. | See Report | SSO Reached Receiving Water | Saint Joseph River
11983 | 40344 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-09-23 15:36 | 2013-09-23 17:05 | 2013-09-24 14:19 | 0 |  | 441 E LaSalle Ave main line cave in. | Business had slow drainage No damage to basement No Photos taken | Removed Blockage See Report | SSO Basement Backup
11983 | 41066 | IN0024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-10-08 18:45 | 2013-10-08 19:35 | 2013-10-09 09:20 | 0 |  | 1020 Evergreen Lane Manhole in street | Unknown This is a residential area with no restaurants or business- we will CCTV to find the private lateral discharging the grease | Removed Blockage See Report | SSO Reached Public Land
50989 | 35124 | IN0024660 | ELDEN KUEHL POLLUTION CONTROL FACILITY | St Joseph | 2013-01-25 12:30 | 2013-01-25 13:45 | 2013-01-28 09:48 | 10 | gallons | 703 Monroe Street Valparaiso IN. first floor bath toilet and tub. | Sanitary sewer backup into residence | Removed blickage found in city sewer. Sewer Dept. will televise this city sanitary sewer main in the morning 1/28/13 to check for any further problems. | SSO Basement Backup; SSO Affected Private Property
30955 | 35563 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-01-09 10:00 | 2013-01-09 11:00 | 2013-01-09 14:25 | 500 | gallons | CSO 002 | Equipment malfunction caused an untreated release from CSO 002 to an unnamed receiving water. Lift station pumps became airlocked. Telemetry indicated a high wet well level with two pumps running. This lift station is directly downstream of CSO 002. If wet well level rises to CSO dam crest a CSO will occur. | Mechanic vented air from pumps restoring them to proper functionality. The area tributary to CSO is being separated. To be completed by 6/2013. Lift station is being completely refurbished this year. | SSO Reached Receiving Water
30955 | 34927 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-02-09 | 2013-02-10 | 2013-02-13 14:35 | 0 |  | Basement backups occurred at 1312 Benton and 1315 Benton in Mishawaka IN | Basement backups caused by debris build up as a result of lateral lining contractor working for city. | City sewer maintenance crew jetted and vacuumed line to remove obstruction. Flow returned to normal. | SSO Basement Backup
30955 | 34837 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-02-19 09:55 | 2013-02-19 16:10 | 2013-02-20 11:20 | 0 |  | CSO 004 at the headworks of rivercrossing #3 in Mishawaka IN | CSO 004 is located at the headworks of river crossing #3 which has two 8 inverted siphons. It appears that one barrel became obstructed causing a partial overflow in CSO 004 | CSO was vactored out to check for dbris and the rivercrossing was jetted. After jetting flow returned to normal and the D.W.O ceased | SSO Reached Receiving Water | Saint Joseph River
30955 | 35400 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-04-11 |  | 2013-04-12 13:31 | 0 |  | 803 West 8th Street Mishawaka IN | Precipitation event triggered an basement backup. No estimation of untreated backup. | Area of back-up is slated for sewer separation as an element of CSO LTCP. | SSO Basement Backup
30955 | 36753 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-05-02 14:00 | 2013-05-02 15:00 | 2013-05-03 12:30 | 50 | gallons | manhole | Grease clogging sewer main caused a surcharge and untreated release from a manhole to storm sewer. | Sewer maintenance cleaned manhole and surcharge was alleviated.Further sewer line cleaning monitoring on a regular basis and discussions with an upstream restaurant by the city F.O.G. inspector. | SSO Reached Public Land; Storm Sewer
30955 | 37958 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-06-13 |  | 2013-06-17 14:47 | 0 |  | 715 W Third St Basement Backup | Rain Heavy rain resident has a backflow valve but it did not function. |  | SSO Affected Private Property
30955 | 38026 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-06-20 | 2013-06-21 | 2013-06-26 09:00 | 0 |  | 813 Seventh St. Basement Backup | Rain Unknown properly owner had been gone for past 2 weeks and just noticed that it had backed up while she was gone. Basement contaminated area seemed to have been 240 sq ft. | Sewer department televised the lateral 6/25.13 and round no breakage or obstruction in the line. Discussed installing backflow preventer. | SSO Basement Backup
30955 | 40276 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-09-19 10:31 | 2013-09-19 10:31 | 2013-09-20 15:13 | 0 |  | 803 W 8th 1620 Meridian St. | Basement Backup | Precipitation Related basement backups at: 803 W 8th - minimal volume 3-5 gallons 1620 Meridian 12 inch radius of backup | SSO Basement Backup
30955 | 40248 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-09-20 13:00 | 2013-09-20 13:15 | 2013-09-20 09:45 | 0 |  | Manhole at intersection of Prospect and Indiana | Rain 3.44 inches The manhole on a combined sewer surcharged during heavy rainfall. | See Report | SSO Reached Public Land
30955 | 40247 | IN0025640 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-09-20 13:00 | 2013-09-20 14:00 | 2013-09-20 09:45 | 0 |  | Manhole 19 in Crawford Park | Rain 3.44 inches A manhole on combined sewer surcharged in Crawford park. The event was caused by heavy rainfall totaling 3.44 inches. | See Report | SSO Reached Public Land
30955 | 41076 | IN0025640 Outfall 001 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-10-05 09:28 |  | 2013-10-09 14:00 | 0 |  | 115 George St | Rain .75 inches Resident was not home on the weekend. They discovered back-up on 10-7 and notified sewer maintenance department. | See Report | SSO Basement Backup
30955 | 41628 | IN0025640 Outfall 001 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-11-05 20:00 | 2013-11-05 22:30 | 2013-11-05 10:47 | 0 |  | Juday Creek Lift Station Pump Station Failure | Equipment Failure See Attached Sheet | Repaired Pump Station See Report | SSO Affected Private Property
30955 | 42297 | IN0025640 Outfall 001 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-12-03 10:30 | 2013-12-03 10:31 | 2013-12-04 09:25 | 0 |  | CSO 002 - Upstream of Middleboro Lift Station | See Attachment | See Attachment | SSO Reached Receiving Water | Saint Joseph River
30955 | 45008 | IN0025640 Outfall 002 | MISHAWAKA MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-12-25 | 2014-01-02 09:30 | 2014-01-02 15:21 | 110000 | gallons | CSO 002 | A piece of broken concrete became wedged in 12x12 opening between CSO 002 structure and lift station wet well. This collected enough debris to restrict flow into lift station and caused an overflow at CSO 002. | Removed Blockage | SSO Reached Receiving Water | Saint Joseph River
42709 | 39177 | IN0032476 | Anderson Municipal Sewage Treatment Plant | St Joseph | 2013-06-27 19:17 |  | 2013-06-28 15:59 | 0 |  | primary Clarifiers | Rain .51 inches rain event | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | White River
58549 | 35549 | IN0039837 | CARLISLE MUNICIPAL WASTE WATER TREATMENT PLANT | St Joseph | 2013-04-04 03:00 | 2013-04-05 08:50 | 2013-04-05 12:04 | 40000 | gallons | Dead End on North Wintergreen Rd Wintergreen Lift Station Released directly into ditch leading to Nespodziany Ditch | Untreated Release Power Failure Power failure at lift station. call box did not call out to report power failure. | Spread Lime around manhole Reprogrammed callout box and tested. | SSO Reached Receiving Water
105662 | 38895 | IN0063258 | Saint Joseph County Regional Water & Sewer District Waste Water Treatment Plant | St Joseph | 2013-06-25 03:00 | 2013-06-25 13:00 | 2013-06-26 12:56 | 0 |  | Corner of Beckley St and Bittersweet Tr Granger In | The St Joseph County Regional Sewer District satellite collection system contracts with the City of Edwardsburg for bulk sewage treatment. The collection system is operated by contract operations firm Astbury Water Technology Inc. Power failure at lift station caused water to back-up in lift station causing an overflow to the grassy area around station. aseptic pumper was contacted and lift station pumped down. Pumping continued until power was restored at approx 9:55pm. Power failure due to storm damage of power lines. | Power Failure Pump Station Failure | SSO Affected Private Property
105662 | 39434 | IN0063258 (Granger Sub District) | Saint Joseph County Regional Water & Sewer District Waste Water Treatment Plant | St Joseph | 2013-07-18 16:00 | 2013-07-18 16:45 | 2013-08-19 11:19 | 0 |  | Corner of Beckley St. & Bittersweet Trail Granger In | The St Joseph Co Regional Water & Sewer Dist. Granger In satellite collection system contracts with the City of Edwardsburg Michigan for bulk sewage treatment. Said collection system is operated by Ashbury Water Tech. Apower failure at the lift station a small overflow to the grassy area surrounding the lift station; the spill did not leave the premises. A septic hauler responded to pump-down the lift station an clean the spill while power was restored and the unit resumed operation. | See Report | SSO Affected Private Property
11983 | 39455 | IN024520 | South Bend Waste Water Treatment Plant | St Joseph | 2013-07-22 04:00 | 2013-07-22 07:00 | 2013-07-22 14:33 | 0 |  | Basement at 825 Liberty St | Rain 2. inches heavy rain | See Report | SSO Basement Backup; SSO Affected Private Property
31370 | 34933 | No NPDES Permit | NEW CARLISLE WASTE WATER TREATMENT PLANT | St Joseph | 2013-02-11 22:00 | 2013-02-12 08:00 | 2013-02-12 11:33 | 25000 | gallons | 341 E. Michigan St. New Carlisle IN 46552. Junction box where all town sewer mains meet to go into main sewer. | Untreated Release caused by a 1 x2 piece of plastic blowing into the main junction box and blocking the sewer main outlet | As soon as the problem was cleared lime was spread over the affected areas. Piece of plastic used for snowfall measurement was secured. | SSO Reached Public Land; SSO Reached Receiving Water; Storm Sewer | Niespodziany Ditch
59695 | 38622 | IN0020877 | NORTH JUDSON MUNICIPAL WASTE WATER TREATMENT PLANT | Starke | 2013-06-12 07:45 | 2013-06-12 10:05 | 2013-06-13 15:30 | 131326 | gallons | CSO #4 Unnamed ditch to Pine Creek | Rain 1.30 inches Untreated Release. @ days of rain then 1.30 inches i 4 hr caused bypass at the treatment plant. | All equipment running at max speed (Plant - CSO Basin) . Franklin St. and various other sections of town combined storm sewer working on plans to remove. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Pine Creek
59695 | 39768 | IN0020877 | NORTH JUDSON MUNICIPAL WASTE WATER TREATMENT PLANT | Starke | 2013-08-13 06:45 | 2013-08-12 07:30 | 2013-08-13 22:38 | 0 |  | CSO #004 Unnamed Ditch to Pine Creek | According to computer rain gauge rain event lasted 16 minutes which would equal 3.4 inches in one hour. | All plant equipment operating at full speed. Town is looking into rermoving combination wastewater and storm | SSO Reached Receiving Water | Pine Creek
59695 | 40239 | IN0020877 | NORTH JUDSON MUNICIPAL WASTE WATER TREATMENT PLANT | Starke | 2013-09-18 09:55 | 2013-09-18 10:45 | 2013-09-19 16:12 | 0 |  | CSO 004 | Rain 1 inch raingage recorded 1.2 inches in 1 hour 40 min with highest intensity .70 in 15 minutes. | All equipment operating at full speed. Town is looking into removing more combination wastewater/storm lines. | SSO Reached Receiving Water | Pine Creek
59695 | 40246 | IN0020877 | NORTH JUDSON MUNICIPAL WASTE WATER TREATMENT PLANT | Starke | 2013-09-20 01:30 | 2013-09-20 02:30 | 2013-09-20 08:39 | 0 |  | CSO 004 | Computer raingauge recorded 1.5 rain in 15 minutes. | All equipment operating at full speed. Town is looking to remove more combined storm sewer lines. | SSO Reached Receiving Water | Pine Creek
| 34604 |  | Angela Gardens Rentals | Steuben | 2013-03-06 01:00 | 2013-03-06 07:00 | 2013-03-07 13:04 | 0 |  | Manhole Ground | Untreated Equipment Failure Blockage in sewer lines prior to the lift station. | Shorty s Sewer service on sight to determine the reason for the blockage and eliminate the blockage. | SSO Affected Private Property
60094 | 35569 | IN0021296 | ANGOLA WATER WORKS | Steuben | 2013-01-07 13:00 | 2013-01-07 14:15 | 2013-01-08 15:48 | 500 | gallons | Manhole at intersection of Park and Kinney Streets | Grease blockage in the sewer segment used by the University Center. Result was an untreated release into the street and storm drain. | Manhole lid stayed in place during discharge. No solids were discharged. Crews jetted the sanitary sewer and the 12 main. Grease deposits were removed. Cleaned manholes and affected line. Contacted the University Director of Maintenance and discussed the situation with him. The city will be working with the University to resolve this issue. | SSO Reached Public Land; Storm Sewer
60094 | 37094 | IN0021296 | ANGOLA WATER WORKS | Steuben | 2013-05-22 15:00 | 2013-05-23 08:30 | 2013-05-24 07:00 | 0 |  | 402 E Stocker St Basement Backup | Property owner called WWTP after business house & left a message about water in his basement. Collection system was sent to the site to investigate after message was received on the morning of 5/23. The crew found that the sewer was blocked somewhere downstream of the complainants home. The sewer was jetted & the blockage was cleared. No obvious reasons for the blockage was discovered. | Once notification was made to the wastewater department crews immediately mobilized to the site clear the blockage. The Angola WWTP contracts CCTV inspection annually to identify problems in the sewer system and operates the sewer system to minimize sewer backups and overflows. | SSO Basement Backup
60094 | 37233 | IN0021296 | ANGOLA WATER WORKS | Steuben | 2013-05-25 02:00 | 2013-05-25 02:57 | 2013-05-28 11:18 | 200 | gallons | 101 Woodhull Dr Woodhull Lift Station Air Release Valve Ground. | Police Dispatch notified the On-call operator of water coming out to a manhole structure at the above address. The on-call operator immediately went to the location and verified that the spill was from an air release valve structure for the Woodhull Lift Station force main. The Lift Station was immediately shut down the valve structure was cleaned and personnel found that the aluminum quick release fitting on the bottom of the A/R valve had failed due to corrosion. The fitting was replaced with a stainless steel fitting and the lift station was returned to service. All liquid and debris was vacuumed from the site and on 5/26 hydrated lime was applied to the ground around the structure. | Once notification was made to the wastewater department crews immediately mobilized to the site to confirm the release was from the wastewater system stopped the release fixed the failed valve and cleaned the area where the wastewater pooled. A/R valve structures are inspected on a regular basis by wastewater staff. A/R valves and appurtenances are inspected are cleaned and maintained as necessary. | SSO Affected Private Property
60094 | 39862 | IN0021296 | ANGOLA WATER WORKS | Steuben | 2013-08-28 10:00 | 2013-08-28 10:18 | 2013-08-29 04:49 | 0 |  | Manhole @ intersection of Park & Kinney Sts. | At 10:00 Trino Operations Director Rod Olson contacted wastewater treatment staff that wastewater was discharging from a sanitary sewer manhole at the described intersection. Wastewater personnel responded to the location and identified the backup occurring in the sewer segment that the University Center discharges into. They immediately called for our vacuum truck to suck up wastewater from the overflowing manhole and called the Vactor crew to jet the sewer main (The Vactor was in another community assisting with sewer cleaning for CCTV work). The vacuum truck arrived within 15 minutes of notification and immediately stopped the overflow from the manhole. the Vactor arrived onsite within 40 minutes and jetted the sanitary sewer. Significant grease deposits were found blocking the sanitary sewer and crews cleaned the affected line and manholes to ensure proper operation. | Wastewater crews immediately mobilized to the scene and had restored sewer service within 60 minutes of being notified of the overflow. The Wastewater Superintendent contacted the University Director of Maintenance & discussed the situation with him. As noted in the January report the grease trap is being cleaned on a regular basis and all indications show that grease accumulation in the trap is minimal. Further discussions indicate that although he food preparation room drains through the grease trap the dish room does not and the University s plumbing contractor has (incorrectly) argued that the plumbing code prohibits dishwater discharge into the grease trap. The City will be working with the University to resolve this issue. Until it is demonstrated that the University has implemented and effective plan to reduce the discharge of grease into the sanitary sewer WW staff has been directly to jet the effected sewer segments regularly. | SSO Affected Private Property; SSO Reached Receiving Water | Center Lake
60094 | 40659 | IN0021296 | ANGOLA WATER WORKS | Steuben | 2013-10-01 04:00 | 2013-10-11 05:15 | 2013-10-02 07:36 | 0 |  | 1440 W 200 Force Main AR Valve Ground | Resident notified the on-call operator of water coming out of a manhole structure at the above address. The on -call operator immediately went to the location and verified that the spill was from an air release valve structure for the CR 200 N force main. The valve structure was cleaned and personnel found that the alumin | See Report | SSO Affected Private Property
59487 | 41393 | IN0022942 | FREMONT WASTE WATER TREATMENT PLANT | Steuben | 2013-10-26 03:00 | 2013-10-26 03:22 | 2013-10-28 12:00 | 0 |  | LS #4 SR 120 W of SR 127 | Power Failure Equipment Failure #1 pump (north) had thrown overload #2 pump (south) had thrown breaker. When arrived on scene 1 wire around overload on #1 #2 was unable to reset breaker. Pumped station down and shortened the distance between on and off float. Received instruction from Town Mgr to repair. Crew on scene 12:00 noon pulled #1 pump removed debriscleaned breaker #2 pump reset. Both pumps and station operational as normal 2:30pm. | Removed Blockage Repaired Pump Station | SSO Reached Public Land
59487 | 41604 | IN0022942 | FREMONT WASTE WATER TREATMENT PLANT | Steuben | 2013-11-04 | 2013-11-04 07:47 | 2013-11-04 13:27 | 0 |  | LS #1SR !@) W of CR 100E | Equipment Failure Observed LS #1 on alarm at 7:40am responded at 7:55 after gathering safety equip & maintenance truck. Found #1 pump breaker off and #2 pump overload tripped. Reset and station began operating correctly however #2 pump began working contractor a erratically. Shut #2 pump off and reset. Pump began working correctly. Sucked up standing sewage on ground. | Reparied Pump Station | SSO Affected Private Property
59487 | 41606 | IN0022942 | FREMONT WASTE WATER TREATMENT PLANT | Steuben | 2013-11-04 | 2013-11-04 14:13 | 2013-11-04 13:27 | 0 |  | LS #3 SR 120 W of CR 50 | Received call on phone from Steuben County Communication that LS was on alarm. Maintenance person arrived and found a float had hung up. LS pumps worked on hand upon arrival float was unstuck and LS went back into normal operation. | Repaired pump station See Report | SSO Affected Private Property
59608 | 36481 | IN0050822 | HAMILTON LAKE TREATMENT PLANT | Steuben | 2013-04-19 14:30 | 2013-04-19 15:30 | 2013-04-19 18:48 | 200 | gallons | Force Main North of Ln 201 along E Bellfountain RD Ground | Untreated Release Construction Related Boring crew creased zinch sewer main. Main was located prior to boring. | Pipe was repaired | SSO Affected Private Property
59608 | 36511 | IN0050822 | HAMILTON LAKE TREATMENT PLANT | Steuben | 2013-04-19 14:30 | 2013-04-19 15:30 | 2013-04-19 18:38 | 200 | gallons | Force main north of LN201 along East Bellfountaine Road | Boring crew creased 2 inch sewer main resulting in untreated release to surrounding ground and swamp. Main was located prior to boring. | Pipe was repaired. | SSO Reached Public Land
59608 | 41900 | IN0050822 Outfall 001 | HAMILTON LAKE TREATMENT PLANT | Steuben | 2013-11-15 09:08 | 2013-11-15 12:15 | 2013-11-15 14:48 | 0 |  | 1540 Ln 201 Ball Lake Manhole | Air release valve vent stuck open. Leak was reported at 11:35am. Homeowner was not sure what time the release began. It was noticed when the person went out to get their mail. | See report | SSO Affected Private Property
60581 | 34707 | IN0061557 | STEUBEN LAKES REGIONAL SEWAGE DISTRICT | Steuben | 2013-02-27 11:00 | 2013-02-27 11:30 | 2013-02-27 16:00 | 100 | gallons | 650 B Snow Lake Fremont IN 46737 | A faulty tap broke off of main | Repaired faulty tap and added a stainless steel saddle. | SSO Reached Public Land
60581 | 35280 | IN0061557 | STEUBEN LAKES REGIONAL SEWAGE DISTRICT | Steuben | 2013-03-30 | 2013-03-30 12:00 | 2013-03-31 08:30 | 15 | gallons | 220 Lane 650 BB Snow Lk- home owners 300 Lane 440 Lk James-Home owners Ground | Untreated Release Power Failure 220 Lane 650 BB Snow lake Residents breaker tripped. 300 Lane 440 Lake James resident has power from home off. | Try to educate people to leave there power on even if not present. Same as above there is probably some 3 to 4 thousand home owners grinder tanks and they are all responsible for supplying power to there tanks. | SSO Affected Private Property
60581 | 35284 | IN0061557 | STEUBEN LAKES REGIONAL SEWAGE DISTRICT | Steuben | 2013-04-01 08:30 | 2013-04-01 09:10 | 2013-04-01 12:41 | 5 | gallons | 3170 W Sycamore Beach Rd Angola In Grinder Station home owners Ground | Untreated Release Equipment Failure Broken transition fitting allowing sewage to seep when pump turns on. | Replace plastic fitting with stainless steel nipple and brass check valve. | SSO Affected Private Property
60581 | 39516 | IN0061557 | STEUBEN LAKES REGIONAL SEWAGE DISTRICT | Steuben | 2013-07-14 | 2013-07-14 13:30 | 2013-07-05 08:20 | 0 |  | 235 In 101 Jimmerson Lake Lateral Line | Construction Related Contractor hit lateral line when installing fiber optic line by directional drilling. | Repaired Pipe | SSO Affected Private Property
60581 | 39803 | IN0061557 | STEUBEN LAKES REGIONAL SEWAGE DISTRICT | Steuben | 2013-08-23 09:30 | 2013-08-23 09:45 | 2013-08-23 10:37 | 0 |  | 5110 N 450 W Lateral Line Lift St | Equipment Failure Line broken on outside of Lift Station. Leaking sewage when pumps kicked on. | Repaired Pipe See Report | SSO Affected Private Property
60581 | 39932 | IN0061557 | STEUBEN LAKES REGIONAL SEWAGE DISTRICT | Steuben | 2013-08-31 08:52 | 2013-08-31 13:33 | 2013-08-31 12:19 | 0 |  | 5110 N 450 W Manhole area | Breaker tripped. | Re-set breaker and cleaned up. Plans to redesign this duplex lift station. Collection system still waiting on parts ordered. | SSO Affected Private Property
60581 | 42439 | IN0061557 | STEUBEN LAKES REGIONAL SEWAGE DISTRICT | Steuben | 2013-12-13 08:05 | 2013-12-13 08:20 | 2013-12-13 09:50 | 0 |  | Duplex Station 3861 N Bay View | Equipment Failure Grease built up on floats and alarm switch failed. | See Report | SSO Affected Private Property
59584 | 38210 | IN0020389 | SHELBURN MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-07-01 18:00 | 2013-07-01 16:30 | 2013-07-01 18:35 | 0 |  | Manhole at Jefferson and Poplar Lift Station on Thomas | Exceeded Max Capacity Rain 4.5 inches. One of the pumps in the Thomas sit lift station overheated and tripped out-could not keep up with rain and inflow- backed up to a manhole that overflowed as well. | Reset overheated pump - pump started working and I watched the overflow stop. Reset pumps. | SSO Reached Public Land; SSO Affected Private Property
59584 | 42018 | IN0020389 | SHELBURN MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-11-16 10:00 | 2013-11-17 11:00 | 2013-11-18 10:00 | 0 |  | Lift Station #1 | Rain 1.5 inches Equipment Failure When we got to lift station both pumps tripped out-reset pumps and they both started pumping. No explanation other than power surge. | Repaired Pump Station See Report
58959 | 36300 | IN0021148 | KERNS SERVICE STATION | Sullivan | 2013-04-22 | 2013-04-22 08:00 | 2013-04-24 15:41 | 0 |  | WWTP | Precipitation event(s) triggered overflows at WWTP resulting in untreated release and treatment bypass to surrounding ground. High flow due to rain caused Contact Tank EQ tank Clarifiers and Digesters to overflow. | Cleaned up affected area. | SSO Occurred at Treatment Plant
58958 | 36157 | IN0021148 | FARMERSBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-04-24 08:00 |  | 2013-04-24 10:04 | 0 |  | Contact tank clarifiers EQ Tank Ground | Rain 2.1 inches High Flow due to rain. Plant drain station over flowing contact tank is over flowing and clarifiers are over flowing. |  | SSO Affected Private Property
58958 | 36661 | IN0021148 | FARMERSBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-04-25 | 2013-04-25 13:45 | 2013-04-26 07:38 | 0 |  | WWTP Effluent Tank and Clarifiers | Precipitation event flow caused treatment bypass due to contact tank and clarifier tank overflow to surrounding ground. | Cleaned up affected area. | SSO Occurred at Treatment Plant
58958 | 37644 | IN0021148 | FARMERSBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-05-31 |  | 2013-06-01 12:00 | 100000 | gallons | Farmersburg WWTP | Precipitation events filled EQ and overloaded plant hydraulically. | Turned off blowers and RAS pumps to preserve solids.Will clean up floaties when overflow stops.Identify inflow areas in town and fix them. | SSO Occurred at Treatment Plant
58958 | 38054 | IN0021148 | FARMERSBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-06-26 08:00 |  | 2013-06-26 18:35 | 0 |  | EQ tank effluent tank clarifiers | Exceeded Max Capacity Rain 3.5 inches. Excess inflow has filed EQ to overflow both clarifiers effluent tank and most likely the aeration and digesters by tomorrow. The water moved down hill towards the receiving stream. | I turned off the blowers and RAS pumped to preserve solids for operation when flow slows down. The Town of Farmersburg is currently putting together a compliance plan where we will find sources of inflow and try to eliminate them- nothing further we can do at facility. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water
58958 | 38207 | IN0021148 | FARMERSBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-06-30 |  | 2013-07-01 09:10 | 0 |  | Clarifier EQ Effluent Tank | Exceeded Max Capacity Rain 4.5 inches Treatment Bypassed | Plant hydraulically overloaded-clarifier EQ effluent contact tank overflowed onto ground. | SSO Occurred at Treatment Plant
58958 | 41557 | IN0021148 Outfall 001 | FARMERSBURG MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-10-31 10:11 | 2013-11-01 17:00 | 2013-11-01 19:18 | 0 |  | 1040 N Section St | Rain 2.5 inches Exceeded Max Capacity Inflow and infiltration in collection system added too much flow to plant and overflowed the clarifiers and effluent tank. | See Report | SSO Occurred at Treatment Plant; SSO Reached Receiving Water
58759 | 43097 | IN0024554 Outfall 001 | SULLIVAN MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-11-11 | 2013-11-11 | 2013-12-24 11:35 | 250 | gallons | CSO #002003 | Equipment Failure Influent pumps had rags around impellrs-had to reset one pump and reverse the other. Thursday pumps were going and overflow stopped by Sat night-extra rain Friday and Saturday. DNR notified first IDEM then notified. | Repaired Pump Station | SSO Affected Private Property
58759 | 43629 | IN0024554 Outfall 001 | SULLIVAN MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-12-21 16:00 | 2013-12-23 21:00 | 2013-12-24 11:37 | 250000 | gallons | CSO #002 003 | Equipment Failure Influent pumps had rags around impellers-had to reset one pump and reverse the other- Thursday pumps were going and overflow stopped by sat night-extra rain Friday and Saturday. DNR & IDEM then notified. | See Report | SSO Affected Private Property
58759 | 37825 | IN0024554 - Washed to combined system drain downstream. | SULLIVAN MUNICIPAL WASTE WATER TREATMENT PLANT | Sullivan | 2013-02-05 | 2013-02-05 | 2013-06-11 09:10 | 5000 | gallons | Manhole at Johnson and Crowder | Rain 1.3 inches Line from Baesiers clogged with grease and debris. Overflowed at manhole and flowed down street. Street superintendent notified Chris Olsen in morning. IDEM was on site-tried to open line but old vac-truck failed- were able to repair truck and get line open by end of day. | City opened a hydrant to flush debris and wastewater down to next storm drain where it was conveyed to the wastewater plant. Sullivan is a combined system so no wastewater made it to any receiving stream or caused any damage to the environment. We are currently updating our collection system maintenance schedule as well as our CSOOP. The City has since spent 350K on a new vac truck to keep such a schedule and not bread down during operation. We have also received grease pumping manifests from Baesler s market to prove they are having their grease traps pumped. | SSO Affected Private Property
58559 | 34970 | IN0039322 | DUGGER MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-03-18 02:00 | 2013-03-18 06:00 | 2013-03-18 11:25 | 100 | gallons | Dugger WWTP S Aeration Tank Ground | Partially Treated Release Equipment Failure Clog in line to N Aeration tank caused all flow to go to South tank and overflow. | Will unclog line. | SSO Affected Private Property
58556 | 34924 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-03-18 14:00 | 2013-03-18 17:30 | 2013-03-19 12:26 | 11000 | gallons | Lift station #2 ditch | Untreated Equipment Failure Rain .25 inches Lift pump #2 O/S | Picked up observable debris Called electrician to troubleshoot pump/ electrical | SSO Affected Private Property
58556 | 37066 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-05-20 02:00 | 2013-05-21 05:00 | 2013-05-22 15:06 | 50000 | gallons | #1 & #2 Lift Station Town drainage ditch | Untreated Release Power Failure Power still not on as of 1600hrs. Plant operating off of generator only 1 rotor operating. Both digester blowers down clarifier drives both operating. | Debris picked up. | SSO Affected Private Property
58556 | 37513 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-05-31 04:00 | 2013-05-31 12:00 | 2013-05-31 14:14 | 12000 | gallons | #2 Lift Station Wet Well | Precipitation event along with a pump being out of service for repair resulted in an untreated release from Lift Station wet well to an unnamed ditch. | #1 pump pulled for repair. #2 pump running at capacity. Town is making plans to seal manhole covers to minimize stormwater infiltration. | SSO Reached Public Land
58556 | 37621 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-06-02 | 2013-06-03 | 2013-06-03 14:32 | 20000 | gallons | Lift Station #2 | Precipitation event coupled with inflow exceeded capacity of Lift Station resulting in untreated release to an unnamed ditch. Problem submitted by homeowner. | Will pick up debris spread lime on affected area when overflow stops.
58556 | 37791 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-06-11 17:30 | 2013-06-11 17:50 | 2013-06-12 14:42 | 1000 | gallons | Lift Station #2 Ground | Untreated Release Lift Station has one pump out for repair. The pump in Lift Station was tripped out. | Reset pump should have 2nd pump back from repair in 2 to 3 business days. | SSO Affected Private Property
58556 | 37789 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-06-11 17:30 | 2013-06-11 17:50 | 2013-06-12 14:16 | 1000 | gallons | Lift Station #2 Ground | Equipment Failure Lift Station has one pump out for repair. The pump in Lift station was tripped out. | Reset pump should have 2nd pump back from repair in 2 to 3 business days. | SSO Affected Private Property
58556 | 37792 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-06-11 17:30 | 2013-06-11 17:50 | 2013-06-12 14:39 | 1000 | gallons | Lift Station #2 Ground | Equipment Failure Lift Station has one pump out for repair. The pump in Lift Station was tripped out. | Reset pump should have 2nd pump back from repair in 2 to 3 business days. | SSO Affected Private Property
58556 | 37790 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-06-11 17:30 | 2013-06-11 17:50 | 2013-06-12 15:03 | 1000 | gallons | Lift station #2 Ground | Equipment Failure Lift Station has one pump out for repair. The pump in Lift Station was Tripped out. | Reset pump. Should have 2nd pump back from repair in 2 to 3 business days. | SSO Affected Private Property
58556 | 37695 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-06-13 08:10 | 2013-06-13 08:45 | 2013-06-04 06:57 | 800 | gallons | Lift Station #2 Ground | Untreated Release Equipment Failure. One pump is in shop being repaired and will be back on 6-14-13 the remaining pump over heated and tripped out. | Reset pump pump will be back on 6-14-13 and installed. | SSO Affected Private Property
58556 | 39841 | IN0040134 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-08-23 10:38 | 2013-08-24 13:00 | 2013-08-24 19:09 | 0 |  | Lift Station #1 | Power Failure Power surge knocked out one phase of 3 phase power- received at call at 8:30am 8/24/13 that lift station overflowing- tried to reset could not-phase monitor in control panel said front phase unbalanced. Called electrician - he was able to reset phase monitor and replace fuse. Lift Station running and OK | Repaired Pump Station See Report | SSO Reached Public Land
58556 | 42625 | IN0040134 Outfall 001 | HYMERA MUNICIPAL SEWAGE TREATMENT PLANT | Sullivan | 2013-12-20 | 2013-12-22 | 2013-12-22 13:49 | 0 |  | Lift Station #1 and #2 | Exceeded Max Capacity Rain 4 inches. Too much inflow -hydraulically overloaded pumps operational but couldn t keep up. | See Report | SSO Affected Private Property
18969 | 35167 | IN0020231 | Vevay Municipal Waste Water Treatment Plant | Switzerland | 2013-01-30 11:00 | 2013-01-30 13:00 | 2013-01-30 14:48 | 0 |  | Vevay Municipal Wastewater Treatment Plant Vevay IN | Plugged effluent line at plant. Caused partially treated release | cleared obstruction in effluent line with jetter. Perform daily inspections of effluent line. | SSO Occurred at Treatment Plant
18969 | 43632 | IN0020231 | Vevay Municipal Waste Water Treatment Plant | Switzerland | 2013-12-24 12:30 | 2013-12-24 12:35 | 2013-12-24 13:38 | 0 |  | Lift Station Washington St | Equipment Failure pump was plugged with some type of sanitary or baby wipe. | See Report | SSO Affected Private Property
11821 | 36548 | IN0002861 | Evonik Corporation | Tippecanoe | 2013-04-19 13:50 |  | 2013-04-19 16:37 | 0 |  | Storm Water Retention Pond. Evonik Degussa Corp. Tippecanoe Labs | Precipitation event caused flooding and the infiltration from the Wabash River to a storm water only retention pond. This pond is used as a retention area and lift station for storm water only. | Once the Wabash River has receded from the storm water retention pond and the bypass condition has ceased a follow up fax will be sent. | SSO Affected Private Property; SSO Reached Receiving Water | Wabash River
11821 | 36041 | IN0002861 | Evonik Corporation | Tippecanoe | 2013-04-19 13:50 | 2013-04-22 18:00 | 2013-04-23 11:52 | 0 |  | Wabash River Storm Water Retention Pond | Untreated Release Rain The Wabash River is above flood stage and overflowed into a storm water retention pond. The pond is used as a retention area and lift station for storm water only. The level of the Wabash River has receded from the storm water retention pond and the by-pass condition has ceased to exist from the incident faxed on 4/19/2013 |  | SSO Affected Private Property | Wabash River
10847 | 34957 | IN0020036 | Battle Ground Municipal Waste Water Treatment Plant | Tippecanoe | 2013-02-07 09:00 | 2013-02-07 09:30 | 2013-02-07 18:36 | 3000 | gallons | River Bluffs Lift Station | Deteriorated galvanized bubbler piping resulted in overflow at the River bluffs Lift Station | Lift station pumps turned on manually stopping overflow. Deteriorated galvanized piping replaced with PVC. | SSO Occurred at Treatment Plant
10847 | 36482 | IN0020036 | Battle Ground Municipal Waste Water Treatment Plant | Tippecanoe | 2013-04-18 17:00 | 2013-04-19 14:00 | 2013-04-19 14:45 | 0 |  | Woods Edge Lift StationHawks Nest Lift StationProphets Rock Heights Lift Station | Precipitation event(s) exceeded the capacity of lift stations resulting in untreated release to surrounding ground. | Areas will be cleaned up and limed. Facility is working to reduce infiltration and inflow. | SSO Reached Public Land
10847 | 36476 | IN0020036 | Battle Ground Municipal Waste Water Treatment Plant | Tippecanoe | 2013-04-18 18:00 | 2013-04-19 07:00 | 2013-04-19 14:45 | 0 |  | Town of Battleground WWTP | Precipitation event(s) flow exceed the influence structure at WWTP resulting treatment center bypass and untreated release to receiving waters. | Facility undergoing construction upgrade. Shut down aeration to save biological mass to shorten non compliance duration. Finish upgrade. Sandbag structure. | SSO Reached Receiving Water | Burnetts Creek
10847 | 36666 | IN0020036 | Battle Ground Municipal Waste Water Treatment Plant | Tippecanoe | 2013-04-18 18:00 | 2013-04-23 10:00 | 2013-04-26 12:42 | 900000 | gallons | WWTP | Precipitation event flow caused an untreated release from WWTP inflow structure to receiving water. | Analysis was performed on water around aeration basins and surface water in the north east area of plant. All standing water in north east area had drained down by the morning of 4/21/13.All inflow/stormwater waspumped andprocessed through the plant. Inflow structure was repaied and handled flow on 4/23/13 - 4/24/13. | SSO Reached Receiving Water | Burnett Creek
10847 | 37754 | IN0020036 | Battle Ground Municipal Waste Water Treatment Plant | Tippecanoe | 2013-06-04 18:40 | 2013-06-04 19:05 | 2013-06-05 17:30 | 2000 | gallons | Hawk Nest Lift Station Area around lift station | Power Failure Pump Station Failure Battle ground employee found that power box had been tampered with. He opened door and found that the main breaker was off. | Cleaned up area of any debris and limed. June 5th Battle Ground employees installed new locking system on breaker box with new lock. | SSO Affected Private Property
10847 | 41790 | IN0020036 Burnett Cr | Battle Ground Municipal Waste Water Treatment Plant | Tippecanoe | 2013-11-08 23:10 | 2013-11-08 23:30 | 2013-11-09 14:12 | 0 |  | River Bluffs LS Structure #4 Resident lateral on Greenview Dr Resident basement on Centerview Ct | Six inch main prior to River Bluff LS jetted to unplug line opened up over whelming structure #4 allowing 1500 gallon over flow also allowing resident broken lateral to release 600 gallon to enter ditch three miles away from wet lands- Prior to jetting plug caused back-up into resident basement (100 gallons) | Removed Blockage See Report
2653 | 36148 | IN0023990 | OTTERBEIN TOWN HALL | Tippecanoe | 2013-04-19 | 2013-04-19 | 2013-04-19 13:24 | 250 | gallons | 28 West 3rd Street | Precipitation event resulted in an untreated release from an abandoned property sewer line. | Old abandoned property. Assuming that service was not properly capped. Applying HTH to the affected lawn. Property owner or town will excavate service and check the problem and properly cap if therein lies the problem. | SSO Affected Private Property
11287 | 34721 | IN0024821 | WEST LAFAYETTE WASTE WATER TREATMENT PLANT | Tippecanoe | 2013-03-15 15:05 | 2013-03-15 15:50 | 2013-03-15 15:59 | 0 |  | Manhole at Walgreen at 1000 Sagamore Parkway West Lafayette | Untreated Release Overflow was the result of a blockage in the sewer line. | Vactor crew was dispatched to clean up the overflow and clear any blockages in the sewer main. More frequent inspection to look for blockages in this sewer main. | SSO Affected Private Property
11287 | 36149 | IN0024821 | WEST LAFAYETTE WASTE WATER TREATMENT PLANT | Tippecanoe | 2013-04-19 03:47 |  | 2013-04-19 08:44 | 0 |  | Manhole near 2920 Browing Street | Precipitation event(s) caused an untreated release from manhole to surrounding ground and storm drain. | Lift station is pumping and slowly catching up. | SSO Reached Public Land
11287 | 39832 | IN0024821 | West Lafayette Waste Water Treatment Plant | Tippecanoe | 2013-08-21 15:27 | 2013-08-21 16:30 | 2013-08-21 17:35 | 0 |  | 224 Cedar Hollow Ct. in easement | Unknown Blockage in sewer was reported by homeowner. | Removed Blockage See Report | SSO Affected Private Property
12227 | 34871 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-02-19 12:54 | 2013-02-19 13:50 | 2013-02-19 14:00 | 20 | gallons | City Sewer Manhole Lafayette IN | Water backing up for sanitary manhole in the street. Sewer line plugged with grease. | Crews responded immediately and unplugged sewer. Blockage follow up will be performed. | SSO Reached Public Land; Paved Surface
12227 | 34781 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-02-26 15:55 | 2013-02-26 16:30 | 2013-02-26 16:35 | 3 | gallons | Basement at 2203 Summerfield. | Water backing up in subscriber basement | Call came in that water was backing up in basement at 2203 Summerfield. City sewer line plugged. Crews reponded immediately and unplugged sewer. Blockage follow-up will be performed. | SSO Basement Backup
12227 | 34578 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-03-03 20:25 | 2013-03-03 21:57 | 2013-03-04 08:11 | 300 | gallons | City Sewer Basement @ 3604 Platte Court. | Rain .98 inches Call cam in that water was backing up in basement at 3604 Platte Court. The City sewer was plugged with grease. | Crews responded immediately and unplugged sewer. Blockage fellow-up will be performed today. | SSO Basement Backup
12227 | 36029 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-04-16 16:00 | 2013-04-13 18:00 | 2013-04-17 14:00 | 150000 | gallons | Wastewater Treatment Plant | Precipitation event and power surge loss of control of some plant operations and untreated release and treatment bypass at the WWTP. | Contacted Duke Energy and went to manual mode for plant operation. Investigating the cause of the power surge. | SSO Reached Receiving Water | Wabash River
12227 | 36178 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-04-18 15:44 | 2013-04-19 07:44 | 2013-04-19 09:30 | 4600 | gallons | 40 & 8 lift station wet well | Precipitation event(s) triggered an untreated release from lift station wet well to surrounding ground. | We maintain the lift station. It is checked weekly and routine maintenance is performed to keep the pumps running efficiently. We continue to perform maintenance and repairs on the collection system that feeds this station. | SSO Reached Public Land
12227 | 36718 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-04-18 16:14 | 2013-04-18 16:45 | 2013-04-19 11:44 | 0 |  | 1700 - 1900 Block of N 27th Street Catch Basins | Untreated Release Rain 2.5 inches Heavy rains the week of 4/8/13 - tenth approximately 5 of rain the week of 4/15/13. Area is checked in rain events and was discovered by personnel. Flows at the wastewater treatment plant are currently @ 45 MGD due to heavy rains. | Clean entire area. Consultant has been hired to design an infrastructure correction. | SSO Occurred at Treatment Plant
12227 | 36125 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-04-18 18:00 |  | 2013-04-19 11:45 | 500 | gallons | Manhole at South and Creasy Lane3927 South Orchard Court - Manhole in front yard3896 Baldwin Avenue - Basement Backup | Precipitation event caused an apparent sewer collapse resulting in untreated release to surrounding ground residential basement and another manhole. | Contractor hired to excavate sewer and make repairs. Tank trucks brought into haul waste to a separate sewer so that repairs can be made. Will investigate further after repairs are made. | SSO Basement Backup; SSO Reached Public Land; SSO Affected Private Property
12227 | 36352 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-04-18 18:00 | 2013-04-19 21:00 | 2013-04-22 10:40 | 0 |  | Manhole at South Street and Creasy Lane3927 South Orchard Court3896 Baldwin Avenue | Follow up to original incident #36125. Precipitation event(s) caused collapse of manhole and untreated release as a result. | Crews worked around the clock to repair collapsed manhole which serves the area. Repairs completed 4/20/13. Merrill Brothers worked around the clock to haul flow from the lift station to alleviate overflow. | SSO Basement Backup; SSO Reached Public Land; SSO Affected Private Property
12227 | 36123 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-04-18 18:00 | 2013-04-18 19:00 | 2013-04-19 11:43 | 5500 | gallons | 2509 Eckman Place - Basement Backup14 South 30th Street - Basement Backup1305 South 18th Street - Basement Backup617 South 26th Street - Basement Backup1015 South 30th Street - Basement Backup1212 Southlea Drive - Manhole at East Court30 West Court - Manhole at West Court | Precipitation event(s) resulted in untreated release from sewer system to manholes and residential basements. | Sewers full.We will perform follow-up inspections. Continue routine preventative maintenance schedules. | SSO Basement Backup; SSO Reached Public Land; SSO Affected Private Property
12227 | 36747 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-04-30 19:50 | 2013-04-30 20:53 | 2013-05-01 08:15 | 300 | gallons | 401 Park Avenue | Main sewer blockage resulted in untreated release into residential basement. | Jetted city sewer for 350 to clear blockage. Will perform blockage follow up on 5/1/13.5/3/13 Blockage Follow up. Rubber kick ball found lodged in sewer. Removed ball. Flow is normal now. | SSO Basement Backup
12227 | 36777 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-05-06 09:00 | 2013-05-06 16:30 | 2013-05-07 09:30 | 250 | gallons | 1329 Windmill Drive | Apparent private lateral blockage and root intrusion via a crack in the main sewer line resulted in an untreated release into a residential basement. | We jetted the City sewer 120 feet. Blockage follow up performed. Found crack in main sewer line with roots coming through it. We will repair the crack to prevent future occurrences. | SSO Basement Backup
12227 | 37067 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-05-22 11:50 | 2013-05-22 12:15 | 2013-05-22 15:36 | 25 | gallons | 1311 Windmill Drive Basement | Untreated Release. We received a call from 1311 Windmill Drive at 11:50 am with basement back-up. The technician determined that our City sewer was plugged. | We jetted and root cut the City sewer 125 to clear the blockage. We will perform a blockage follow-up on 5/23/2013 | SSO Basement Backup
12227 | 39975 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-09-03 10:15 | 2013-09-03 10:50 | 2013-09-03 13:21 | 0 |  | 1222 N 14th Street | Unknown Backup from city sewer into basement at 1222 N 14th Street. We received a call at 10:15 am the sewer crew went out and found the blocked sewer | Remove Blockage See Report | SSO Basement Backup
12227 | 40227 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-09-19 06:40 | 2013-09-19 07:00 | 2013-09-19 22:43 | 0 |  | 1015 S 30th (Basement) | Exceeded Max Capacity. System running full due to almost two inches of rainfall in less than 2 hours-backed up in basement. | See Report | SSO Basement Backup
12227 | 40258 | IN0032468 | LAFAYETTE WATER POLLUTION CONTROL | Tippecanoe | 2013-09-20 09:20 | 2013-09-20 10:20 | 2013-09-20 13:02 | 0 |  | Fairgrounds regulator | Construction Related construction materials (2x4 s suction hose and discharge hose) stuck in gate. | Removed Blockage See Report | SSO Reached Public Land
55359 | 39810 | IN0043273 | AMERICAN SUBURBAN UTILITIES | Tippecanoe | 2013-08-26 | 2013-08-26 07:00 | 2013-08-26 10:15 | 0 |  | Plant discharged Indian Creek | Partially Treated Release Equipment Failure The blowers kick off sometime during the night. Water was going threw the plant but not being treated. Stop discharge pump contact tank to old pond will work water back into system. | Going to have a meeting with owner maintenance men and figure how to prevent this from happening again. Called Patrick Colcord and reported problem. | SSO Reached Receiving Water | Indian Creek
60249 | 34816 |  | SHARPSVILLE WATER UTILITY | Tipton | 2013-02-25 19:00 | 2013-02-27 03:00 | 2013-03-01 14:23 | 29768 | gallons | Station A pump pit Sharpsville | Untreated release from Station A pump pit Sharpsville due to low pump rates causes by snow melt and rain. Unpermitted Discharge Untreated Release |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Mud Creek
58582 | 36795 | IN0021474 | TIPTON MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-05-06 | 2013-05-07 | 2013-05-07 09:24 | 0 |  | CSO Outfall #5 | CSO Outfall #5 was active from 12:00am to 7:00pm due to a water main break. | 12:00am to 7:00pm 2013 the problem is fixed.
58582 | 37787 | IN0021474 | TIPTON MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-06-09 | 2013-06-10 | 2013-06-12 07:54 | 0 |  | 415 S Independance | Rain 5.0 inches | Repaired Pipe Repair Lateral | SSO Affected Private Property
58582 | 37777 | IN0021474 | TIPTON MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-06-10 | 2013-06-10 | 2013-06-11 13:43 | 0 |  | 220 W. Washington St. | Rain 4 inches Exceeded Max Capacity Notified of complaint by Beck Ruark IDEM Representative at 10:00AM on 6-11-13. No evidence of sewage in street water drained as collection system caught up. |  | SSO Affected Private Property
58582 | 38869 | IN0021474 | TIPTON MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-06-21 07:00 | 2013-06-21 08:30 | 2013-06-21 13:01 | 0 |  | Tipton Park | Pump station failure. | Cleaned it up with Vactor Put down NTH we shut down bathrooms for the weekend to get a new pump. | SSO Affected Private Property
60249 | 35850 | IN0040614 - Terminated | SHARPSVILLE WATER UTILITY | Tipton | 2013-01-13 00:01 | 2013-01-14 10:00 | 2013-01-15 09:37 | 263702 | gallons | Station A pump pit Sharpsville | Precipitation event coupled with snow melt resulted in high inflow levels to WWTP and caused a non permitted unrtreated release from the plant to receiving waters. |  | SSO Reached Receiving Water | Mud Creek
60249 | 35213 | IN0040614 - Terminated | SHARPSVILLE WATER UTILITY | Tipton | 2013-01-30 08:50 | 2013-01-30 15:00 | 2013-01-31 12:25 | 8809 | gallons | Station A pump pit Sharpsville IN | Precipitation event coupled with ground moisture and thaw resulted in untreated unpermitted release from Station A pump pit to Mud Creek |  | SSO Reached Receiving Water | Mud Creek
60249 | 38601 | IN0040614 - Terminated | SHARPSVILLE WATER UTILITY | Tipton | 2013-06-13 01:30 | 2013-06-17 02:00 | 2013-06-17 03:00 | 168902 | gallons | Station A pump pit Sharpsville Mud Creek | Rain 2.25 inches. Overflow due to 2.25 inches of rain on 6/13 and 6/14 and power outage 6/15 |  | SSO Reached Receiving Water | Mud Creek
58542 | 35503 | IN0040762 | WINDFALL MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-01-14 07:50 | 2013-01-14 18:00 | 2013-01-14 13:30 | 0 |  | Manholes #4 and #5 | Precipitation event and snow melt caused untreated release from manholes to storm sewers. | Reduced flow from Lift Stations #2 and #3. | SSO Reached Public Land; Storm Sewer
58542 | 36231 | IN0040762 | WINDFALL MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-04-19 07:30 |  | 2013-04-19 10:11 | 0 |  | Manholes #3 #4 and #5 | Precipitation event triggered untreated release from multiple manholes to storm sewers. | Reduced flow from Lift Stations #2 and #3 to relieve overflow. | SSO Reached Public Land; Storm Sewer
58542 | 36712 | IN0040762 | WINDFALL MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-04-19 07:30 | 2013-04-21 13:00 | 2013-04-28 12:51 | 2000 | gallons | Manholes #3 #4 and #5. | Flow from precipitation exceeded capacity of sewer collection system resulting in untreated release from manholes to storm sewer. | Reduced flow from Lift Stations #2 and #3. | SSO Reached Public Land; Storm Sewer
58542 | 37903 | IN0040762 | WINDFALL MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-06-10 07:20 | 2013-06-17 | 2013-06-19 16:50 | 5000 | gallons | Manhole #3 #4 and #5 Round Prairie Creek | Rain 4.35 inches 6/20/13 4.62 inches 6/13/13 3.07 inches | Reduced flows from L/S #2 and #3 | SSO Reached Public Land
58542 | 37764 | IN0040762 | WINDFALL MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-06-10 07:20 |  | 2013-06-10 15:13 | 0 |  | Manhole #3 #4 and #5 | Rain 4.35 inches Manhole | Reduced flows from L.S. #2 and #3 | SSO Reached Public Land
58542 | 43634 | IN0040762 Oufall 001 | WINDFALL MUNICIPAL WASTE WATER TREATMENT PLANT | Tipton | 2013-12-22 10:30 | 2013-12-22 21:30 | 2013-12-23 09:06 | 2000 | gallons | Manhole #3 and #4 | Rain 2.0 inches Rainfall plus 6 of snow melt. | See Report | SSO Reached Public Land | Round Prairie Creek
108732 | 35438 | No NPDES Permit | Brookville Lake Regional Waste District | Union | 2013-03-23 10:00 | 2013-03-23 11:30 | 2013-03-24 07:01 | 2000 | gallons | Force main along west side of State Highway 101 approximately 2000 feet North of the intesection of Pea Ridge Road. | Untreated Release to ground and unnamed receiving waters during repair of broken force main. | Damaged section of pipe was removed and replaced. Sealed the junctions tested the system and put back in service. | SSO Reached Receiving Water
| 39479 | Terminated Permit | Brookville Lake Regional Waste District | Union | 2013-08-15 15:30 | 2013-08-16 10:00 | 2013-08-16 15:45 | 0 |  | New Fairfield Lift Station Intersection of Klein & causeway | Equipment Failure Pump Station Failure. The breaker for the control circuitry was tripped. | Repaired Pump Station Breaker was reset and system resumed normal operation. Breaker may have been inadvertently tripped late yesterday afternoon while station was being serviced. Ground around lift station was flushed with water. All breakers will be double-checked after stations have been serviced. | SSO Affected Private Property
| 35437 | Unpermitted |  | Union | 2013-03-16 | 2013-03-21 | 2013-03-23 02:34 | 100000 | gallons | Force main along west side of Stater Highway 101 approximately 2000 feet north of the intersection of Pea Ridge Road. | An undiscovered break in the force main resulted in an untreated release to the ground surrounding the break and unnamed receiving waters. | Repairs to force main scheduled 3/24/13. Bypass pumping will continue until repairs are completed. | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 42996 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-21 08:15 | 2013-12-22 03:00 | 2013-12-21 21:05 | 28125 | gallons | 601 W Mill Road Manhole | Exceeded Max Capacity Rain 6.27 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Dry Branch
12329 | 42945 | 0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 08:00 | 2013-12-22 18:30 | 2013-12-21 21:05 | 51750 | gallons | 6616 Lincoln Avenue | Exceeded Max Capacity Rain 6.27 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Affected Private Property
11292 | 35590 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-04 18:00 | 2013-01-04 19:00 | 2013-01-05 12:40 | 0 |  | 7200 Sweet Gum Court | Obstructed residential lateral resulted in untreated release into residential basement | Cleaned lateral connection to remove grease blockage. Affected area cleaned by homeowner. Lateral connection will be televised to ensure that lateral is clear of grease waste. Homeowner informed of backflow prevention requirements. Area was visually monitored for 72 hours. | SSO Basement Backup
11292 | 35594 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-05 15:45 | 2013-01-05 16:15 | 2013-01-07 09:45 | 10 | gallons | 709 Thornberry Drive | Obstruction in private property lateral resulted in untreated release from the cleanout to the private property around the clean out. | Cleaned lateral connection. Affected area cleaned and lime applied. Lateral connection will be televised to determine source of obstruction. Corrective actions dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35506 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-09 11:00 | 2013-01-09 13:00 | 2013-01-10 10:00 | 50 | gallons | 1304 North Heidelbach Avenue | Untreated release into residential basement due to residential grease waste. | Cleared lateral connection and main sewer. Release eliminated. Homeowner cleaned affected area. Lateral and Main sewer will be televised to ensure that lines are clear of obstruction. Homeowner informed of backflow prevention requirements. Area was visually monitored for 72 hours. | SSO Basement Backup
11292 | 35601 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-09 12:15 | 2013-01-09 16:30 | 2013-01-10 11:55 | 40264 | gallons | Ninth Avenue CSO 020 | City water main broken upstream from CSO diversion structure. Untreated release to receiving waters | Water Utility construction shut down and repaired broken water main. The outfall and diversion structure will be visually monitored for 72 hours. | SSO Reached Receiving Water | Ohio River
11292 | 35837 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-11 02:00 | 2013-01-11 02:15 | 2013-01-11 20:45 | 150 | gallons | Oak Meadow #2 Lift Station Wet Well41 Oak Meadow | Precipitation event triggered high wet well alarm at lift station. Station hydraulically maximized triggering an untreated release to the ground surrounding the Lift Station. | Affected area cleaned. Sewers will be instpected to determine source of infiltration. Corrective actions dependent upon findings. Lift Station will be visually monitored for 72 hours. | SSO Reached Public Land
11292 | 35835 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-11 07:20 | 2013-01-11 08:15 | 2013-01-11 19:20 | 200 | gallons | 3 Richardt Avenue | Precipitation event and main sewer obstruction combined to cause an untreated release into a residential basement | Cleaned main sewer to remove obstruction. Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. Area was visually monitored for 72 hours. | SSO Basement Backup
11292 | 35507 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-11 07:40 | 2013-01-11 08:15 | 2013-01-11 19:40 | 150 | gallons | 3130 Waterman Drive | Main sewer blockage by residential grease resulted in untreated release into residential basement. | Cleaned main sewer line to remove obstruction. Release eliminated. Affected area cleaned by homeowner. Sewer will be televised to ensure tht line is clear of grease waste. Homeowner infromed of backflow prevention requirements. Area was visually monitored for 72 hours.
11292 | 35838 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-11 08:45 | 2013-01-11 10:00 | 2013-01-11 21:15 | 200 | gallons | 520 Sout Barker Avenue | Main sewer obstruction resulted in untreated release from a cleanout to the ground around it. | Cleaned main sewer to remove obstruction. Affected area cleaned and lime applied. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35836 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-11 14:05 | 2013-01-11 14:15 | 2013-01-11 21:20 | 10 | gallons | 1221 Western Hills Avenue | Lateral connection obstruction resulted in an untreated release from a Property Line Cleanout to surrounding ground. | Cleaned lateral connection to remove obstruction. Affected area cleaned. Lateral connection will be televised to determine source of obstruction. Corrective action dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35833 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-12 16:15 | 2013-01-14 13:30 | 2013-01-13 15:30 | 1000 | gallons | Manhole at 4129 Kedzie Avenue | Precipitation event and main sewer line obstruction triggered an untreated release from a manhole to the surrounding ground. | Cleaned main sewer to remove obstruction. Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area was visually monitored for 72 hours. | SSO Reached Public Land
11292 | 35832 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-12 17:10 | 2013-01-13 04:30 | 2013-01-13 15:30 | 500 | gallons | 101 East Eichel Avenue | Precipitation event and sewer obstruction resulted in untreated release from a manhole and into residential basement. | Cleaned main sewer to remove obstruction. Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective action dependent upon findings. Homeowner informed of backflow prevention requirements. Area was visually monitored for 72 hours. | SSO Basement Backup; SSO Reached Public Land
11292 | 35831 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-12 23:30 | 2013-01-13 02:00 | 2013-01-13 15:30 | 100 | gallons | 713 East Buena Vista Road | precipitation event anc obstructed main sewer line triggered an untreated release into a residential basement. | Cleaned main sewer to remove obstruction. Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. Area was visually monitored for 72 hours. | SSO Basement Backup
11292 | 35827 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-13 | 2013-01-13 23:00 | 2013-01-13 15:30 | 82500 | gallons | Manhole at 2524 North Baker Avenue | Precipitation event caused manhole cover to be dislodged resulting in an untreated release to receiving waters. | Manhold cover secured to casing. Area was monitored visually for 72 hours. | SSO Reached Receiving Water | Pigeon Creek
11292 | 35828 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-13 | 2013-01-13 19:00 | 2013-01-13 15:30 | 18000 | gallons | Manhole at 711 West Mill Road | Precipitation event caused hydraulic maximization of collection system resulting in an untreated release from a manhole to the surrounding ground and storm sewer. | Affected area cleaned. Manhole was visually monitored for 72 hours. | SSO Reached Public Land; Storm Sewer
11292 | 35829 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-13 00:15 | 2013-01-13 00:30 | 2013-01-13 15:30 | 150 | gallons | Lift Station Wet Well in Oak Meadow #2 Lift Station at 41 Oak Meadow | Precipitation event triggered a high wet well alarm at Lift Station resulting in untreated release to surrounding ground. | Affected area cleaned. Lift Station was visually monitored for 72 hours. | SSO Reached Public Land
11292 | 35834 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-15 11:50 | 2013-01-15 12:30 | 2013-01-15 19:15 | 10 | gallons | 1125 West Mill Road | Main sewer obstruction resulted in untreated release from a residential private property clean out to the ground surrounding the cleanout. | Cleaned main sewer to remove obstruction. Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35625 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-15 14:45 | 2013-01-15 16:00 | 2013-01-16 14:30 | 60 | gallons | 619 North Tenth Avenue | Residential grease obstruction in main sewer caused untreated release from manhole to ground surrounding manhole. | Cleared residential grease obstruction. Cleaned affected area. Sewer will be televised to ensure that line is clear. Area will be visually monitored for 72 hours. | SSO Reached Public Land
11292 | 35620 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-16 06:30 | 2013-01-16 08:30 | 2013-01-16 16:30 | 8000 | gallons | Ninth Avenue CSO 020 | Debris in lift station pump resulted in overflow and untreated release to receiving waters. | Used combination truck to rmove debris from pump and station and return it to service. Lift station will be inspected for 72 hours. The outfall and diversion structure will be visually monitored fro 72 hours. | SSO Reached Receiving Water | Ohio River
11292 | 35830 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-16 21:00 | 2013-01-17 | 2013-01-17 20:55 | 500 | gallons | Manhole at 1151 East Olmstead Avenue | Failure of a flood protection sluice gate resulted in a sewer obstruction and untreated release from a manhole to surrounding ground | The Levee Authority removed the malfuntioning sluice gate. Main sewer was cleaned to remove obstruction. Affected area cleaned. Levee Authority to replace flood protection sluice gate. Sewer will be televised to determine that line is clear of obstructions. Corrective actions dependent upon findings. Area was visually monitored for 72 hours. | SSO Reached Public Land
11292 | 35652 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-18 11:05 | 2013-01-18 11:20 | 2013-01-18 16:30 | 1500 | gallons | 2424 Schutte Road Schutte Road Lift Station | Power failure resulted in untreated release from Lift Station to receiving waters public ground and storm spillway. | Utility crews restored power to station with generator until commercial power was restored. Affected area was cleaned and lime applied. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water; Storm Sewer | Bayou Creek
11292 | 35648 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-19 18:45 | 2013-01-19 22:30 | 2013-01-20 15:00 | 22500 | gallons | 2424 Schutte Road Shutte Road Lift Station | Lift Station pump failures resulted in Untreated release from lift station to public ground storm spillway and receiving waters | Contractor installed bypass pump in upstream manhole to resume normal station operation. Lift Station to operate on bypass pumping while pumps are repaired. Affected area cleaned and lime applied. Bypass pump will be monitored until lift station pumps are reinstalled. | SSO Reached Public Land; SSO Reached Receiving Water; Storm Sewer | Bayou Creek
11292 | 35147 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-24 14:15 | 2013-01-24 15:45 | 2013-01-25 09:20 | 0 |  | 1016 Wyngate Court Evansville IN | Sanitary sewer obstructed and releasing untreated waste from a damaged section of sewer. | City sewer crew cleaned sewer and removed obstruction and construction crew repaired the damaged section of sewer. Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Reached Public Land; Storm Sewer
11292 | 35145 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-26 14:45 | 2013-01-26 15:00 | 2013-01-27 13:40 | 0 |  | 7734 Miranda Drive Property Line Cleanout Evansville IN | main sewer obstruction caused untreated release from property line clean out. | Cleaned main sewer to clear obstruction. Affected area around property line clean out limed. Sewer wil be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will ve visually monitored for 72 hours. | SSO Affected Private Property
11292 | 34996 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-29 14:45 | 2013-01-29 15:15 | 2013-01-30 11:45 | 5 | gallons | 18 East Delaware Street Evansville IN | Crew responsed to request for service. Private property cleanout had evidence of prior release but was not releasing upon arrival | Crew cleaned lateral connection to remove obstruction. Release eliminated. Cleaned affected area. Lateral connection will be televised to determine source of obstruction. Corrective actions dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 34997 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-30 01:15 | 2013-01-30 01:50 | 2013-01-30 23:15 | 3500 | gallons | Manhole at 2524 North Baker Avenue Evansville IN | Crew observed wastewater releasing from manhole. | Manhole cover dislodged during rain event. resecured manhole cover to casting. Area will be monitored for 72 hours | SSO Reached Receiving Water | Pigeon Creek
11292 | 34998 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-01-30 07:00 | 2013-01-30 09:30 | 2013-01-30 23:15 | 25 | gallons | manhole at 1117 Englewood Court Evansville IN | Crew responded to report of wastewater release from manhole. | As a result of 2+ inch rain combined collection system was hydraulically maximized. Affected area cleaned. Sewer will be televised to determine that sewer is free and clear of obstructions. Corrective actions dependent upon findings. Area will be visuall monitored for 72 hours. | SSO Reached Public Land
11292 | 35078 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-02-02 | 2013-02-04 13:00 | 2013-02-05 08:20 | 14400 | gallons | 4909 Sunnyside Court Evansville IN | Private Sanitary Sewer Overflow untreated release. Manholes releasing wastewater due to grease obstructions in the private SSO for The Arbors at Red Bank Apartments. | Utility crew cleaned private sewer to remove obstructions release was eliminated. Property owner responsible for cleanup. Property owner instructed to remove grease from manholes and implement preventative maintenance schedule. Area will be visually monitored for 72 hours.ss | SSO Reached Public Land; SSO Reached Receiving Water | Carpentier Creek
11292 | 34994 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-02-09 13:30 | 2013-02-09 14:00 | 2013-02-10 10:00 | 75 | gallons | 2601 Westchester Drive Evansville IN | Cleanout releasing wastewater | Private Property cleanout releasing wastewater. Main sewer line obstructed. Cleaned main sewer line. Release eliminated.Affected area cleaned adn lime applied. Sewer will be televised to determine source of obstruction. Corrective acctions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 34788 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-02-25 07:00 | 2013-02-25 08:30 | 2012-02-25 22:00 | 225 | gallons | Manhole at 3019 Hartig Avenue | Report of manhole releasing water. Release caused by root infiltration | Crew cleaned main sewer to remove root obstruction release eliminated. Affected area cleaned. Utility to televise sewer to ensure that roots were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land; Surface Soil
11292 | 34792 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-02-26 14:45 | 2013-02-26 20:00 | 2013-02-27 14:45 | 33000 | gallons | Manhole at 4110 North Fourth Avenue Evansville IN | Report of manhole at 4110 North Fourth Avenue releasing wastewater | Crew responded to report of manhole releasing wastewater. Crew attempted to clean main sewer to remove unknown obstruction but was unsuccessful. Thus a bypass pump was installed in manhole to eliminate release and to allow crew to clean main sewer to remove obstruction. Upon investigation it was determined that root infiltration was the source of the release. Affected area was cleaned. Utility to televise sewer to ensure that roots were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Dry Branch
11292 | 34390 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-08 15:00 | 2013-03-08 15:45 | 2013-03-09 14:15 | 900 | gallons | 381 Sorenson Avenue Manhole | Untreated Release Equipment Failure SSO Estimated Flow Released 900 Gallons. Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that roots and rags in the main sewer were the source of the release. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned. Utility to televise sewer to ensure that line is free clear of obstructions. corrective actions dependent up findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land; Storm Sewer
11292 | 34391 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-11 10:30 | 2013-03-11 11:45 | 2013-03-12 10:15 | 5 | gallons | 2919 Hartig Avenue Manhole | Untreated Release Equipment Failure SSO Estimated Flow Released 5 Gallons. Crew responded to request for service. manhole had evidence of prior release but was not releasing when crew arrived. Upon investigation it was determined that root infiltration was the cause of the release. Crew cleaned main to remove root obstruction release eliminated. | Affected area cleaned. Utility to televise sewer to ensure that roots were removed. Corrective actions dependent upon findings. area will be visually monitored for 72 hours | SSO Reached Public Land
11292 | 34380 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-12 11:30 | 2013-03-12 11:45 | 2013-03-12 19:30 | 10 | gallons | 2705 Oakley Street Private Property Cleanout | Untreated Release SSO Estimated Flow Released 10 Gallons. Crew responded to request for service. Private property cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned lateral connection to remove obstruction release eliminated. | Affected area cleaned and lime applied. Lateral connection will be televised to determine source of obstruction. Corrective actions dependent upon finding. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 36706 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-05-07 18:45 | 2013-05-08 20:00 | 2013-05-08 15:35 | 100 | gallons | 111 Beale Street Ground | Untreated Release Equipment Failure SSO Estimated Flow Released 100 Gallons. Crew responded to report of wastewater periodically releasing in backyard. Upon CCTV pipe inspection it was determined that a hole in a section of the min sewer was the cause of the release. Construction crew replaced damaged section of main sewer release eliminated. | Affected area cleaned and lime applied. Utility replaced damaged section of main sewer. Area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 36704 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-05-09 13:00 | 2013-05-09 13:45 | 2013-05-10 12:40 | 90 | gallons | 8181 Berry Drive Manhole Ground | Untreated Release Equipment Failure SSO Estimated Flow Released 90 Gallons: Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that root infiltration in the main sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | Affected area cleaned and Lime applied. Utility to televise sewer to ensure that roots were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 36705 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-05-09 13:40 | 2013-05-09 14:00 | 2013-05-10 12:40 | 20 | gallons | 1221 N Garvin Street Private Property Cleanout Ground | Untreated Release Equipment Failure CSSR Estimated flow Released 20 Gallons. Crew responded to request for service. Private property cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned later connection to remove obstruction release eliminated. | Affected area cleaned. Lateral connection will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 37549 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-06 12:40 | 2013-06-07 10:30 | 2013-06-07 12:29 | 80 | gallons | 3708 Stringtown Road Ground | Equipment Failure manhole Pipe Failure Crew responded to request for service. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. A CCTV pipeline inspection of the sewer segment determined that a broken section of the main sewer was the source of the obstruction. | Removed Blockage Repaired Pipe Affected area cleaned Utility to replace section of broken sewer. area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 39198 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-06 12:40 | 2013-06-26 10:30 | 2013-07-26 10:47 | 0 |  | 3708 Stringtown Road Ground | Equipment Failure. Crew responded to request for service. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminate. A CCTV pipeline inspection of the sewer segment determined that a broken section of the main sewer was the source of the obstruction. | See Report | SSO Affected Private Property
11292 | 39206 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-12 09:15 | 2013-06-12 13:00 | 2013-06-13 08:30 | 0 |  | 51 Nunning Road Manhole | Crew responded to report of wastewater releasing from manhole. Upon arrival it was determined that grease obstructions in the main sewer was the source of the release. Crew cleaned main sewer to remove obstructions release eliminated. | See Report | SSO Affected Private Property; SSO Reached Receiving Water | Carpentier Creek
11292 | 38073 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 09:45 | 2013-06-24 12:00 | 2013-06-24 20:00 | 0 |  | 1304 N Heidelbach Ave Floor Drain | Equipment Failure Manhole Lateral Crew responded to report of wastewater releasing in basement. Upon investigation it was determined that the main sewer was obstructed with residential grease waste. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned by homeowner. Homeowner informed of backflow prevention requirements. Area was visually monitored for 72 hours. | SSO Basement Backup
11292 | 39207 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 09:45 | 2013-06-24 12:00 | 2013-06-24 20:00 | 0 |  | 1304 N Heidelbach Ave floor drain manhole house lateral | Crew responded to report of wastewater releasing in basement. Upon investigation it was determined that the main sewer was obstructed with residential grease waste. Crew cleaned main sewer to remove obstruction release eliminated. | See Report | SSO Basement Backup
11292 | 38074 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 10:00 | 2013-06-24 11:15 | 2013-06-24 20:00 | 0 |  | 600 Drexel Drive | Exceeded Max Capacity Rain 5.30 inches Manhole Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 38075 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 10:00 | 2013-06-24 11:15 | 2013-06-24 20:00 | 0 |  | Manhole | Exceeded Max Capacity Rain 5.30 inches Manhole Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 39209 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 10:00 | 2013-06-24 11:15 | 2013-06-24 20:00 | 0 |  | 600 Drexel Drive Manhole Manhole | Crew responded to report of wastwewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Affected Private Property; SSO Reached Receiving Water | Wolf Creek
11292 | 38098 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 12:00 | 2013-06-24 13:45 | 2013-06-24 | 0 |  | 4080 Millersburg Rd | Exceeded Max Capacity Rain 5.30 inches. Crew observed that manhole had evidence of prior release. Upon investigation it was determined that the manhole cover dislodged during rain event due to the collection system being hydraulically maximized. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Firlick Creek
11292 | 39210 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 12:00 | 2013-06-24 13:45 | 2013-06-24 20:00 | 0 |  | 4080 Millersburg Road Manhole | Rain 5.30 inches Crew observed that manhole had evidence of prior release. Upon investigation it was determined that the manhole cover dislodged during rain event due to the collection system being hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Firlick Creek
11292 | 38099 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 12:00 | 2013-06-24 13:45 | 2013-06-24 20:00 | 0 |  | Manhole | Exceeded Max Capacity Rain 5.30 inches. Crew observed that manhole had evidence of prior release. Upon investigation it was determined that the manhole cover during rain event due to the collection system being hydraulically maximized. | Affected area cleaned and lime applied. Manhole cover secured to casting. area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Firlick Creek
11292 | 38101 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 12:10 | 2013-06-24 12:40 | 2013-06-24 20:00 | 0 |  | 41 Oak Meadow | Exceeded Max Capacity Rain 5.30 inches Crew responded to high wet well alarm. Upon investigation it was determined that the lift station was hydraulically maximized. | Affected area cleaned. Lift Station was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 38102 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 12:10 | 2013-06-24 12:40 | 2013-06-24 20:00 | 0 |  | Lift Station Wet Well | Exceeded Max Capacity Rain 5.39 inches. Crew responded to high wet well alarm. Upon investigation it was determined that the lift station was hydraulically maximized. | Affected area cleaned. Lift station was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 39219 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 12:10 | 2013-06-24 12:40 | 2013-06-24 20:00 | 0 |  | 41 Oak meadows Lift Station Wet Well | Rain 5.30 inches Exceeded Max Capacity Crew responded to high wet well alarm. Upon investigation it was determined that the lift station was hydraulically maximized. | Affected area Cleaned. Lift Station was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 38110 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 13:30 | 2013-06-24 16:00 | 2013-06-24 20:00 | 0 |  | Baumgartner Road & Burch Drive | Exceeded Max Capacity Rain 5.30 inches | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Little Pigeon Creek
11292 | 39220 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 13:30 | 2013-06-24 16:00 | 2013-06-24 20:00 | 0 |  | Baumgart Road & Burch Drive Manooles | Rain 5.30 inches Exceeded Max Capacity. Crew responded to report of wastewater releasing from manholes. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water
11292 | 38111 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 13:30 | 2013-06-24 16:00 | 2013-06-24 20:00 | 0 |  | Manhole | Exceeded Max Capacity Rain 5.30 inches Crew responded to report of wastewater releasing from manholes. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Little Pigeon Creek
11292 | 38118 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 14:00 | 2013-06-24 16:30 | 2013-06-24 20:00 | 0 |  | 711 W Mill Rd | Exceeded Max Capacity Rain 5.30 inches. Crew responded to report of wastewater releasing from manhole. upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Dry Branch
11292 | 39221 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 14:00 | 2013-06-24 16:30 | 2013-06-24 20:00 | 0 |  | 711 W Mill Road Manhole | Rain 5.30 inches Exceeded Max Capacity. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Dry Branch
11292 | 38121 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-24 14:00 | 2013-06-24 16:30 | 2013-06-24 20:00 | 0 |  | Manhole | Exceeded Max Capacity Rain 5.30 inches. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Dry Branch
11292 | 38204 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-25 14:00 | 2013-06-26 17:30 | 2013-06-25 21:15 | 0 |  | 4820 Hogue Rd - Cleanout | Equipment Failure Manhole House Lateral. This is being reported as a Private Sanitary Sewer Overflow on behalf of Ms. Tina Brumley property manager of The Arbors at Red Bank Apartments and Mr. William Phipps property owner of 4820 Hogue Rd. Crew responded to report of cleanout releasing wastewater. Upon investigation it was determined that roots in the private sanitary sewer manhole and house lateral were the source of the release. Private sewer contractor vacuumed wastewater from manhole and removed roots release eliminated. | Property owners responsible for cleanup. Area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 38201 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-25 14:00 | 2013-06-26 17:30 | 2013-06-25 21:15 | 0 |  | 4909 Sunnyside Court - Manhole | Equipment Failure Manhole House Lateral. This is being reported as a Private Sanitary Sewer overflow on behalf of ms. Tina Brumley property manager of The Arbors at Red Bank Apartments and Mr. William Phipps property owner of 4820Hogue Rd. Crew responded to report of cleanout releasing wastewater. Upon investigation it was determined that roods in the private sanitary sewer manhole and house lateral were the source of the release. Private sewer contractor vacuumed wastewater from manhole and removed roots release elimiminated. | Property owners responsible for cleanup. Area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 38554 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-09 10:40 | 2013-07-09 11:10 | 2013-07-10 09:30 | 750 | gallons | 2601 N Saint Joseph Ave Private Property Cleanout | Equipment Failure House Lateral Pump Station Failure . Crew responded to report of private property cleanout releasing wastewater. Upon investigation it was determined that tangle pump float cords at the release. Lift station crew turned pumps on manual and untangled pump float cords release eliminated. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water | Locust Creek
11292 | 39286 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-21 20:25 | 2013-07-21 21:15 | 2013-07-22 11:10 | 0 |  | 2550 N Baker Avenue | Rain 2.04 inches Exceeded Max Capacity Crew observed that manhole cover had displaced during rain event. This was the result of five hour 2.04 inch rain. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 39283 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-21 20:25 | 2013-07-21 21:15 | 2013-07-22 11:10 | 0 |  | 2524 N Baker Ave | Rain 2.04 inches Exceeded Max Capacity. Crew observed that manhole had released during rain event. This was the result of five hour 2.04 inch rain | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 39285 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-22 03:30 | 2013-07-22 04:30 | 2013-07-22 11:10 | 0 |  | Manhole | Rain 2.04 inches Exceeded Max Capacity. Crew observed that manhole had released during rain event. This was the result of five hour 2.04 inch rain. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water
11292 | 39287 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-22 03:30 | 2013-07-22 04:30 | 2013-07-22 11:10 | 0 |  | First Avenue Siphon Chamber | Rain 2.04 inches Exceeded Max Capacity Crew observed that manhole cover had displaced during rain event. This was the result of five hour 2.04 inch rain. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 39292 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-24 11:30 | 2013-07-24 17:00 | 2013-07-24 18:45 | 0 |  | 5417 Stringtown Road Manhole | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area will be monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water | Little Pigeon Creek
11292 | 39313 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-29 20:45 | 2013-07-29 21:35 | 2013-07-30 18:00 | 0 |  | 5704 Ashbrooke Rd Floor Drain | Equipment Failure Crew responded to report of wasrtewater releasing in basement. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | See Report | SSO Basement Backup
11292 | 39481 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-08-15 07:40 | 2013-08-15 08:00 | 2013-08-15 16:00 | 0 |  | 3815 Stringtown Road utility Cleanout | Equipment Failure. Crew responded to request for service. Utility cleanout had evidence of prior release but was not releasing upon arrival. Upon investigation it was determined that root infiltration in the main sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | Remove Blockage See Report | SSO Affected Private Property
11292 | 40016 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-09-01 02:00 | 2013-09-01 04:45 | 2013-09-01 14:30 | 0 |  | 600 Drexel Drive Manhole | Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water | Wolf Creek
11292 | 40269 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-09-19 13:35 | 2013-09-19 14:05 | 2013-09-20 13:05 | 0 |  | 8401 West Terrance Drive University Heights Force Main | Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that a damaged air release valve on the force main was the source of the release. Crew vacuumed wastewater from manhole and closed air release shut off valve release eliminated. | Removed Blockage See Report | SSO Affected Private Property
11292 | 40680 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-04 18:00 | 2013-10-24 18:45 | 2013-10-05 16:45 | 0 |  | 701 W Berkeley Ave Manhole | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that root infiltration in the main sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | Removed Blockage See Report | SSO Reached Public Land
11292 | 40693 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-06 03:40 | 2013-10-06 04:45 | 2013-10-06 21:45 | 0 |  | 2524 N Baker Ave Manhole | Rain 3.21 inches Exceeded Max Capacity Crew observed that manhole had released during rain event. This was the result of a 24 hour 3.21 inch rain. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 40689 | IN0032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-06 03:40 | 2013-10-06 04:45 | 2013-10-06 21:45 | 0 |  | 2550 N Baker Ave First Ave Siphon Chamber | Rain 3.21 inches Exceeded Max Capacity Crew observed that manhole had released during rain event. This was the result of a 24 hour 3.21 inch rain. | Affected area cleaned. area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water
11292 | 40015 | IN0032956 Affected Waterbody - Storm Retention Basin | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-08-31 16:40 | 2013-08-31 19:00 | 2013-08-31 20:41 | 0 |  | 418 Holly Hill Drive Storm Ditch | Crew responded to request for service. Upon investigation it was determined that root infiltration in the min sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | Removed Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 37593 | IN0032956 Affected Waterbody: Carpentier Creek Tributary | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-12 09:15 | 2013-06-12 13:00 | 2013-06-13 08:30 | 28125 | gallons | 51 Nunning Road Carpentier Creek Tributary | Equipment Failure Manhole. Crew responded to report of wastewater releasing from manhole. Upon arrival it was determined that grease obstructions in the main sewer was the source of the release. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned and lime applied. Sewer main will be televised to ensure that obstruction were removed. Corrective actions dependent upon findings. Utility FOG staff will investigate the food establishments that are tributary to the main sewer to find a potential source of the grease waste. Area will be visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 37671 | IN0032956 - Bayou Creek Tributary | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-06-12 13:00 | 2013-06-12 14:15 | 2013-06-13 13:00 | 375 | gallons | 5301 Nurrenburn Road | Equipment Failure This is being reported das a private Sanitary Sewer overflow on behalf of Mr. Steve Craig manager of Burdette Park. The Utility responded to report of wastewater releasing from manhole. Upon investigation it was determined that the private sewer was obstructed. Utility crew cleaned private sewer to remove obstruction release eliminated. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 40938 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-14 10:00 | 2013-10-14 12:15 | 2013-10-15 08:45 | 0 |  | 1407 Sandallwood Court Sanitary Sewer | Equipment Failure Crew responded to report of wastewater releasing from sanitary sewer. Upon investigation it was determined that a damaged section of sewer was the source of the release. Construction crew repaired damaged section of sewer release eliminated. | Repaired Pipe See Report | SSO Affected Private Property
11292 | 41815 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-11-12 14:10 | 2013-11-12 15:30 | 2013-11-13 13:45 | 0 |  | 719 Sonntag Avenue | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the min sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Removed Blockage See Report | SSO Reached Public Land
11292 | 42022 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-11-17 17:50 | 2013-11-17 21:55 | 2013-11-18 16:45 | 0 |  | 614 Biddle Court Manhole | Equipment Failure Crew responded to request for service. Upon investigation it was determined that root infiltration i the main sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction released eliminated. | Removed Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water | Wolf Creek
11292 | 42027 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-11-18 18:00 | 2013-11-18 19:30 | 2013-11-19 16:30 | 0 |  | 4909 Sunnyside Court Manhole | Equipment Failure This is being reported as a private sanitary sewer overflow on behalf of Ms. Tina Brumley property manager of The Arbors at Red Bank Apartments. The utility responded to report of manhole releasing wastewater. Upon arrival it was determined that debris in the private sanitary sewer system for the apartments was the source of the release. Utility crew cleaned private sewer to remove obstructions release eliminated. | Removed Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water | Carpentier Creek
11292 | 42029 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-11-19 12:30 | 2013-11-19 17:30 | 2013-11-20 12:00 | 0 |  | 4008 N First Avenue Manhole | Equipment Power This is being reported as a private sanitary sewer overflow. The utility responded to report of wastewater releasing from manhole. Upon arrival it was determined that a grease obstruction in the private sanitary sewer system for the commercial development was the source of the release. Private sewer contractor cleaned sewer to remove grease obstruction release eliminated. | Removed Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water | Dry Branch
11292 | 42308 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-04 09:30 | 2013-12-04 17:30 | 2013-12-05 09:00 | 0 |  | 4008 N First Avenue Manhole | Equipment Failure this is being reported as a private sanitary sewer overflow. The utility responded to report of wastewater releasing from manhole. Upon arrival it was determined that a grease obstruction in the private sanitary sewer system for the commercial development was the source of the release. Utility crew cleaned sewer to remove grease obstruction release eliminated. | Removed Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water | Dry Branch
11292 | 42424 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-08 11:50 | 2013-12-08 14:00 | 2013-12-09 09:45 | 0 |  | 3330 W Maryland St Manhole | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed with residential grease waste. Crew cleaned main sewer to remove obstruction release eliminated. | Removed Blockage. See Report | SSO Reached Public Land
11292 | 42995 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-21 08:15 | 2013-12-22 03:00 | 2013-12-21 21:05 | 112500 | gallons | 711 W. Mill Road | Exceeded Max Capacity Rain 6.27 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Dry Branch
11292 | 42946 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-21 08:15 | 2013-12-22 03:00 | 2013-12-21 21:05 | 168750 | gallons | Baumgart Raod & Burch Drive Manholes | Exceeded Max Capacity Rain 6.27 inches Crew responded to report of wastewater releasing from manholes. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Little Pigeon Creek
11292 | 42999 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-21 08:15 | 2013-12-22 17:30 | 2013-12-21 21:05 | 99750 | gallons | 700 Fairway Drive Manhole | Exceeded Max Capacity Rain 6.27 inches Crew observed wastewater releasing form manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Dry Branch
11292 | 43006 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-21 09:30 | 2013-12-22 06:30 | 2013-12-21 21:05 | 94500 | gallons | Manholes | Exceeded Max Capacity Rain 6.27 inches Crew responded to report of wastewater releasing from manholes. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Carpentier Creek
11292 | 43001 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-21 09:30 | 2013-12-22 06:30 | 2013-12-21 21:05 | 94500 | gallons | 4211 Western Avenue | Exceeded Max Capacity Rain 6.27 inches Crew responded to report of wastewaer releasing from manholes. Upon investigation it was determined that the collection system was hydraulically maximized | See Report | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Carpentier Creek
11292 | 43092 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-23 15:45 | 2013-12-23 16:05 | 2013-12-24 13:00 | 250 | gallons | 600 Drexel Drive Manhole | Equipment Failure Utility responded to high wet well alarm at University Heights Lift Station. Upon investigation it was determined that a root obstruction in the pumps was preventing the lift station from operating. Lift Station crew removed obstruction from pumps to resume normal station operation release eliminated. | See Report | SSO Affected Private Property; SSO Reached Receiving Water | Wolf Creek
11292 | 43101 | IN0032956 Outfall123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-24 09:45 | 2013-12-24 11:15 | 2013-12-24 18:45 | 25 | gallons | 5215 Stratford Rd | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Removed Blockage | SSO Reached Public Land
11292 | 35295 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-26 16:50 | 2013-03-26 17:50 | 2013-03-27 11:15 | 10 | gallons | 113 W Berkeley Ave Private Property Cleanout Ground | Untreated Release Equipment Failure SSO Estimated Flow Released: 10 Gallons. Crew responded to report of cleanout releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 40723 | IN0032956 Outfall 023 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-02 06:35 | 2013-10-02 19:10 | 2013-10-03 09:45 | 0 |  | First avenue Siphon Chamber | Rain 2.85 inches Exceeded Max Capacity Crew observed that manhole had released during rain event. This was the result of a two hour 2.85 inch rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 40731 | IN0032956 Outfall 023 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-02 16:00 | 2013-10-02 16:30 | 2013-10-03 09:45 | 0 |  | 2628 Hillcrest Terrance Floor Drain | Rain 2.85 inch Exceeded Max Capacity Crew responded to report of wastewater releasing from abasement floor drain. Upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Basement Backup
11292 | 40721 | IN0032956 Outfall 023 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-02 16:10 | 2013-10-02 16:35 | 2013-10-03 09:45 | 0 |  | 2550 N Baker Avenue | Rain 2.85 inches Exceeded Max Capacity Crew observed that manhole had released during rain event. This was the result of a two hour 2.85 inch rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 40726 | IN0032956 Outfall 023 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-02 16:10 | 2013-10-02 16:35 | 2013-10-03 09:45 | 0 |  | 2524 N Baker Avenue | Rain 2.85 inches Exceeded Max Capacity Crew observed that manhole had released during rain event. This was the result of a two hour 2.85 inch rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 40729 | IN0032956 Outfall 023 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-02 18:35 | 2013-10-02 19:10 | 2013-10-03 09:45 | 0 |  | Manhole | Rain 2.85 inches Exceeded Max Capacity Crew observed that manhole had released during rain event. This was the result of a two hour 2.85 inch rain. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
11292 | 40694 | IN0032956 Outfall 023 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-10-06 10:47 | 2013-10-06 05:30 | 2013-10-06 21:45 | 0 |  | Affected area cleaned. area will be visually monitored for 72 hours. | Rain 3.21 inches Exceeded Max Capacity Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Dry Branch
11292 | 42534 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-15 16:50 | 2013-12-15 18:30 | 2013-12-16 13:45 | 0 |  | 620 Drexel Dr Basement Floor | Crew responded to report of wastewater releasing in basement. Upon investigation it was determined that root infiltration in the main sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | Removed Blockage See Report | SSO Basement Backup
11292 | 43234 | IN0032956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-30 14:20 | 2020-12-30 13:03 | 2013-12-31 11:45 | 5 | gallons | 6013 Whitethorne Drive Manhole | Equipment Failure Crew responded to report of manhole releasing wastewater. Manhole had evidence of prior release but was not releasing upon arrival. Crew cleaned main sewer to remove obstruction release eliminated. | See Report | SSO Reached Public Land
11292 | 42198 | IN0032956 Outfall 123 Receiving Water Impacted - Private Lake | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-11-21 15:40 | 2013-11-21 16:50 | 2013-11-22 08:30 | 0 |  | 6015 Kratzville Road Manhole | Equipment failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. A CCTV pipeline inspection of the sewer segment determined that grease and rags in an offset section of the main sewer was the source of the obstruction. | Removed Blockage Repaired Pipe See Report | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 34672 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-13 09:20 | 2013-03-13 09:35 | 2013-03-13 17:35 | 0 |  | 2811 Saint Joseph Avenue Manhole | Untreated Release Equipment Failure SSO Estimated Flow Released: 200 Gallons. Crew responded to report of manhole releasing wastewater. Manhole had evidence of prior release but was not releasing when crew arrived. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property; Storm Sewer
11292 | 35325 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-17 15:50 | 2013-03-17 16:10 | 2013-03-26 14:31 | 100 | gallons | 2761 N Kentucky Ave Private Property Manhole Ground | Untreated Release Equipment Failure CSSR Estimated Flow Released 100 Gallons. Crew responded to report of manhole releasing wastewater. Up[on investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35329 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-18 | 2013-03-18 07:00 | 2013-03-26 14:31 | 6000 | gallons | 711 W Mill Rd Ground/Storm Sewer Bayou Creek Tributary | Untreated Release Rain SSO Estimated Flow Released 6000 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. This was a result of 3.84 of precipitation in a 24 hour period. | Affected area cleaned. Manhole was visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water | Bayou Creek
11292 | 35328 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-18 10:00 | 2013-03-18 11:00 | 2013-03-26 14:31 | 525 | gallons | 2000 N Fifth Ave Floor Drain Basement | Untreated release Equipment Failure Basement | Affected area cleaned by homeowner. Sewer will be televised to determine that line is clear of obstructions. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35324 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-21 06:45 | 2013-03-21 07:15 | 2013-03-26 18:40 | 750 | gallons | 8600 University Blvd Bypass Manhole Ground | Untreated Release Equipment Failure SSO Estimated Flow Released 750 Gallons. Utility contractor renovating USI lift station reported wastewater releasing from bypass manhole. Upon investigation it was determined that ht bypass pump had failed. Contractor replaced bypass pump release eliminated. | Release contained to construction limits and pumped into bypass manhole. Contractor cleaned affected area. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35305 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-22 10:15 | 2013-03-22 10:30 | 2013-04-01 16:30 | 15 | gallons | 4129 Meadowridge Rd Private Property Cleanout Ground | Untreated Release Equipment Failure SSO Estimated Flow Released 15 Gallons. Crew responded to request for service. Private property cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned lateral connection to remove obstruction release eliminated. | Affected area cleaned. lateral connection will be televised to determine source of obstruction. Corrective actions dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35459 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-22 10:15 | 2013-03-22 10:30 | 2013-03-26 | 0 |  | 4129 Meadowridge Road Private Property Cleanout Ground | Untreated Release Equipment Failure SSO Estimated Flow Released: 15 Gallons. Crew responded to request for service. Private property cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned lateral connection to remove obstruction release estimated. | Affected area cleaned. Lateral connection will be televised to determine source of obstruction. Corrective actions dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35302 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-26 11:30 | 2013-03-26 18:00 | 2013-04-01 | 100 | gallons | 2108 N Heidellbach Avenue Floor Drain Basement | Untreated Release Equipment Failure Estimated CSSR Property Backup Release: 100 gallons. Crew responded to report of a wastewater release in basement. upon investigation it was determined that the main sewer was obstructed. Crew clean main sewer to remove obstruction release eliminated. | Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area was visually monitored for 72 hours. | SSO Basement Backup
11292 | 35304 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-03-26 16:50 | 2013-03-26 17:50 | 2013-04-01 11:15 | 10 | gallons | 113 W Berkeley Ave Private property Cleanout Ground | Untreated Release Equipment Failure SSO Estimated Flow Released: 10 Gallons. Crew responded to report of cleanout releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 35474 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-01 08:30 | 2013-04-01 09:30 | 2013-04-02 08:15 | 10 | gallons | 819 W Iowa Street Utility Cleanout Ground | Untreated Release Equipment Failure CSSR Estimated Flow Released 10 Gallons. Crew responded to request for service. Utility Cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 37115 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-11 07:00 | 2013-04-11 13:00 | 2013-04-11 15:30 | 100 | gallons | 707 Kleymeyer Avenue Ground CSSR Estimated Flow Released 100 Gallons. Crew responded to request for service. Upon investigation it was determined that roots in the main sewer were the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | Untreated release Equipment Failure Rain 1.96 inches CSSR Estimated Flow Released 100 Gallons. Crew responded to request for service. Upon investigation it was determined that roots in the main sewer were the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | Affected area cleaned. Sewer will be televised to ensure that roots were removed. Corrective actions dependent upon findings. Area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 36495 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-11 17:05 | 2013-04-11 17:50 | 2013-04-12 16:15 | 0 |  | 4717 N Kentucky Avenue Floor Drain Basement | Untreated Release Equipment Failure Estimated SSO Property backup release 250 gallons. Crew responded to report for a wastewater release in basement. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. Area will be visually monitored for 72 hours. | SSO Basement Backup
11292 | 37117 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-11 17:05 | 2013-04-11 17:50 | 2013-04-12 16:15 | 250 | gallons | 4717 N Kentucky Ave Floor Drain Basement | Untreated Release Equipment Failure Rain 1.96 inches Estimated SSO Property Backup Release 250 gallons. Crew responded to report of wastewater release in basement. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. Area will be visually monitored for 72 hours. | SSO Basement Backup
11292 | 37114 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-12 08:30 | 2013-04-01 09:30 | 2013-04-02 08:15 | 10 | gallons | 819 W Iowa Street Utility Cleanout Ground | Untreated release Equipment Failure CSSR Estimated Flow Released 10 Gallons. Crew responded to request for service. Utility cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer sill be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 37119 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-19 00:30 | 2013-04-19 05:00 | 2013-04-19 23:00 | 27000 | gallons | 711 W Mill Road Manhole Ground/Storm Sewer Bayou Creek Tributary | Untreated Release Rain 2.60 inches. SSO Estimated Flow released 27000 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. This was a result of 2.60 inches of precipitation in a 7 hour period. | Affected area cleaned. Manhole will be visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water; Storm Sewer | Bayou Creek
11292 | 36570 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-19 00:30 | 2013-04-19 05:00 | 2013-04-19 23:00 | 27000 | gallons | 711 W Mill Road Manhole Ground/Storm Sewer Bayou Creek Tributary | Untreated Release Rain SSO Estimated Flow Released: 27000 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. This was a result of 2.60 inches of precipitation in a 7 hour period. | Affected area cleaned. Manhole will be visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water; Storm Sewer | Bayou Creek
11292 | 37120 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-04-30 | 2013-04-30 11:00 | 2013-04-30 10:40 | 4000 | gallons | 1187 Burch Drive Manhole Ground | Untreated Release Equipment Failure SSO Estimated Flow Released 4000 Gallons. maintenance crew observed that manhole cover was displaced and immediate area showed evidence that manhole had released. | Manhole cover reinstalled and affected area cleaned. Utility to televise sewer to ensure that line is free and clear of obstructions. Corrective action dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
11292 | 36996 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-05-12 02:00 | 2013-05-12 18:00 | 2013-05-13 12:30 | 420 | gallons | 9101 Meghan Court Manhole Ground/Storm Sewer | Untreated Release Equipment Failure. SSO Estimated Flow released 420 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the cause of the release was root intrusion in the manhole that has obstructed the main sewer. Crew cleaned manhole and main sewer to remove root obstruction release eliminated. | Affected area cleaned and lime applied. Utility to repair manhole to eliminate root intrusion. Area was visually monitored for 72 hours. | SSO Affected Private Property
11292 | 37099 | in0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-05-17 13:30 | 2013-05-10 16:00 | 2013-05-18 08:00 | 100 | gallons | 8221 Berry Drive Manhole/Floor Drain Ground Basement | Untreated Release Equipment Failure SSO Estimated Flow Released 100 Gallons. Crew responded to request for service. Manhole was releasing upon arrival and property owner communicated that wastewater had released from basement floor drain. Upon investigation it was determined that roots and rags in the main sewer were the cause of the release. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned and lime applied. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area was visually monitored for 72 hours. | SSO Basement Backup
11292 | 37100 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-05-20 20:00 | 2013-05-20 21:45 | 2013-05-21 18:15 | 190 | gallons | 1009 Old Post Road Manhole/Floor Drain Ground/ Storm Sewer/ Lower Level | Untreated Bypass Equipment Failure SSO Estimated Flow Released 190 Gallons. Crew responded to the report of wastewater releasing from manhole. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. Afterwards the property owner of 1005 Old Post Road communicated to crew that wastewater had released from lower level floor drain during sewer cleaning. A CCTV pipeline inspection of the sewer segment determined that roots in a broken section of the main sewer was the source of the obstruction. | Affected area cleaned. Utility to replace section of broken sewer. Homeowner informed of backflow prevention requirements. Area will be visually monitored for 72 hours. | SSO Basement Backup; Storm Sewer
11292 | 37265 | IN0032956 West | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-05-21 22:35 | 2013-05-21 22:45 | 2013-05-22 16:01 | 500 | gallons | 8440 Wolf Creek Drive Manhole/Condensate Drain Ground/Storm Sewer/ Garage Wolf Creek Tributary | Untreated Release Power Failure SSO Estimated Flow Released 500 Gallons. Utility responded to power outage at Key West Lift Station. External power coming into the station had failed Utility Crews restored power to station using generator. Release occurred during downtime. Vectren restored power and station put back in service at 12:30am (5.22/2013) | Affected area cleaned and lime applied. Homeowner informed of backflow prevention requirements. area will be visually monitored for 72 hours. | SSO Affected Private Property | Wolf Creek
12329 | 35619 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-01 18:30 | 2013-01-01 22:45 | 2013-01-02 17:30 | 100 | gallons | 4319 Clover Drive | Main sewer line blockage caused Untreated release to residential basement private property and storm ditch. | Removed roots and rags from sewer main line to relieve release. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property; Storm Sewer
12329 | 35603 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-09 09:45 | 2013-01-09 16:30 | 2013-01-10 09:35 | 100 | gallons | 400 SE Eighth Street | Grease obstruction of main sewer line resuulted in untreated release from private property cleanout to surrounding ground. | Cleaned main sewer and lateral connectio to remove obstruction. Affected area cleaned. Sewer main and lateral connection will be televised to ensure that lines are clear of grease waste. Area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 35599 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-09 14:45 | 2013-01-09 16:00 | 2013-01-10 12:45 | 10 | gallons | 2320 East Iowa Street | Root obstruction in lateral connection resulted in untreated release from the property line clean out to the surrounding ground. | Affected area cleaned. Lateral connection will be televised to ensure that roots were removed. Corrective actions dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 35811 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-11 13:00 | 2013-01-11 13:45 | 2013-01-11 21:15 | 225 | gallons | Manhole at 3401 Margybeth Avenue | Main sewer obstruction caused an untreated release from manhole to surrounding ground. | Cleaned main sewer to remove obstruction. Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land
12329 | 35816 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-12 23:00 | 2013-01-13 08:30 | 2013-01-13 15:30 | 25 | gallons | Manhole at 1117 Englewood Court | Main sewer obstruction triggered untreated release to the surrounding ground | Cleaned main sewer to remove obstruction. Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective acctions dependent upon findings. Area was visually monitored for 72 hours. | SSO Reached Public Land
12329 | 35826 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-13 | 2013-01-13 19:00 | 2013-01-13 15:30 | 33000 | gallons | Manhole at 2018 Maxwell Avenue | Precipitation event resulted in increased flow dislodging a manhole cover and allowing an untreated release from the manhole to the surrounding ground and receiving waters. | Manhole cover secured to casing. Area was monitored visually for 72 hours. | SSO Reached Receiving Water | Pigeon Creek
12329 | 35817 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-13 00:15 | 2013-01-13 05:00 | 2013-01-13 15:30 | 7125 | gallons | Manhole at 1475 East Diamond Avenue | Precipitation event triggered manhole overflow of untreated release to surrounding ground and storm sewer. | Combined collection system was hydraulically maximized. Affected area was cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; Storm Sewer
12329 | 35823 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-13 00:40 | 2013-01-13 02:45 | 2013-01-13 15:30 | 150 | gallons | 4212 Saddlebrooke Lane | Precipitation event and equipment failure caused an untreated release into residence. | Cleaned main sewer to remove obstruction and determined that backflow preventer at residence was not working. Affected area cleaned by home owner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area was visually monitored for 72 hours. | SSO Basement Backup
12329 | 35824 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-13 13:00 | 2013-01-13 21:00 | 2013-01-13 15:30 | 12000 | gallons | Manhole at 501 Plaza Drive | Precipitation event triggered an untreated release from Manhole due to system being hydraulically maximized. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land
12329 | 35825 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-13 13:00 | 2013-01-13 21:00 | 2013-01-13 15:30 | 4800 | gallons | Manhole at 6601 East Oak Street | Precipitation event hydraulically maximized collection system resulting in untreated release from manhole to surrounding ground and storm sewer. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; Storm Sewer
12329 | 35772 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-14 15:00 | 2013-01-14 16:15 | 2013-01-15 14:40 | 6000 | gallons | 600 East Chandler Avenue | Precipitation event triggered untreated release into residential basement. | Main sewer and basement had evidence of surcharge but were not obstructed when crew arrived. Affected area cleaned by homeowner. Sewer will be televised to ensure tht line is clear of obstructions. Homeowner informed of backflow prevention requirements. Area was visually monitored for 72 hours. | SSO Basement Backup
12329 | 35814 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-01-15 08:30 | 2013-01-15 10:00 | 2013-01-15 19:15 | 300 | gallons | Manhole at 2031 North Cross Pointe Boulevard | main sewer obstruction caused untreated release to surrounding and storm ditch. | Cleaned main sewer to remove obstruction. Affected area cleaned and limed. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land
12329 | 34360 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-04 15:45 | 2013-03-04 19:30 | 2013-03-05 15:15 | 0 |  | 807 Oak Hill Road Manhole | Untreated Release Equipment Failure Cssr Estimated Flow Released 450 Gallons. Crew responded to report of wastewater release from manhole. Upon investigation it was determined that the main sewer was obstructed with debris and grease waste. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned Sewer main will be televised to ensure that lines are clear of obstructions. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; Storm Sewer
12329 | 36675 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-04 15:45 | 2013-03-04 19:30 | 2013-04-26 16:22 | 450 | gallons | Manhole at 807 Oak Hill Road | Main sewer blockage resulted in untreated release from manhole to surrounding ground and storm sewer. | Cleaned main sewer to remove obstruction. Cleaned affected area. Sewer main will be televise to ensure that lines are clear of obstructions. Area will be visually monitored for 72 hours. | SSO Reached Public Land; Storm Sewer
12329 | 36676 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-17 14:15 | 2013-03-17 14:30 | 2013-04-26 16:22 | 10 | gallons | 207 Kenmore Drive | Main sewer obstruction caused untreated release into residential basement. | Cleaned main sewer to remove obstruction. Release eliminated. Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informaed of backflow prevention requirements. Area will be visually monitored for 72 hours. | SSO Basement Backup
12329 | 35323 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-20 18:45 | 2013-03-20 23:15 | 2013-03-26 18:40 | 810 | gallons | 732 Southfield Rd Manhole Ground | Untreated Release Equipment Failure SSO Estimated flow Released 810 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main to remove obstruction release eliminated. CCTV pipe inspection it was determined that a communication ground rod in the sewer was the source of the obstruction. | Affected area cleaned. Communication contractor to remove ground rod and repair sewer. Area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 39224 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-03 14:00 | 2013-06-03 16:15 | 2013-06-04 13:07 | 0 |  | 1167 E Riverside Drive Private Property Cleanout | Equipment Failure | See Report | SSO Affected Private Property
12329 | 37535 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-03 14:00 | 2013-06-03 16:15 | 2013-06-04 13:07 | 30 | gallons | 1167 Riverside Drive Private Property Cleanout | Equipment Failure Manhole House Lateral | Remove Blockage. Crew responded to request for service. Upon investigation it was determined that roots rags in the main sewer were the source of the release. Crew cleaned main sewer to remove obstructions release eliminated. Area was visually monitored for 72 hours. | SSO Affected Private Property
12329 | 37537 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-04 15:15 | 2013-06-04 15:45 | 2013-06-04 22:31 | 10 | gallons | 5236 Vogel Road property Line Cleanout. | Equipment Failure House Lateral | Removed Blockage. Crew responded to report of wastewater releasing from cleanout. Property line cleanout had evidence of prior release but was not releasing when crew arrived. Crew cleaned lateral connection to remove construction release eliminated. | SSO Affected Private Property
12329 | 39228 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-14 14:50 | 2013-06-14 16:00 | 2013-06-14 17:50 | 0 |  | 2018 Glenmoor Road Manhole | Equipment Failure. Crew responded to report of manhole releasing wastewater. manhole had evidence of prior release but was not releasing when crew arrived. Crew cleaned main sewer to remove obstruction release eliminated. | See Report | SSO Affected Private Property
12329 | 37673 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-14 14:50 | 2013-06-14 16:00 | 2013-06-14 17:50 | 5 | gallons | 2818 Glenmoor Road Manhole | Equipment Failure Crew responded to report of manhole releasing wastewater. Manhole had evidence of prior release but was not releasing when crew arrived. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned and lime applied. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 38069 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-17 12:55 | 2013-06-17 14:00 | 2013-06-18 12:00 | 0 |  | 1716 Greencastle Dr Manhole | Equipment Failure Manhole Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned and lime applied. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water
12329 | 39229 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-17 12:55 | 2013-06-17 14:00 | 2013-06-18 12:00 | 0 |  | 1716 Greencastle Drive Manhole | Equipment Failure. Crew responded to report of manhole releasing wastewater. upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | See Report | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Indian Woods Lake
12329 | 38070 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-17 12:55 | 2013-06-17 14:00 | 2013-06-18 12:00 | 0 |  | Manhole | Equipment Failure Manhole Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned and lime applied. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water
12329 | 37748 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-17 12:55 | 2013-06-17 14:00 | 2013-06-18 12:00 | 65 | gallons | 1716 Greencastle Drive Indian Woods Lake | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned and lime applied. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water
12329 | 39231 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 10:45 | 2013-06-24 14:15 | 2013-06-24 20:00 | 0 |  | 1475 E Diamond Avenue Manhole | Rain 5.30 inches Exceeded Max Capacity. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. | Affected area cleaned. Area was visually monitored for 72 hours. |  | Pigeon Creek
12329 | 38078 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 10:45 | 2013-06-24 14:15 | 2013-06-24 20:00 | 0 |  | Manhole | Exceeded Max Capacity Rain 5.30 inches. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 38077 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 10:45 | 2013-06-24 14:15 | 2013-06-24 20:00 | 0 |  | 1475 E Diamond Ave | Exceeding Max Capacity Rain 5.30 inches. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 38089 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 11:45 | 2013-06-24 14:45 | 2013-06-24 20:00 | 0 |  | 2701 N Stockwell Rd Manhole | Exceeded Max Capacity Rain 5.30 inches Manhole. Lift station crew observed that wastewater had released from manhole during rain event. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow 18.0 MGD during maintenance of aeration basins. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land
12329 | 39236 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 11:45 | 2013-06-24 14:45 | 2013-06-24 20:00 | 0 |  | 2701 N Stockwell Rd Manhole | Rain 5.30 inches Exceeded Max Capacity Lift station crew observed that wastewater had released from manhole during rain event. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at designed flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land
12329 | 38109 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 13:00 | 2013-06-24 16:00 | 2013-06-24 20:00 | 0 |  | Manhole | Exceeded Max Capacity Rin 5.30 inches. lift Station crew observed that wastewater was releasing from manhole during rain event. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Eagle Creek
12329 | 38106 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 13:00 | 2013-06-24 16:00 | 2013-06-24 20:00 | 0 |  | 2020 S Green River Road | Exceeded Max Capacity Rain 5.30 inches. Lift station crew observed that wastewater was releasing from manhole during rain event. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water
12329 | 39239 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 13:00 | 2013-06-24 16:00 | 2013-06-24 20:00 | 0 |  | 2020 S Green River Road Manhole | Rain 5.30 inchesExceeded Max Capacity Lift Station crew observed that wastewater was releasing from manhole during rain event. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water
12329 | 39235 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 15:00 | 2013-06-24 17:00 | 2013-06-24 20:00 | 0 |  | 5300 Hitch Peters Road Manhole | Rain 5.30 inchesExceeded Max Capacity Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow fo 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Affected Private Property
12329 | 39234 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 15:00 | 2013-06-25 03:15 | 2013-06-24 20:00 | 0 |  | 501 Plaza Drive Manhole | Rain 5.30 inchesExceeded Max Capacity Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hyraulically maximized. East WWTP operating at design flow of 18.0MGD during maintenance of aeration basins. | wAffected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Stockfleith Ditch
12329 | 38127 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 15:00 | 2013-06-25 03:15 | 2013-06-24 20:00 | 0 |  | 501 Plaza Dr Manhole | Exceeded Max Capacity Rain 5.30 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water
12329 | 39232 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 15:00 | 2013-06-25 03:15 | 2013-06-24 20:00 | 0 |  | 6601 E Oak Street Manhole | Rain 5.30 inches Exceeded Max Capacity. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water | Stockfleith Ditch
12329 | 38133 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 15:00 | 2013-06-24 17:00 | 2013-06-24 | 0 |  | 5300 Hitch Peters Rd Manhole | Exceeded Max Capacity Rain 5.30 inches. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow of 18.0MGD during maintenance of aeration basins. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Affected Private Property
12329 | 38063 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-27 05:45 | 2013-06-27 06:45 | 2013-06-27 23:40 | 0 |  | 6218 Twickingham Drive | Power Failure Manhole House lateral Pump Station Failure. Crew responded to report of property backup and manhole releasing wastewater. Upon investigation it was determined that an internal power failure at Twickingham Lift Station was the source of the release. Crew restored internal power to lift station release eliminated. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Lift Station will be visually monitored for 72 hours. | SSO Basement Backup; SSO Reached Public Land; SSO Affected Private Property
12329 | 39240 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-27 05:45 | 2013-06-27 06:45 | 2013-06-27 23:40 | 0 |  | 6218 Twickingham Dr Manhole Manhole House Lateral Pump Station Failure | Power Failure. Crew responded to report of property backup and manhole releasing wastewater. Upon investigation it was determined that an internal power failure at Twwickingham Lift Station was the source of the release. Crew restored internal power to lift station release eliminated. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned. Lift Station will be visually monitored for 72 hours. | SSO Basement Backup; SSO Reached Public Land; SSO Affected Private Property
12329 | 38066 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-27 05:45 | 2013-06-27 06:45 | 2013-06-27 23:40 | 0 |  | Manhole | Power Failure Manhole House lateral Pump Station Failure. Crew responded to report of property backup and manhole releasing wastewater. Upon investigation it was determined that and internal power failure at Twickingham Lift Station was the source of the release. Crew restored internal power to Lift Station release eliminated. East WWT operating at design Flow of 18.MGD during maintenance of aeration basins. | Affected area cleaned. Homeowner informed of backflow prevention requirements. Lift Station will be visually monitored for 72 hours. | SSO Basement Backup; SSO Reached Public Land; SSO Affected Private Property
12329 | 38460 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-07-03 15:10 | 2013-07-03 16:15 | 2013-07-03 20:15 | 130 | gallons | 5304 Great Lakes Drive Manhole | Equipment Failure Manhole Pump Station Failure Crew responded to report of manhole releasing wastewaer. Upon investigation it was determined that a pump controller failure at Lakeside Manor Lift Station was the source of the release. Lift station crew replaced pump controller release eliminated. East WWTP Operating at design flow of 18.0 MGD during maintenance of aeration basins. | sAffected area cleaned. Area was visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water
12329 | 39373 | IN0033073 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-08-08 14:00 | 2013-08-08 14:15 | 2013-08-09 13:30 | 0 |  | 1475 E. Diamond Ave Manole | Equipment Failure. Crew responded to report of wastewater releasing from manhole. manhole had evidence of prior release but was not releasing when crew arrived. Upon investigation it was determined that debris from a broken water main was obstructing the main sewer. Crew cleaned manhole to remove obstruction release eliminated.East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 40707 | IN0033073 Outfall 003 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-02 22:15 | 2013-10-02 23:00 | 2013-10-03 09:45 | 0 |  | 430 Washington Ave Basement Floor | Rain 2.85 inches Exceeded Max Capacity Crew responded to report of wastewater releasing in basement. upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Basement Backup
12329 | 40684 | IN0033073 Outfall 003 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-06 05:30 | 2013-10-06 08:00 | 2013-10-06 21:45 | 0 |  | 312 Harrison Boulevard Basement Floor | Equipment Failure Crew responded to report of wastewater releasing in basement. Upon investigation it was determined that the main sewer was obstructed with residential grease waste. Crew cleaned main sewer to remove obstruction release eliminated. | Removed Blockage See Report | SSO Basement Backup
12329 | 41098 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-17 13:55 | 2013-10-17 16:45 | 2013-10-18 12:15 | 0 |  | 7201 E Chandler Avenue garage floor | Equipment Failure Crew responded to request for service. Upon investigation it was determined that roots in the lateral connection were the source of the release. Crew cleaned lateral connection to remove obstruction release eliminate. | Removed Blockage See Report | SSO Affected Private Property
12329 | 41862 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-11-10 16:10 | 2013-11-10 18:15 | 2013-11-11 10:30 | 0 |  | 942 plaza Drive Private Property Cleanout. | Equipment Failure Crew responded to report of cleanout releasing wstewater. Upon investigation it was determined that roots in the lateral connection were the source of the release. Crew cleaned lateral connection to remove obstruction release eliminated. | Removed Blockage See Report | SSO Reached Public Land; SSO Affected Private Property
12329 | 41813 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-11-12 13:55 | 2013-11-12 14:50 | 2013-11-13 13:45 | 0 |  | 950 S.Hebron Avenue Manhole | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Remove Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water
12329 | 42020 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-11-15 13:35 | 2013-11-15 15:05 | 2013-11-18 16:45 | 0 |  | 10 E Blackford Ave Private Property Cleanout | Equipment Failure Crew responded to request for service. Private property cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned lateral connection to remove obstruction release eliminated. | Removed Blockage See Report | SSO Affected Private Property
12329 | 42276 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-02 10:30 | 2013-12-02 11:45 | 2013-12-03 09:55 | 0 |  | 100 Washington Avenue Area Drain | Equipment Failure Crew responded to report of area drain releasing wastewater. Upon investigation it was determined that the area drain was connected to a private lateral that was obstructed with grease and rags. Crew cleaned lateral from area drain to remove obstructions released eliminated. | Removed Blockage | SSO Reached Public Land
12329 | 42331 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-04 14:00 | 2013-12-04 15:00 | 2013-12-05 12:40 | 0 |  | 2 E Powell avenue Private Property Cleanout | Equipment Failure Crew responded to report of cleanout releasing wastewater. Upon investigation it was determined that the lateral connection was obstructed. Crew cleaned lateral connection to remove obstruction release eliminated. | Removed Blockage See Report | SSO Reached Public Land; SSO Affected Private Property
12329 | 42933 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 05:45 | 2013-12-22 02:00 | 2013-12-21 21:05 | 30750 | gallons | 1475 E Diamond Avenue | Rain 6.27 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 42942 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 07:00 | 2013-12-22 19:30 | 2013-12-21 21:05 | 109500 | gallons | 501 Plaza Drive Manhole | Rain 6.27 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Stockfleith Ditch
12329 | 42944 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 08:00 | 2013-12-22 18:30 | 2013-12-21 21:05 | 62100 | gallons | 6601 E Oak Street Manhole | Rain 6.7 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | See Reports | SSO Reached Public Land; SSO Reached Receiving Water | Stockfleith Ditch
12329 | 43005 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 09:55 | 2013-12-22 01:00 | 2013-12-21 21:05 | 90480 | gallons | 2020 S Green River Road Manhole | Exceeded Max Capacity rain 6.27 inches Crew responded to report of wastewater releasing from manhole. upon investigation nit was determined that the collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Eagle Creek
12329 | 42952 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 19:00 | 2013-12-21 20:00 | 2013-12-21 21:05 | 12000 | gallons | 2001 N Weinbach Avenue | Exceeded Max Capacity Rain 6.27 inches Crew observed wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 42954 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 19:20 | 2013-12-22 05:30 | 2013-12-21 21:05 | 30480 | gallons | 7301 Lincoln Avenue Manhole | Exceeded Max Capacity Rain 6.27 Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Stockfleith Ditch
12329 | 43768 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-22 19:20 | 2013-12-31 16:20 | 2013-12-31 19:20 | 200 | gallons | 1921 Hawthorne Ave Ground | Equipment Failure Crew responded to report of wastewater releasing from sanitary sewer. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Removed Blockage See Report | SSO Affected Private Property
12329 | 38131 | IN0033073 Waterbody Affected Stockfleith Ditch | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-24 15:00 | 2013-06-25 03:15 | 2013-06-24 20:00 | 0 |  | 6601 E Oak Street Manhole | Exceeded Max Capacity Rain 5.30 inches. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. East WWTP operating at design flow of 18.0 MGD during maintenance of aeration basins. | Affected area cleaned and lime applied. Area was visually monitored for 72 hours. | SSO Reached Public Land; SSO Affected Private Property; SSO Reached Receiving Water
12329 | 39225 | IN0033073 (East) | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-06-04 15:15 | 2013-06-04 15:45 | 2013-06-04 22:31 | 0 |  | 5236 Vogel Road Property Line Cleanout | Equipment Failure | See Report | SSO Affected Private Property
12329 | 34870 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-17 09:00 | 2013-03-17 11:10 | 2013-03-18 09:00 | 650 | gallons | 732 Southfield Road Manhole Ground | Untreated Release Equipment Failure SSO Estimated Flow Released: 650 Gallons. Crew responded to report of wastewater releasing from manholes. Upon in investigation it was determined that root infiltration was the cause of the release. Crew cleaned main to remove root obstruction release eliminated. | Affected area cleaned. Utility to televise sewer to ensure that roots were removed. Corrective actions dependent upon findings. area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 34863 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-17 12:35 | 2013-03-17 13:05 | 2013-04-03 10:15 | 400 | gallons | 6408 Washington Avenue Floor Drain Basement | Untreated Release Equipment Failure Rain 3.84 Estimated SSO Property Backup release: 400 gallons. Crew responded to report of a wastewater release in basement. Upon investigation it was determined that the main sewer was obstructed. Crew leaned main sewer to remove obstruction release eliminated. | Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. Area will be visually monitored for 72 hours. | SSO Basement Backup
12329 | 34866 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-17 14:15 | 2013-03-17 14:30 | 2013-03-18 09:00 | 10 | gallons | 207 Kenmore Drive Floor Drain | Untreated Release Equipment Failure Estimated SSO Property Backup Release: 10 gallons Rain 3.84 Crew responded to report of a wastewater release in residence. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. Area will be visually monitored for 72 hours. | SSO Basement Backup
12329 | 35326 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-18 03:00 | 2013-03-18 04:00 | 2013-03-26 14:31 | 0 |  | 1475 E Diamond Ave Manhole Ground/Storm Sewer Pigeon Creek | Untreated Release Rain CSST Estimated Flow Released 1500 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. This was a result of 3.84 of precipitation in a 24 hour period. |  |  | Pigeon Creek
12329 | 35444 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-18 07:20 | 2013-03-18 18:30 | 2013-03-26 | 16750 | gallons | 501 Plaza Drive Manhole | Untreated Release 3.84 Rain SSO Estimated Flow released: 16750 Gallons. Crew responded to report of wastewater releasing from manhole. upon investigation it was determined that the collection system was hydraulically maximized. This was a result of 3.84 inch rain in a 24 hour period. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water; Storm Sewer
12329 | 35457 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-18 07:20 | 2013-03-18 18:30 | 2013-03-26 14:31 | 0 |  | 6601 E Oak Street Manhole Ground/Storm Sewer/Stockfleith Ditch Tributary | Untreated Release Rain 3.84 inches SSO Estimated Flow released 1675 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the collection system was hydraulically maximized. This was a result of 3.84 inches of precipitation in a 24 hour period. | Affected area cleaned. Area was visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water; Storm Sewer
12329 | 35445 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-18 09:45 | 2013-03-18 20:30 | 2013-03-26 | 300 | gallons | 1407 Fuquay Rd Manhole Ground | Untreated Release Equipment failure Rain 3.84 inches. SSO Estimated Flow Released 300 gallons. Crew responded to request for service. Upon investigation it was determined that the main sewer was obstructed. Crew leaned main to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine ounce of obstruction. corrective ac5ions dependent upon findings. area was visually monitored for 72 hours. | SSO Affected Private Property
12329 | 35442 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-18 10:25 | 2013-03-18 10:30 | 2013-03-26 | 0 |  | 7301 Lincoln Ave Manhole Ground | Untreated release Equipment Failure SSO Estimated Flow Released: 250 Gallons. Utility contractor installing new pumps for martins Lane Lift Station reported wastewater releasing from force main discharge manhole. Upon investigation it was determined that the lift station was pumping excess capacity. The variable frequency drives for the pumps were adjusted to meet discharge sewer capacity release eliminated. | Affected area cleaned Lift Station was visually monitored for 72 hours. | SSO Affected Private Property
12329 | 34859 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-03-19 14:40 | 2013-03-19 15:45 | 2013-03-20 12:15 | 10 | gallons | 2212 Hialeah Drive Manhole | Untreated Release Equipment Failure SSO Estimated Flow Released: 10 Gallons. Crew responded to report of manhole releasing wastewater. Manhole had evidence of prior release but was not releasing when crew arrived. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 37121 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-14 13:30 | 2013-04-14 13:45 | 2013-04-15 12:40 | 3 | gallons | 516 N Boeke Road Utility Cleanout Ground | Untreated Release Equipment Failure CSSR Estimated Flow Released 3 Gallons. Crew responded to request for service. Utility cleanout had evidence of prior release but was not releasing upon arrival. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 36568 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-19 00:30 | 2013-04-19 03:00 | 2013-04-19 23:00 | 3750 | gallons | 1475 E Diamond Ave Manhole Ground/Storm Sewer Pigeon Creek | Untreated Release Rain CSSR Estimated Flow Released 3.750 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. This was a result of 2.60 inches of precipitation in a 7 hour period. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Affected Private Property; SSO Reached Receiving Water; Storm Sewer | Pigeon Creek
12329 | 37122 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-19 00:30 | 2013-04-19 03:00 | 2013-04-19 23:00 | 3750 | gallons | 1475 E Diamond Avenue Manhole Ground/Storm Sewer/ Pigeon Creek | Untreated Release Rain 2.60 inches CSSR Estimated Flow Released 3.750 gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. This was a result of 2.60 of precipitation in a 7 hour period. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Affected Private Property; Storm Sewer | Pigeon Creek
12329 | 36567 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-19 07:00 | 2013-04-19 09:00 | 2013-04-19 23:00 | 600 | gallons | 2800 Longacre Drive Manhole Ground | Untreated Release Power Failure SSO Estimated Flow Released 600 gallons. Crew responded to report of wastewaer releasing from manhole. Upon investigation it was determined that a power outage at the Blossom Lane Lift Station was the source of the release. Utility crews restored to station release eliminated. | Affected area cleaned. area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 37124 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-19 07:00 | 2013-04-19 09:00 | 2013-04-19 23:00 | 600 | gallons | 2800 Longacre Drive Ground | Untreated Release Power Failure SSO Estimated Flow Released 600 Gallons. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that a power outage at the Blossom Lane Lift Station was the source of the release. Utility crews restored power to station release eliminated. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 37127 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-24 12:30 | 2013-04-24 13:15 | 2013-04-25 12:00 | 135 | gallons | 4314 E Oak Street Private Property Cleanout Ground | Untreated Release Equipment Failure SSO Estimated Flow Released 135 Gallons. Crew responded to report of cleanout releasing wastewater. Upon investigation it was determined that roots and rags in the main sewer were the source of the release. Crew cleaned main sewer to remove obstructions. release eliminated. | Affected area cleaned. Utility to televise sewer to ensure that line is free and clear of obstructions. Corrective actions dependent upon findings. Cleanout will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 37139 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-29 | 2013-04-29 11:00 | 2013-04-30 10:40 | 4000 | gallons | 4430 Lynch Road Manhole Ground | Untreated Release Equipment Failure SSO Estimated Flow Released 4000 Gallons. Maintenance crew observed that manhole cover was displaced and immediate area showed evidence that manhole had released. | Manhole cover reinstalled and affected area cleaned. Utility to televise sewer to ensure that line if free and clear of obstructions. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 36574 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-04-29 00:01 | 2013-04-29 11:00 | 2013-04-30 10:40 | 0 |  | 4430 Lynch Road Manhole Ground | Untreated Release Equipment Failure SSO Estimated Flow Released: 4000 Gallons. Maintenance crew observed that manhole cover was displaced and immediate area showed evidence that manhole had released. | Manhole cover reinstalled and affected area cleaned. Utility to televised sewer to ensure that line is free and clear of obstructions. Corrective actions dependent upon findings. area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 36600 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-05-05 17:50 | 2013-05-05 23:20 | 2013-05-06 22:00 | 250 | gallons | 4219 Derby Lane Basement Floor Drain | Untreated Release Equipment Failure Estimated SSO Property Backup Release 250 gallons. Crew responded to report of a wastewater release in basement. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstruction release eliminated. | Affected area cleaned by homeowner. Sewer will be televised to determine source of obstruction. Corrective actions dependent upon findings. Homeowner informed of backflow prevention requirements. area will be visually monitored for 72 hours. | SSO Basement Backup
12329 | 37000 | IN0033073 East | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-05-16 14:00 | 2013-05-16 14:45 | 2013-05-17 10:35 | 30 | gallons | 1113 S Grand Avenue Private Property Cleanout Ground. | Untreated Release Equipment Failure CSSR Estimated Flow Released 30 Gallons. Crew responded to request for service. upon investigation it was determined that the lateral connection was obstructed. Construction crew replaced section of obstructed lateral release eliminated. | Affected area cleaned. Utility replaced section of obstructed lateral. Area will be visually monitored for 72 hours. | SSO Affected Private Property
12329 | 40719 | IN0033073 Outfall 003 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-02 17:00 | 2013-10-02 17:30 | 2013-10-03 09:45 | 0 |  | 532 Runnymeade Avenue Floor Drain House Lateral | Rain 2.85 inches Exceeded Max Capacity Crew responded to report of wastewater releasing from basement floor drain. Upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Basement Backup
12329 | 40708 | IN0033073 Outfall 003 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-02 19:15 | 2013-10-02 21:15 | 2013-10-03 09:45 | 0 |  | 1475 E Diamond Ave Manhole | Rain 2.85 inches Exceeded Max Capacity Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 40706 | IN0033073 Outfall 003 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-02 19:15 | 2013-10-02 21:15 | 2013-10-03 09:45 | 0 |  | 1475 E Diamond Avenue Manhole | Rain 2.85 inches Exceeded Max Capacity. Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 40703 | IN0033073 Outfall 003 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-02 22:15 | 2013-10-02 23:00 | 2013-10-03 09:45 | 0 |  | 430 Washington Avenue Basement Floor | Rain 2.85 inches Exceeded Max Capacity Crew responded to report of wastewater releasing i basement. Upon investigation it was determined that the combined collection system was hydraulically maximized. | See Report | SSO Basement Backup
12329 | 40701 | IN0033073 Outfall 003 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-10-06 11:26 | 2013-10-06 05:30 | 2013-10-06 21:45 | 0 |  | 1475 E Diamond Avenue Manhole | Rain 3.21 inches Exceeded Max Capacity Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that the combined collection system was hydraulically maximized. | Affected area cleaned. Area will be visually monitored for 72 hours. | SSO Reached Public Land; SSO Reached Receiving Water | Pigeon Creek
12329 | 42564 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-17 15:55 | 2013-12-17 17:10 | 2013-12-19 08:58 | 0 |  | 206 S Royal Avenue Manhole | Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Removed Blockage See Report | SSO Reached Public Land; SSO Reached Receiving Water
12329 | 42953 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 19:00 | 2013-12-22 06:00 | 2013-12-21 21:05 | 6600 | gallons | 2171 Shelby Avenue | Equipment Failure rain 6.27 inches Crew responded to report of wastewater releasing from manhole. Upon investigation it was determined that root infiltration in the main sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | See Report | SSO Affected Private Property; SSO Reached Receiving Water | Eagle Creek
12329 | 42955 | IN0033073 Outfall 103 | Evansville Waste Water Treatment Plant Eastside | Vanderburgh | 2013-12-21 21:30 | 2013-12-22 | 2013-12-21 21:05 | 100 | gallons | 1817 Van Bibber Avenue Basement Floor | Equipment Failure Rain 6.27 inches Crew responded to report of wastewater releasing in basement. Upon investigation it was determined that root infiltration in the main sewer was the cause of the release. Crew cleaned main sewer to remove root obstruction release eliminated. | See Report | SSO Basement Backup
11292 | 42562 | IN00362956 Outfall 123 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-12-14 04:30 | 2013-12-14 07:15 | 2013-12-14 15:30 | 0 |  | 2424 Schutte Road Manhole | Utility responded to high wet well alarm at Schutte Road Lift Station. Upon investigation it was determined that a pump float failure was preventing the lift station from operating. Contractor repaired pump float controller release eliminated. | Repaired Pump Station See Report | SSO Affected Private Property; SSO Reached Receiving Water
11292 | 39296 | IN032956 | Evansville Westside Waste Water Treatment Plant | Vanderburgh | 2013-07-26 10:50 | 2013-07-26 13:20 | 2013-07-26 17:45 | 0 |  | 4202 Norwich Place Manhole | Equipment Failure Crew responded to report of manhole releasing wastewater. Upon investigation it was determined that the main sewer was obstructed. Crew cleaned main sewer to remove obstructions release eliminated. | Affected area cleaned. Sewer main will be televised to ensure that obstructions were removed. Corrective actions dependent upon findings. Area will be visually monitored for 72 hours. | SSO Affected Private Property
14546 | 35416 | IN0003506 | Newport Chemical Depot | Vermillion | 2013-04-11 09:45 | 2013-04-15 01:20 | 2013-04-16 | 0 |  | Bypass around Secondary Settling Tank Outfall 001 Wabash River | Bypass of a Treatment Process Equipment Failure The Newport Chemical Depot Reuse Authority (NeCDRA) Wastewater Treatment plant developed and equipment failure in the Secondary Settling Tank. The chains and flights were out-of-alignment in turn not allowing the flights to rake settled sludge to be recycled to the Secondary Aeration Basin. Replacement parts were acquired on 4/15/13 and the Secondary Settling Tank was repaired. | To minimize violation of final effluent parameter limits the bypass was planned during low flow conditions. To prevent recurrence of a bypass for the Secondary Settling Basin for chains and fights the Secondary Settling Basin was cleaned and unneeded barriers which was constructed of wood was removed. | SSO Reached Receiving Water | Wabash River
14546 | 35843 | IN0003506 | Newport Chemical Depot | Vermillion | 2013-04-18 19:22 | 2013-04-18 15:45 | 2013-04-23 20:30 | 0 |  | Bypass around Secondary Settling Tank Outfall 001-Wabash River | Bypass of a Treatment Process Equipment Failure The Newport Chemical Depot Reuse Authority (NeCDRA) Wastewater Treatment Plant conducted and anticipated bypass of the Secondary Settling Tank as a continuation of the anticipated bypass from 4/11/2013 to 4/15/2013 in 4/18/13. The root cause of the chain-and -flight system was that a bushing on the East end of the top south-end shaft had seized onto the shaft. | The seized bushing on the shaft was heated to relax the shaft. Also lubricate was applied to all bushings. which support all shafts in the Secondary Settling Tank. The existing drive chain was replaced with a new chain. The Secondary Settling Tank appears to be functioning normally. Another issue was identified however with gaskets failing on the telescopic valves. A follow-up anticipated bypass must be preformed at a later date to replace gasketing as part of the telescopic valves. | SSO Reached Receiving Water | Wabash River
105695 | 36838 | IN0063843 | Dana Waste Water Treatment Plant | Vermillion | 2013-04-19 09:00 | 2013-04-19 10:00 | 2013-05-13 09:06 | 0 |  | UV Effluent Chamber WWTP Facility Grounds. | Equipment Failure Rain 3.5 inches Infiltration of collection system do to rainfall. | Excess capacity released from plant Town board looking into having collection system smoke tested. | SSO Occurred at Treatment Plant
105695 | 36836 | IN0063843 | Dana Waste Water Treatment Plant | Vermillion | 2013-05-07 13:00 |  | 2013-05-13 09:06 | 0 |  | UV Effluent Chamber WWTP Facility Grounds. | Equipment Failure Rain 9 inches High flow do to rain fall and clogging of clarifier inlet pipes. | Excess capacity release from facility Increase cleaning of clarifier meters pipes remodel baffle on inlet pipe into clarifier. | SSO Affected Private Property
105695 | 38021 | IN0063843 | Dana Waste Water Treatment Plant | Vermillion | 2013-06-26 07:40 | 2013-06-26 08:00 | 2013-06-26 09:00 | 0 |  | UV Effluent Chamber | Equipment Failure Pipe Failure Treatment Bypassed. Bypass occurred do to the unplugging of the clarifier inlet pipes. | Will unplug clarifier inlet pipes every other day instead of just on Mondays and Fridays as I started doing after the last occurrence. Looking into removing baffles over inlet pipes in clarifier or just extending them higher above the inlet pipes. | SSO Occurred at Treatment Plant
12048 | 35537 | IN0025607 | Terre Haute Waste Water Treatment Plant | Vigo | 2013-01-13 06:24 | 2013-01-13 22:37 | 2013-01-14 13:38 | 1800000 | gallons | Terre Haute Wastewater Utility Primary Sedimentation Tanks to Final Contact Tank | Precipitation event caused bypass of a treatment stage and partially treated release from the Primary Sedimentation Tanks to the Final Contact Tank within WWTP | We are presently undergoing our Phase II plant upgrades to increase plant capacity. Will be completed in three years. | SSO Occurred at Treatment Plant
12048 | 34744 | IN0025607 | Terre Haute Waste Water Treatment Plant | Vigo | 2013-02-25 19:47 | 2013-02-26 04:50 | 2013-02-27 09:29 | 3100000 | gallons | Primary Sedimentation Tanks | A rain event which exceeded the capacity of the plant causing a bypass of a Treatment Process resulting in a Partially Treated Release that was Blended with the Final Effluent and Sampled. | Heavy rain caused more flow than the plant could handle. Undergoing Phase II plant upgrades to increase plant capacity. To be completed in 2016. | SSO Occurred at Treatment Plant
12048 | 35171 | IN0025607 | Terre Haute Waste Water Treatment Plant | Vigo | 2013-03-28 10:43 | 2013-03-28 11:15 | 2013-03-28 14:41 | 2000 | gallons | Glenn North Lift Station wet well manhole Ground | Untreated Release Power Failure Equipment Failure PLC control fuse that controlled the auto side of pumps blew. | Maintenance crew was able to pump the station down on hand and replaced the fuse and limed the ground where overflow occurred. | SSO Affected Private Property
12048 | 36410 | IN0025607 | Terre Haute Waste Water Treatment Plant | Vigo | 2013-04-19 00:50 | 2013-04-20 05:50 | 2013-04-22 13:41 | 15100 | gallons | Primary Sedimentation Tanks Final Contact Tank | Power Failure Rain 4.9 inches We had 4.9 inches of rain from 4/16 through 4.20 and the plant could not handle all the flow without flooding the Primary Sedimentation Tanks. | Filled our equalization basin handled as much flow as we could shut bypass as soon as plant could handle flow. We are presently in our Phase II construction of plant which will increase our capacity to handle the added flow. Is slotted for completion in 2015 | SSO Occurred at Treatment Plant
12048 | 36721 | IN0025607 | Terre Haute Waste Water Treatment Plant | Vigo | 2013-04-24 03:00 | 2013-04-25 15:00 | 2013-04-30 10:12 | 0 |  | Bypass from Primary Sedimentation Tanks to Final Contact Tank. | Flow from precipitation event exceeded plant capacity resulting in treatment bypass to final effluent. Recombined and sampled prior to discharge. | Filled equalization basins handled as much flow as we could. Shut down bypass as son as plant could handle the flow.We are presently in our Phase II construction of plany which will increase our capacity to handle the added flow. Completion slotted in 2015.
12048 | 36765 | IN0025607 | Terre Haute Waste Water Treatment Plant | Vigo | 2013-04-24 03:00 | 2013-04-25 15:00 | 2013-05-03 11:35 | 17800000 | gallons | Terre Haute WWTP | Flow caused by precipitation event(s) exceeded the capacity of the WWTP resulting in bypass of a treatment process and partially treated release that was blended with final effluent. Bypass from Primary Sedimentation Tanks to Final Contact Tank. | Original report sent 4/30/13. Resent on 5/3/13. Filled Equalization Basins handled as much flow as possible without flooding Primary Sedimentation Tanks. Shut down bypass as soon as the plant could handle the flow.We are presently in our Phase II construction of plant which will increase our capacity to handle the added flow. It is slotted for completion in 2015. | SSO Occurred at Treatment Plant
12048 | 38240 | IN0025607 | Terre Haute Waste Water Treatment Plant | Vigo | 2013-06-27 08:15 | 2013-06-27 13:07 | 2013-07-02 09:28 | 0 |  | Southside Lift Station #30 4201 S Longyear Place | Power Failure Rain 3.8 inches. We received 3.8 inches of rain on the 26th and the #2 pump tripped out in the lift station and the station backed up and flooded the building and out onto the ground. pump was checked out and reset ground was cleaned up and limed. | The #2 pump tripped out. We did not find a definite reason for the pump failure. We had a tremendous amount to rain the day before with lightning and may have had a power serge. The ground around out lift station was vactored up and lime applied. | SSO Affected Private Property
12048 | 43658 | IN0025607 Outfall 001 (Incorrect Lat/Long) | Terre Haute Waste Water Treatment Plant | Vigo | 2013-12-22 14:30 | 2013-01-22 14:40 | 2013-12-26 11:41 | 300 | gallons | Youngstown lift Station | Power Failure Rain 2.4 inches Liftstation float Bad | Repaired Pump Station | SSO Affected Private Property
12048 | 43652 | IN0025607 Outfall 001 (Bad Lat/Long) | Terre Haute Waste Water Treatment Plant | Vigo | 2013-12-21 23:30 | 2013-12-22 | 2013-12-26 11:26 | 200 | gallons | 5518Ernest St Riley In | Exceeded max Capacity Rain 2.4 inches High flow station would not keep up. Called in vac trucks to haul loads out of station to help the station and to clean up overflow off of ground. | See Report | SSO Affected Private Property
56353 | 36414 | IN0055085 | WEST TERRE HAUTE WASTE WATER TREATMENT PLANT | Vigo | 2013-04-22 09:10 |  | 2013-04-22 13:41 | 0 |  | 4 Manholes between Ferris and Ratcliff and three eastward on Ratcliff toward plant. Ground | Untreated Release We received .68 of rain on 4/11 1.6 4/16 .10 4/17 2/30 4/18 44 4/19. We have also received reports that two reservoir s have opened their flood gates to relieve the pressure on the dam. This added flow has raised the Wabash River to a level of 28 feet which is cresting today. The town of West Terre Haute floods due to seep water in the South end as well as parts of the North end. Everyone who is effected by this flooding is doing everything to relieve themselves of the water by pumping basements out into their cleanouts. The flood waters are getting into manholes and overloading the system which is backing up and causing water to flow out of these manhole listed above. The main lift is pumping but is not designed to handle the added influent infiltration. The flood waters are coming up to serious heights inside the plant. We may be looking at the water breaching our plants Final Contact Tank. | There is NO Way to stop what is happening due to Nature itself and act that we have no control over. We will continue to try and run the plant to the best of our abilities. Pray the flooding goes not occur. | SSO Occurred at Treatment Plant
53888 | 36517 | IN0020362 | NORTH MANCHESTER WASTE WATER TREATMENT PLANT | Wabash | 2013-04-19 10:00 | 2013-04-20 01:00 | 2013-04-19 18:25 | 200000 | gallons | Manhole outside plant gate. | Precipitation event(s) resulted in flooding receiving waters that prevented outflow from the WWTP. UV plant overflowed into electronics. Untreated release and treatment bypass resulted. | Shut down UV system and removed bulbs to prevent loss of system. System will be restored once inspected and fitness determined. | SSO Reached Receiving Water | Eel River
53888 | 39804 | IN0020362 | NORTH MANCHESTER WASTE WATER TREATMENT PLANT | Wabash | 2013-08-22 04:00 | 2013-08-22 04:30 | 2013-08-22 03:59 | 0 |  | 712 Ruse ST | Pipe Failure Basement Backup | Removed Blockage See Report | SSO Basement Backup
53888 | 39912 | IN0020362 Outfall 101 | NORTH MANCHESTER WASTE WATER TREATMENT PLANT | Wabash | 2013-11-08 05:00 | 2013-11-08 07:30 | 2013-11-08 15:11 | 0 |  | 9661 Coverdale Rd D43 006 | Operator left clarifier off floating sludge was carried out to river. | See Report | SSO Reached Receiving Water | Eel River
55472 | 36521 | IN0061298 | WHITES RESIDENTIAL & FAMILY SERVICES | Wabash | 2013-04-19 07:00 | 2013-04-19 11:30 | 2013-04-19 18:36 | 1000 | gallons | Corner of lagoon | Precipitation event(s) caused flooding of the normal receiving waters preventing full outflow. The pipe from the primary pond to the secondary pond could not transfer water quickly enough to prevent untreated and partially treated release to the surrounding ground. | Once overflow stopped limed area where discharge took place. Will build up low corner of the primary lagoon to prevent future occurrences. | SSO Affected Private Property
55472 | 36277 | IN0061298 | WHITES RESIDENTIAL & FAMILY SERVICES | Wabash | 2013-04-20 07:00 | 2013-04-22 10:00 | 2013-04-24 15:07 | 7000 | gallons | Corner of Lagoon Ground | Partially Treated Release Rain 3.50 inches Primary lagoon continue to seep off and on over corner wall of lagoon. Pipe from primary to secondary lagoon reported at 50000 per day flow. | Workers installed pump on 4-22-13 and transferred it to secondary lagoon discharge stopped leaking. Continuing to pump to make more room. Inquiring about an overflow pipe to transfer water if ponds get high in the future. | SSO Affected Private Property
55472 | 39441 | IN0061298 | WHITES RESIDENTIAL & FAMILY SERVICES | Wabash | 2013-07-10 14:00 | 2013-07-10 16:00 | 2013-07-21 10:12 | 0 |  | Influent Manhole | Rain 2.5 inches Discharge to grass over on private property of White s Residential. | See Report | SSO Affected Private Property
59585 | 38608 | IN0020435 | CHANDLER MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-06-18 07:00 | 2013-06-18 09:30 | 2013-06-20 09:00 | 0 |  | MH #7-287 Yard/Easement | Sewer main stopped up by pea gravel from an unknown source. May be construction from years past. | Jetted pressure washed and manually removed couple cu.yds. Ran camera through nearby mains looking for source. | SSO Affected Private Property
59585 | 38888 | IN0020435 | CHANDLER MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-06-24 01:10 | 2013-06-24 02:15 | 2013-06-26 07:00 | 0 |  | MH - #7 - 198 | Lift Station #7 hydraulically overloaded | See Report | SSO Reached Receiving Water
59585 | 38890 | IN0020435 | CHANDLER MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-06-24 09:37 | 2013-06-24 09:37 | 2013-07-31 09:39 | 0 |  | MH #108 | Sewer mains hydraulically overloaded. Manhole lid was bouncing. | See Report | SSO Affected Private Property
59585 | 43665 | IN0020435 | CHANDLER MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-12-21 10:30 | 2013-12-21 11:30 | 2013-12-23 11:15 | 0 |  | Manhole #7-198 | Rain 4.06 inches Overflow/Bypass (tickle from lid) was observed by collection tech. | See Report | SSO Reached Receiving Water
59585 | 43098 | IN0020435 Outfall 001 | CHANDLER MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-12-21 10:30 | 2013-12-21 11:30 | 2013-12-23 | 0 |  | Manhole #7-198 | Rain 4.06 inches Overflow/Bypass (trickle from lid) was observed by collection tech. | See Report | SSO Reached Receiving Water
59575 | 34625 | IN0020788 | ELBERFELD MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-03-08 02:29 | 2013-03-08 02:41 | 2013-03-08 05:52 | 0 |  | Bluebell Lift station Storm Ditch | Untreated Release Equipment Failure | Clean and Spread AG Lime Pump failed. Called electrician and repaired pump. | SSO Affected Private Property
| 34626 | IN0020788 |  | Warrick | 2013-03-08 10:21 | 2013-03-08 02:25 | 2013-03-08 05:50 | 0 |  | Nobles chapal Lif Station | Untreated Release Equipment Failure | Clean and Spread AG Lime Fixed electrical malfunction. | SSO Reached Public Land
59575 | 43662 | IN0020788 | ELBERFELD MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-12-21 06:12 | 2013-12-21 08:48 | 2013-12-22 11:58 | 0 |  | Manhole 11511 Sevenhills Rd | We had 2.1 inches of rain the night of 12/20/2013 and 3.1 inches of rain on 12/21/2013 | Clean and spread Ag lime | SSO Affected Private Property
59811 | 36736 | IN0022420 | BOONVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-04-30 | 2013-04-30 16:00 | 2013-05-01 15:11 | 250 | gallons | Manhole at Shawnee Lift Station | Grease blockage in gravity sewer line resulted in back up and overflow of untreated release to surrounding ground. | Hydro-Max jetted line and cleaned up affected area. Lime also spread on affected area.Line to be added to quarterly cleaning. | SSO Reached Public Land
13755 | 34602 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-03-06 12:12 | 2013-03-06 12:45 | 2013-03-07 10:37 | 60 | gallons | Clean-out @ 8887 High Point Drive Ground | Untreated Release Line Blockage. A grease Clog caused the overflow. | The line was immediately jet cleaned. Standing sewage in the area of the overflow was vacuumed into a tank truck and placed back into the collection system. | SSO Affected Private Property
13755 | 35357 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-03-06 12:12 | 2013-03-06 12:45 | 2013-03-07 10:40 | 60 | gallons | Clean-out at 8887 High Point Drive | Untreated Release - A grease clog caused the overflow. | The line was immediately jet cleaned. Standing sewage in the area of the overflow was vacuumed into a tank truck and placed back into the collection system. The main lines in area of the grease clog will be TV inspected to trace the source of the grease and the source will be eliminated via enforcement of the FOG Ordinance. | SSO Affected Private Property
13755 | 37871 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-06-12 14:00 | 2013-06-12 14:20 | 2013-06-13 10:21 | 500 | gallons | Air Release Valve No. 8 on Lift Station No. 2 Relief Force Main station No 78 +12 | Equipment Failure Force Air Release Valve. Staff was performing maintenance on the release valve when the isolation valve broke creating the overflow. | Sewage in the air release manhole was pumped to a tank and transported to the WWTP. The defective valve was replaced immediately. No other action is planned. | SSO Affected Private Property
13755 | 38606 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-06-17 08:45 | 2013-06-17 10:00 | 2013-06-17 14:25 | 50 | gallons | 7322 Lenn Lane Manhole #15140 | Equipment Failure Manhole. The staff discovered that the sanitary sewer pipe penetration of Manhole No 15-140 had developed a small leak. The leak was immediately grouted and sealed. | The staff grouted the pipe penetration of the manhole base. The manhole base is in poor condition. The staff will obtain and pursue at corrective action plan from our engineers. | SSO Reached Receiving Water | Summer Pecka Ditch
13755 | 38740 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-06-24 13:57 | 2013-06-24 13:58 | 2013-06-25 09:40 | 500 | gallons | WWTP Headworks Overflow. | Equipment Failure. During an extreme storm event which generated extremely high flows at the WWTP the computer controlled SBR influent gates were slightly out of syncronization. At the end of the fill cycle of SBR 5 the influent gate closed faster than SBR 7 s (the next SBR in series) gate opened. This generated a 20 second overflow at the WWTP headworks. | Staff was positioned on the SBR tanks at the time of the incident surveying for problems during the extreme storm event. The staff immediately recognized the problem and began to open the influent gate to SBR 6 to relieve the flow until SBR 7 s gate was fully open (i.e. SBR 6 was in standby mode at the time). These gates require approximately 3 minutes to open or close and synchronization is critical at an extreme flow of 23.6 MGD. The staff will have the Aqua Aerobics (the SBR vendor) software programmers investigate the influent gate synchronization in the control program and if problems are found the program will be modified.
13755 | 38873 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-06-24 13:57 | 2013-06-24 13:58 | 2013-06-25 09:40 | 0 |  | WWTP Headworks | During and extreme storm event which generated extremely high flows at the WWTP the computer controlled SBR influent gates were slightly out of synchronization. At the end of the fill cycle of SBR5 the influent gate closed faster than SBR 7 s (the next SBR in series) gate opened. This generated a 20 second overflow at the WWTP headwork. | See Incident Report | SSO Occurred at Treatment Plant
13755 | 38741 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-06-29 11:45 | 2013-06-29 13:00 | 2013-07-25 14:46 | 100 | gallons | 3755 S Venetian Dr. ITT Lift station force main air release valve. | Equipment Failure. A pivot pin inside the air release valve broke causing the release of wastewater at ITT lift station | Spilled & pooled sewage was vacuumed into a tank truck and taken to the WWTP for disposal. The storm retention basin was posted with E. coli contamination warning signs. The water in the retention basin will be tested for E. coli and the warning signs will remain until the E. coli level is safe. The ITT lift station air release valves are inspected on a 2 month schedule and were last inspected on 6-3-2013. No problems were found at that time. We will continue periodic inspection of the air release valves. | SSO Affected Private Property; SSO Reached Receiving Water
13755 | 39185 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-06-29 11:45 | 2013-06-29 13:00 | 2013-06-29 17:01 | 0 |  | ITT Lift Station force main air release valve 3755 S Venetian Dr. | Equipment Failure. A pivot pin inside the air release valve broke causing the release of wastewater.. | See Report | SSO Affected Private Property
13755 | 39442 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-07-21 21:55 | 2013-07-21 22:20 | 2013-07-22 13:26 | 0 |  | Manhole No 23-120 2422 Briar Cliff Dr. | While 1.92 inches was the total rain fall received at the WWTP in a 3 hour period the maximum rain fall intensity hit 6.40 inches/hour. This generated localized flooding and a number of manholes in the Blue Lake subdivision went under water. This resulted in a hydraulic overload of the Blue Lake Lift Station which resulted in the overflow. | See Report | SSO Affected Private Property; SSO Reached Receiving Water
13755 | 39465 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-07-22 13:30 | 2013-07-22 14:45 | 2013-07-23 08:46 | 0 |  | ITT Lift Station Force Main 100 Epworth Crossing | Construction Related Pipe Failure. A contractor working for the St Mary s Health System at their St Mary s Epworth Crossing development excavated hit and broke the ITT lift station s force main. This in a release of sewage. The contractor did not request utility location marking prior to excavating. | See Report | SSO Reached Receiving Water
13755 | 39805 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-07-23 14:15 | 2013-07-23 14:45 | 2013-07-24 09:20 | 0 |  | Victoria Lift Station Force Main 200 Ft south of Vann Rd along Wethers Rd | Pipe Failure A defective pipe caused the sewage release. Upon excavation of the 12-inch force main a 10-inch longitudal split was discovered. The defective pipe was immediately replaced. | Repaired Pipe See Report | SSO Affected Private Property
13755 | 39591 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-07-23 14:15 | 2013-07-23 14:45 | 2013-07-24 09:20 | 0 |  | Victoria Lift Station Force Main 200 ft south of Vann Rd along Wethers Rd | Equipment Failure A defective pipe caused the sewage release. Upon excavation of the 12 in force main a 10 inch longitudal split was discovered. The defective pipe was immediately replaced | Repaired Pipe See Report | SSO Affected Private Property
13755 | 39600 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-07-24 13:50 | 2013-07-24 14:15 | 2013-07-25 10:30 | 0 |  | Manhole No 13-156 6766 Old Stone House Drive | Equipment Failure A root clog i the 8 inch main caused the overflow. The sewage spilled onto the ground and did not reach a ditch stream or other body of water. | Removed Blockage | SSO Affected Private Property
13755 | 39806 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-07-24 13:50 | 2013-07-24 14:15 | 2013-07-25 10:35 | 0 |  | Manhole No 13-156 6766 old Stone House Drive | A root clog in the 8 - inch main caused the overflow. The sewage spilled into the ground and did not reach a ditch stream or other body of water. | Removed Blockage See Report | SSO Affected Private Property
13755 | 39930 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-08-29 16:53 | 2013-08-29 19:05 | 2013-08-30 08:24 | 0 |  | Manhole No 14-209 5488 East Esche Dr. | A root clog in a 10- inch main caused the overflow. | Removed Blockage See Report | SSO Affected Private Property; SSO Reached Receiving Water
13755 | 41753 | IN0023892 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-11-08 17:10 | 2013-11-08 18:00 | 2013-11-12 14:24 | 0 |  | 8800 Hickory Ln Halston Force Main | Equipment Failure Approx 3 foot split in 6 force main | Repaired Pipe | SSO Affected Private Property
13755 | 41142 | IN0023892 Outfall 001 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-09-30 16:05 | 2013-09-29 09:06 | 2013-10-13 13:20 | 0 |  | Basement drains and sinks at 5199 and 5177 East Timberwood | Rain 0.52 inches Equipment Failure On the afternoon of 9-23-13 at the time of the sewage backup into the basement the home owners called in a plumber to address the problem. They did not contact the Newburgh Sewer Department. Apparently the plumber began to use a cable machine to clear the lateral lines when the backup abated. On 9-30-13 at 4:05pm the plumber contacted the Newburg Sewer department and informed the staff of the backups that ha occurred on the 29th. A jet truck was immediately dispatched to the site and the sanitary sewer main was jet cleaned with a hydraulic root cutter. A root obstruction was removed from the line 15 feet up-stream of manhole number 15-40. | Removed Blockage See Report | SSO Basement Backup
13755 | 43666 | IN0023892 Outfall 001 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-12-28 10:00 | 2013-12-28 10:20 | 2013-12-28 11:47 | 1000 | gallons | MH- 11_230 8100 outer Lincoln Ave | Equipment Failure pipe was plugged between 11-230 and 11-232. | Equipment failure Pipe was plugged between 11-230 and 11-232. | SSO Affected Private Property
13755 | 40660 | IN0023892 Outfall 001 | Newburgh Municipal Sewage Treatment Plant | Warrick | 2013-09-29 16:05 | 2013-09-29 13:52 | 2013-10-01 13:20 | 0 |  | Basement drains and sinks at 5199 and 5177 East Timberwood | Rain 0.52 inchesEquipment Failure On the afternoon of 9-29-13 at the time of the sewage backup into the basements the home owners called in a plumber to address the problem. They did not contact the Newburgh Sewer Department. Apparently the plumber began to use a cable machine to clear the lateral lines when the backups abated. On 9-30-13 at 4:05pm the plumber contacted the Newburgh Sewer Department and informed the staff of the backups that had occurred on the 29th. A jet truck was immediately dispatched to the site and the sanitary sewer main was jet cleaned with a hydraulic root cutter. A root obstruction was removed from the line 15 feet up-stream of manhole number 15-40. | Removed Blockage See Report | SSO Basement Backup
59770 | 37365 | IN0040282 | LYNNVILLE MUNICIPAL WASTE WATER TREATMENT PLANT | Warrick | 2013-05-03 | 2013-06-04 13:30 | 2013-06-04 01:09 | 0 |  | Man hole south of Hwy 61 and Hwy 68 intersection on the south east corner Ground | Untreated Release Equipment Failure. Grease blockage seems to be the cause. | Owner notified and asked to re-double efforts to keep grease trap operational. We will watch the manhole and open and inspect monthly.
59769 | 34912 | IN0021059 | NEW PEKIN MUNICIPAL WASTE WATER TREATMENT PLANT | Washington | 2013-03-18 06:00 | 2013-03-18 14:30 | 2013-03-19 12:37 | 50000 | gallons | Lift Station | Lift Station Rain and snow on saturated ground river out of it banks. |  | SSO Reached Receiving Water | Blue River
59769 | 38929 | IN0021059 | NEW PEKIN MUNICIPAL WASTE WATER TREATMENT PLANT | Washington | 2013-06-26 16:00 | 2013-06-27 06:30 | 2013-06-26 09:26 | 0 |  | Lift Station | Rain 6 inches Exceeded Max Capacity. Heavy rain on saturated ground 10 since 6-24-13 minor flash flooding. | See Report | SSO Reached Receiving Water | Blue River
59769 | 43669 | IN0021059 Outfall 001 | NEW PEKIN MUNICIPAL WASTE WATER TREATMENT PLANT | Washington | 2013-12-21 12:00 | 2013-12-22 06:00 | 2013-12-23 03:04 | 150000 | gallons | Lift station Charles ST | Rain 4 inches Exceeded Max Capacity 3-4 inches rain or saturated ground minor flooding. | See Report | SSO Reached Receiving Water | Blue River
59768 | 34851 | IN0021644 | SALEM MUNICIPAL WASTE WATER TREATMENT PLANT | Washington | 2013-02-17 | 2013-02-17 13:00 | 2013-02-18 08:08 | 20000 | gallons | Manhole 507A Salem IN | County sewer main clog triggered untreated release from manhole. | Cleaned sewer with Jetter. Cleaned paper and flotsam around overflow area. Treated area around manhole with hydrated lime. | SSO Reached Public Land; Surface Soil
59768 | 42013 | IN0021644 | SALEM MUNICIPAL WASTE WATER TREATMENT PLANT | Washington | 2013-11-18 05:00 | 2013-11-18 06:40 | 2013-11-18 12:34 | 0 |  | Aeration Bays Stream | Partially Treated Release No aquatic damage observed. | See Report
60488 | 39079 | IN0022489 | CAMPBELLSBURG WATER WORKS | Washington | 2013-06-26 16:00 |  | 2013-06-26 17:47 | 0 |  | Manhole | See Report | See Report | SSO Affected Private Property
55380 | 43670 | IN0040029 Outfall 010 | FOUNTAIN CITY MUNICIPAL WASTE WATER TREATMENT PLANT | Wayne | 2013-12-21 21:30 | 2013-12-21 23:55 | 2020-12-22 13:03 | 18000 | gallons | Liftstation a SSO #005 Park on US 27 | Exceeded Max Capacity Rain 5.4 We had 6 inches of snow and ice on the ground then we got 5.4 inches of rain in about 36 Hrs we had flooding around town that overloaded liftstation. | See Report | SSO Reached Receiving Water | Nolands Fork
55221 | 35077 | IN0020010 | HAGERSTOWN MUNICIPAL WASTE WATER TREATMENT PLANT SITE A | Wayne | 2013-02-02 08:00 | 2013-02-02 10:00 | 2013-02-02 11:15 | 0 |  | 202 North Elm Street Hagerstown IN | Basement back up through washing machine drain. | Jetted the line. | SSO Basement Backup
55221 | 40033 | IN0020010 | HAGERSTOWN MUNICIPAL WASTE WATER TREATMENT PLANT SITE A | Wayne | 2013-09-04 14:30 | 2013-09-04 17:30 | 2013-09-04 17:02 | 0 |  | 619 Teetor St Hagerstown IN | Forced main was blocked causing sewer to flow into the home of the address at 619 Teetor St. We dug up two locations to jet and vac the lines to open the obstruction. The first was on Teetor St and the second was on Paul R Foulke Way Dr (Industrial Parkway). We have closed these back up and believe to have taken care of this problem. | Removed Repaired Pipe See Report | SSO Basement Backup
55221 | 40034 | IN0020010 | HAGERSTOWN MUNICIPAL WASTE WATER TREATMENT PLANT SITE A | Wayne | 2013-09-04 20:30 | 2013-09-06 16:00 | 2013-09-04 17:02 | 0 |  | Teetor & Industries Pkwy Hagerstown In | Forced main was blocked causing sewer to flow into the home of the address at 619 Teetoe St. We dug up two locations to jet and vac the lines to open the obstruction. The first was on Teetor St and the second was on Paul R Faulke Way Dr (Industrial Parkway). We have closed these back up and believe to have taken care of this problem. | Removed Blockage Repaired Pipe See Report | SSO Basement Backup
55293 | 35502 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-01-11 15:30 |  | 2013-01-14 13:11 | 0 |  | Manhole 143-068 | Precipitation event untreated release from shallow manhole to receiving waters. | Richmond Sanitary District is involved in the ongoing master plan to eliminate future events. Structural upgrading will be done. | SSO Reached Receiving Water | White River
55293 | 35771 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-01-11 15:30 | 2013-01-15 02:30 | 2013-01-15 09:47 | 0 |  | Manhole 143-068 | Untreated release from manhole as a result of precipitation event. Release area limitied to ground around manhole. | Once flow has normalized we will be checking downstream for any blockage/obstruction. To this time none have been discovered. | SSO Reached Public Land
55293 | 35241 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-01-12 21:37 | 2013-01-13 17:00 | 2013-01-14 09:44 | 300000 | gallons | Manhole 143-102 Richmond IN | Precipitation event resulted in Untreated Release from a manhole to Receiving Waters | Richmond Sanitary District is involved in an ongoing master plan to eliminate future bypass events. | SSO Reached Public Land; SSO Reached Receiving Water | White River
55293 | 35498 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-01-12 21:37 | 2013-01-13 17:00 | 2013-01-14 13:10 | 10760 | gallons | Manhole 143-102 | Precipitation event resulted in untreated release from manhole to receiving water. | Richmond Sanitary District is involved in an ongoing master plan to eliminate future bypass events. | SSO Reached Receiving Water | White River
55293 | 35770 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-01-13 17:00 | 2013-01-13 18:00 | 2013-01-15 09:47 | 15600 | gallons | Manhole 143-102 | Untreated release reaching receiving waters due to power failure during precipitation event resulting in manhole overflow. | Power restored and pumps were able to catch up to eliminate the overflow. | SSO Reached Public Land; SSO Reached Receiving Water | Whitewater River
55293 | 34691 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-03-11 12:30 | 2013-03-11 17:30 | 2013-03-12 14:25 | 0 |  | The nearby inlet and to the White Water River | Rain .25 inches Equipment Failure Do to heavy rain fall and some roots found in the system the manhole over flowed into the river the manhole is the lowest point in system. | Richmond Sanitary Dist. is involved in a long term on going master plan to eliminate future bypass events. | SSO Reached Receiving Water | Whitewater River
55293 | 36460 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-04-16 | 2013-04-17 13:30 | 2013-04-19 15:07 | 30000 | gallons | 128-023/128-021 & 128-032 Onto the ground ran to the nearby creek than to the river. | 128-021 The lid was found to be removed and the manhole was filled with debris 128-023 area near the manhole was washed away and solids has been flushing into the creek. | Cleared the manhole from debris removed a section of sewer pipe (exposed to the elements) than removed the blockage. than the man was flushed 6 sections down stream. | SSO Reached Receiving Water
55293 | 38710 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-07-18 08:00 | 2013-07-18 09:45 | 2013-07-18 13:45 | 20000 | gallons | Manhole at State Rd 121 | Power Failure Equipment Failure Manhole 113-002 over flowed onto the grown then ran into the East For of the East Fork of the White river. | Cleared a path to the manhole in question once it dries up tan we may extrack the area and or put down some lime. As for the pump station it will be pumped down manually until the problem is solved. May put the system in an automatic mold and or monitor the station more often. The station is checked weekly. | SSO Reached Receiving Water | White River
55293 | 42616 | IN0025615 | WILLIAM EDWIN ROSS WASTE WATER TREATMENT PLANT | Wayne | 2013-12-21 23:30 |  | 2013-12-23 23:30 | 0 |  | 57 | This is a combination sewer line. To much flow for line to handle. | See Report | SSO Reached Receiving Water | White River
55224 | 37271 | IN0045667 | CLOVERLEAF RICHMOND MOBILE HOME PARK | Wayne | 2013-05-31 19:30 | 2013-05-31 19:45 | 2013-05-31 11:45 | 50 | gallons | Final Effluent field tile | Pipe Failure Overflow is essentially an after treatment effluent field tile that is either broken or frost heaved . The WWTP s final effluent is conveyed through the tile to receive creek. This overflow is at this time wet ground only and in this area the repair will be made. This incident is not a bypass and am unsure whether it is an overflow event. | Piping to be repaired Lime used for any solids. | SSO Affected Private Property
55224 | 42622 | IN0045667 Outfall 001A | CLOVERLEAF RICHMOND MOBILE HOME PARK | Wayne | 2013-12-21 16:45 | 2013-12-22 11:45 | 2013-12-22 12:00 | 0 |  | WWTP Tank overflows raw mixed liquor final | Rain 4.5 inches All systems operational pumps unable to keep up with amount of precipitation directly into exposed tanks as well as I&I | See Report | SSO Occurred at Treatment Plant
55197 | 35877 | IN0020745 | OSSIAN MUNICIPAL WASTE WATER TREATMENT PLANT | Wells | 2013-01-13 16:45 | 2013-01-13 20:00 | 2013-01-13 20:05 | 2943 | gallons | Waste Water Treatment Plant Outfall 001 | Precipitation event and snow melt caused a blended and sampled release from WWTP to receiving waters. | Filled EQ tanks. Also returning sludge at a high rate. The Town of Ossian is looking for I &I sources in town and from lift stations. | SSO Reached Receiving Water | Eightmile Creek
55197 | 35356 | IN0020745 | OSSIAN MUNICIPAL WASTE WATER TREATMENT PLANT | Wells | 2013-04-11 03:10 | 2013-04-11 14:30 | 2013-04-12 13:37 | 40000 | gallons | SSO 008 | Untreated Release - Precipitation 2.5 Inches | Filled E.Q. tanks and started airation on them as flow increased. The town of Ossian is smoke testing and televising sewer lines to look for I & I to eliminate storm water from sewer lines. | SSO Reached Receiving Water | Eightmile Creek
55197 | 35656 | IN0020745 | OSSIAN MUNICIPAL WASTE WATER TREATMENT PLANT | Wells | 2013-04-11 15:10 |  | 2013-04-11 13:28 | 40000 | gallons | SSO 008 8 Mile Creek | Untreated Release Rain 2.5 inches. | Filled E.Q. Tanks and started direction on them as flow increased. The town of Ossian is smoke testing and televising sewer lines to look for I&I to eliminate storm water from sewer lines. | SSO Reached Receiving Water | Eightmile Creek
55197 | 36923 | IN0020745 | OSSIAN MUNICIPAL WASTE WATER TREATMENT PLANT | Wells | 2013-04-18 02:00 | 2013-04-19 10:00 | 2013-04-19 10:35 | 80000 | gallons | SSO 008 8 Mile Creek | Untreated Release Rain 3.25 inches | Filled EQ Tank at Treatment Plant. The town of Ossian is looking at ways to remove I&I from the system. | SSO Reached Receiving Water | Eightmile Creek
55197 | 36272 | IN0020745 | OSSIAN MUNICIPAL WASTE WATER TREATMENT PLANT | Wells | 2013-04-18 19:00 | 2013-04-19 10:00 | 2013-04-19 10:36 | 80000 | gallons | Town of Ossian WWTP | Precipitation event resulted in untreated overflow from the EQ tanks to receiving waters. | Filled E.Q. tanks at treatement plant. Town of Ossian is looking at ways to remove I & I from the system. | SSO Reached Receiving Water | Eightmile Creek
53883 | 35864 | IN0022411 | BLUFFTON WASTE WATER TREATMENT PLANT | Wells | 2013-01-13 04:00 | 2013-01-13 06:00 | 2013-01-13 07:21 | 0 |  | Manhole at State Road 124 and Elm Grove Road | Precipitation event resulted in excessive flow and backup in line before lift station causing a small untreated release from a manhole to surrounding ground. | No actions taken. Continuing search for I & I sources. | SSO Reached Public Land
53883 | 35546 | IN0022411 | BLUFFTON WASTE WATER TREATMENT PLANT | Wells | 2013-01-15 |  | 2013-01-15 12:14 | 0 |  | Manhole on 124 One mile East of Indiana Road #1 | River flooding combined with equipment failure allowed an untreated release to receiving waters. Lid and rim came loose for barrel section of manhole allowing untreated water to seep around edges. Manhole is submerged. | Attempted to use a row boat to reach the manhole and place sand bags atop it to seal it. Must wait until river falls for repairs. | SSO Reached Receiving Water | Wabash River
53883 | 35623 | IN0022411 | BLUFFTON WASTE WATER TREATMENT PLANT | Wells | 2013-04-11 |  | 2013-04-11 13:21 | 0 |  | West of 1820 Western Ave near Lift station Ground Ditch | Untreated Release Rain 3.3 inches All lines surcharged due to large flow. | Plant totally inundated with rain and CSO Search for I&I continues. | SSO Affected Private Property
53883 | 35424 | IN0022411 | BLUFFTON WASTE WATER TREATMENT PLANT | Wells | 2013-04-12 | 2013-04-12 | 2013-04-12 11:10 | 0 |  | Manhole at 1308 South Main Bluffton IN | Untreated release from a manhole to the area around the manhole. Caused by possible blockage from factory waste. | Jetted and cleared line. | SSO Reached Public Land
53883 | 36173 | IN0022411 | BLUFFTON WASTE WATER TREATMENT PLANT | Wells | 2013-04-19 07:50 |  | 2013-04-19 06:10 | 0 |  | West of 1820 Western Avenue near lift station | Precipitation event caused untreated release fro manhole to surrounding ground and ditch. All lines surcharged due to heavy flow. Stopped one pump in lift station to see if it would relieve some of the overflow. Plant inundated with high flow from CSO. The lift station is upstream of the manhole. | Search for I & I continues. | SSO Reached Public Land
53883 | 38504 | IN0022411 | BLUFFTON WASTE WATER TREATMENT PLANT | Wells | 2013-06-17 10:00 | 2013-06-17 13:00 | 2013-06-17 13:00 | 0 |  | 1308 South Main Manhole | The line was plugged due to ice from a industry. Manhole | Additional jetting of line required.
53883 | 39190 | IN0022411 | BLUFFTON WASTE WATER TREATMENT PLANT | Wells | 2013-06-30 13:00 | 2013-06-30 13:00 | 2013-06-01 03:32 | 0 |  | 1308 S Main West of 1820 Western Ave | Rain 3.5 inches small amount | See Report | SSO Affected Private Property
55198 | 35658 | IN0020974 | BROOKSTON MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-11 07:00 | 2013-04-11 07:30 | 2013-04-11 15:22 | 500 | gallons | EQ Basin | 3 inches of Rain Equipment Failure Eq basin got full and control to shut off pump did not operate properly and some flow ran over the top of EQ Basin. | Control repaired | SSO Reached Receiving Water | Moots Creek
55198 | 36045 | IN0020974 | BROOKSTON MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-18 13:00 |  | 2013-04-18 13:55 | 500000 | gallons | Brookston Wastewater Treatment Plant | Precipitation event(s) and saturated ground has resulted in the EQ basin discharging to second clarifier and mixing with treated flow from clarifier one. Then all flow is going thru UV treatment to receiving waters. | Continuing to fight inflow and infiltration problems. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Moots Creek
55198 | 36439 | IN0020974 | BROOKSTON MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-18 13:00 | 2013-04-20 19:00 | 2013-04-22 15:19 | 1000000 | gallons | From Plant Moots Creeks | Rain 8.2 inches total for the past 10 days. EQ basin was full and discharged to second clarifier and mixed with treated flow from clarifier one and then all flow went through UV treatment. | Continuing to fight inflow infiltration | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Moots Creek
55198 | 36247 | IN0020974 | BROOKSTON MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-24 | 2013-04-24 23:59 | 2013-04-24 15:37 | 500000 | gallons | Plant Moots Creek | Rain 1.8 inch Approx 10 inches of rain in last 15 days EQ basin is full and discharging into Clarifier 2 and mixing with treated flow from clarifier one and then going thru UV treatment. | Continuing to fight inflow an infiltration. | SSO Reached Receiving Water | Moots Creek
55198 | 36618 | IN0020974 | BROOKSTON MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-24 06:30 | 2013-04-25 06:00 | 2013-04-25 13:15 | 1000000 | gallons | Brookston WWTP | Follow up to previous report. Precipitation event(s) caused EQ Basin overflow into clarifier 2 and mixing with treated flow from clarifier one and then going to UV treatement. Partially treated release. Treatment process bypass. | continuing to fight inflow and infiltration. | SSO Reached Receiving Water | Moots Creek
55198 | 42079 | IN0020974 | BROOKSTON MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-11-20 05:00 | 2013-11-20 07:30 | 2013-11-20 15:33 | 0 |  | Number 2 Clarifier RAS line plugged mixed liquor overflowed into effluent | Equipment Failure RAS line plugged. Not exactly sure of the time but left plant at 7:00pm 11-19-13 and it was fine. I estimated 5am form flow chart. Got to plant a 7:30am 11-20-13 and fixed problem immediately. | See Report | SSO Reached Receiving Water | Moots Creek
56308 | 36505 | IN0030571 | CHALMERS MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-18 17:30 | 2013-04-19 14:30 | 2013-04-19 16:18 | 81900 | gallons | Manhole #18 | Precipitation event(s) and saturated ground resulted in untreated release from manhole to farm field with no damage to the private land. | Flow going to adjacent farm field 15 feet west of manhole. Continue to search for and eliminate sources of I & I to the sewer collection system. | SSO Affected Private Property
56308 | 36451 | IN0030571 | CHALMERS MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-19 | 2013-04-20 | 2013-04-19 16:20 | 0 |  | Chalmers WWTP EQ Basin | Precipitation event(s) cause a partially treated release from the plant EQ basin through grass and slope to receiving waters. | Will keep EQ basin at the lowest possible level that will keep the rubber liner in place. EQ Basin water will be brought back through the WWTP as the flow lessens. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Spring Creek
56308 | 37209 | IN0030571 | CHALMERS MUNICIPAL WASTE WATER TREATMENT PLANT | White | 2013-04-19 | 2013-04-27 | 2013-05-10 13:09 | 100000 | gallons | Plant E.Q. Basin (Overflowed Retention Pond) Ground Spring Creek | Partially Treated Release Rain I tested E.Q Basin water overflowing toward Spring Creek - over S end basin ream- then flowed through 70 feet of grass and then down grassy 30ft slopped bank into creek. |  | SSO Affected Private Property; SSO Reached Receiving Water | Spring Creek
56316 | 34940 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-02-14 11:51 | 2013-02-14 12:20 | 2013-02-14 15:05 | 3 | gallons | 6196 N. Bedford Bay Ct. Twin Lakes In | Untreated Release caused by defective Check valve and curb stop | Shut of grinder pump and curb stop. Replaced defective check valve and curb stop. | SSO Reached Public Land
56316 | 35303 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-03-28 05:12 | 2013-03-28 07:25 | 2013-04-01 10:17 | 100 | gallons | 3923 Parses Rd Curb Stop Low Pressure Sewer Ground | Untreated Release Equipment Failure Notified at 5:12. First responder at site a 5:34 hours. Excavation of curb stop check valve assembly began at 7:25 which contained overflow in excavated pit. Sewage pumped by Godlove Septic Service at 8:30. Repair of line complete by 9:17. | Repaired defective/failed compression fitting by replacing curb stop assembly. applied lime to affected areas. No preventative measures available. Replaced failed equipment. | SSO Affected Private Property
56316 | 35552 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-04-06 20:36 | 2013-04-06 21:23 | 2013-04-07 15:17 | 50 | gallons | 5573 Stahl Rd curbstop by grinder unit ground. | Untreated Release Equipment Failure Flow stopped called Jim Overbeck also called for utility locater contractor finished. | shut pump off problem fixed. Replaced curbstop and put lime on affected area | SSO Affected Private Property
56316 | 35478 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-04-07 09:30 | 2013-04-07 13:00 | 2013-04-08 08:19 | 6000 | gallons | 5573 Sthal Dr 11/4 on main line break ground Lake Shafer | Untreated release Equipment Failure Arrived and called contractor and the Vac Truck. Contractor and Vac Truck got sewage shut off and finished hooking up. | Had vac truck to suck up sewage from line blocked at main. Truck got filled and needed dump . When they got back it had run across yard and down to Lake. Got it shut down and shut off put on. Finished hooking line up. put new shut off on saddle and limed affected area. | SSO Affected Private Property; SSO Reached Receiving Water | Lake Shafer
56316 | 37183 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-05-25 19:21 | 2013-05-25 19:25 | 2013-05-26 17:08 | 20 | gallons | 4875 Elmer Girtz Dr Discharge line Ground | Untreated Release Equipment Failure Raw pump to verify problem shut pump off to stop flow called in locates called contractor to replace fitting. Contractor on site fitting changed and corrected. | Fix fitting by replaing fitting limed affected area w/ag-lime until contractor arrives site. Replace fitting | SSO Affected Private Property
56316 | 37548 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-06-07 10:03 | 2013-06-07 10:31 | 2013-06-07 16:35 | 100 | gallons | 6655 E Palmers Dr | Equipment Failure Air relief valve failure on low pressure sewer system allowed sewage from the low-pressure sewer to escape into the valve pit. Once the valve pit was full of sewage it began to overflow into E Palmer Dr. | Contained overflow by pumping sewage directly from the valve pit into five (05) 55 Gallon drums in order to contain overflow. Contacted waste hauler and had the hauler pump the valve pit out. Closed the air-relief valve to prevent additional leakage from the air-relief valve into the valve pit until repair/replacement of faulty valve is accomplished. Equipment is new construction and will be replaced by construction contractor. Regular PM checks will be preformed to verify proper functionality once installed no PM can eliminate all potential for such equipment failure.(Follow-Up Comment 6/12/13): In addition to the actions documented in the previous report Twin Lakes RSD took the following action on 6/10/13. The air-relief valve was repaired and placed back in service. | SSO Reached Public Land; SSO Affected Private Property
56316 | 37887 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-06-21 12:45 | 2013-06-21 14:30 | 2013-06-21 18:25 | 50 | gallons | 6032 East 800 North | Equipment Failure Saddle Connection. A failure in a fused saddle connection of a discharge lateral to the low pressure sewer system (LPSS) allowed sewage from the LPSS to escape and work it s way up to ground level. The discharge was intermittent only forcing sewage up when grinders activated. | The overflow was contained by excavation to the failed saddle connection. The failed saddled connection was removed and replaced. Contaminated soil was removed and replaced with new backfill. The failed component was retained for evaluation. System component is newly installed equipment. Installing contractor will be notified. Such equipment failure cannot be diagnosed or prevented as the component was over six-feet beneath surface of the ground. | SSO Affected Private Property
56316 | 41560 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-11-02 10:58 | 2013-11-02 12:05 | 2013-11-02 10:50 | 0 |  | Force Main in Buffalo In | Two fusion couplers in a 2-inch low-pressure sewer system (LPSS) main line failed. This allowed sewage to exit the LPSS and migrate up to the surface of the ground where it entered a drainage ditch along a private drive which in turn discharged into the Tippecanoe River. | Repaired Pipe See Report | SSO Affected Private Property; SSO Reached Receiving Water | Tippecanoe River
56316 | 41565 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-11-02 10:58 | 2013-11-02 12:05 | 2013-11-02 23:51 | 0 |  | Force Main in Buffalo In Pipe Failure Fusion Coupler | Equipment Failure Two fusion couplers in a 2-inch low-pressure sewer system (LPSS) main line failed. This allowed sewage to exit the LPSS and migrate up to the surface of the ground where it entered a drainage ditch along a private drive which in turn discharged into the Tippecanoe river. | Repaired Pipe See Report | SSO Affected Private Property; SSO Reached Receiving Water | Tippecanoe River
56316 | 42149 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-11-24 17:06 | 2013-11-24 20:00 | 2013-11-25 14:40 | 0 |  | Low pressure sewer main pipe failure | Equipment Failure The fusion saddle joint where a 1.25 inch discharge line connects to the 3.0 inch LPSS main line failed allowing sewage from the LPSS to escape below ground. The sewage migrated to the surface to a private lawn and also the edge of a public road (Co.RD.800 North). | Repaired Pipe See Report | SSO Reached Public Land; SSO Affected Private Property
56316 | 42204 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-11-24 17:06 | 2013-11-24 20:13 | 2013-11-27 17:40 | 0 |  | Low pressure sewer main. | Low pressure sewer main. | Repaired Pipe See Report | SSO Reached Public Land; SSO Affected Private Property
56316 | 43230 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-12-29 10:26 | 2013-12-29 12:58 | 2013-12-20 | 75 | gallons | 6218 E 800 N Monticello IN | Equipment Failure The Back-flow preventer component in a curb-stop assembly failed (Cracking along a fused seam); Allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS underground through the failed backflow preventer until it reached the surface overflowing to ground. | See Report | SSO Affected Private Property
56316 | 43103 | IN0060887 | TWIN LAKES REGIONAL SEWER DISTRICT BIG MONON BAY | White | 2013-12-29 10:26 | 2013-12-29 12:58 | 2013-12-30 | 75 | gallons | 6218 E 800 N Monticello In | Equipment Failure The back-flow preventer component in a curb-stop assembly failed (cracking along a fused seam); Allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS underground through the failed backflow preventer until it reaches the surface overflowing to ground | See Report | SSO Affected Private Property
56317 | 39297 | IN0061581 | TWIN LAKES REGIONAL SEWER DISTRICT SNOW DITCH WASTE WATER TREATMENT PLANT | White | 2013-07-29 11:16 | 2013-07-29 11:06 | 2013-07-30 11:06 | 0 |  | 5689 E Pleasant Valley Drive | Equipment Failure. The check-valve component in a curb-stop assembly failed allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS through a crack in the assembly and exit to ground through the valve pit opening. | Equipment Failure The check-valve component in a curb stop assembly failed allowing sewage from the low pressure sewer system (LPSS) to exit the LPSS through a crack in the assembly and exit to ground through the valve pit opening. | SSO Affected Private Property
56317 | 42026 | IN0061581 | TWIN LAKES REGIONAL SEWER DISTRICT SNOW DITCH WASTE WATER TREATMENT PLANT | White | 2013-11-18 02:20 | 2013-11-18 14:38 | 2013-11-19 13:50 | 0 |  | Grinder Pump Field | Equipment Failure Power failure occurred on 11-17-13 causing the grinders at the TLRSD. Pierce-Lakewood grinder field to stop pumping. Those homes in the area that did not lose power continued to discharge to the LPSS; resulting in an overflow from the tank to the grinder vaults and from there to ground via vents in the grinder vaults. | See Report | SSO Affected Private Property
56318 | 35139 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-01-19 13:37 | 2013-01-19 21:05 | 2013-01-12 07:00 | 25 | gallons | Pump station at 12030 North Holiday Heaven Monticello IN | Pump failure at 12030 N Holiday Heaven pump caused an untreated release. | Shut pump off to stop flow. Pumped chamber down to the pump. Replaced defective grommet on pump. Limed affected area. | SSO Reached Public Land
56318 | 36514 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-04-19 17:30 | 2013-04-19 18:25 | 2013-04-19 18:55 | 350 | gallons | 2067 Roundabout Road manhole | A cleanout valve was open resulting in an untreated release from manhole to surrounding ground. | Closed valve and put cap on line. Put lime on affected area. | SSO Reached Public Land
56318 | 36791 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-05-07 17:17 | 2013-05-08 18:00 | 2013-05-09 04:37 | 1000 | gallons | 5924 East U.S. Highway 24 | Contractor damaged low pressure sewer line while boring to install a utility line. Resulted in untreated release to surrounding ground. | Contractor dug hole to contain release until repairs completed. Additional contractors brought in to excavate and repair two sections of the damaged sewer.Twin Lakes will continue efforts and existing policy to verify that construction contractors working near sewers properly locate all utilities. Locates had been performed in this case and the contractor still damaged the sewer as a result of their own actions. No additional preventative action possible. | SSO Reached Public Land
56318 | 37561 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-06-01 08:00 | 2013-06-01 08:45 | 2013-06-02 16:14 | 350 | gallons | 10558 CC Beach Drive | Back flow at curb stop failed and blew a grommet out of the grinder unit. | Changed grommet on grinder unit. Contractor called to replace Backflow Preventer.
56318 | 38053 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-06-01 08:45 | 2013-06-01 08:45 | 2013-06-26 16:05 | 0 |  | 10568 C&C Beach Dr. Check-Valve | Equipment Failure Check-Valve. The check-valve component in a curb stop assembly failed allowing sewage from the low pressure sewer system (LPSS) to exit the LPSS and backflow into the discharge line from the grinder unit. This in turn causes a grommet failure allowing sewage to enter the grinder vault and eventually overflow to ground. | 6/01/2013: Replaced grommet on grinder unit discharge line. 6/14/2013: Contractor excavated and replace faulty check-valve component of curb-stop assembly. The failed component was retained for evaluation. Such equipment failure cannot be diagnosed or prevented as the component was beneath surface of the ground and had been covered by pavement by the property owner without consulting Twins Lakes RSD | SSO Affected Private Property
56318 | 37800 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-06-18 11:31 | 2013-06-18 13:10 | 2013-06-19 11:10 | 75 | gallons | E of intsec of US 39N & 24E | Equipment Failure Air-Relief valve (ARV) failure on low-pressure sewer system (LPSS) allowed sewage from the LPSS to escape into the ARV Vault and once full sewage from the fault overflowed onto the ground North of the Westbound Land of US HWY 24. | Overflow was contained by having GODLOVE ENTERPRISES INC. pump sewage out of the vault into a waste hauling truck. Twin Lakes RSD Personnel attempted to close a ball valve mechanism to isolate flow to the air-relief valve but the ball valve would not close. Twin Lakes RSD personnel stopped the leak from the air-relief valve by securing a PVC CAP to the air-relief valve. A new ball valve and air-relief valve will be installed to replace the faulty ball valve and air-relief valve. New components have been ordered and replacement of faulty equipment is scheduled for 6-24-2013. | SSO Reached Public Land
56318 | 38006 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-06-18 11:31 | 2013-06-24 12:17 | 2013-06-25 09:25 | 0 |  | E. of Intsec of US 39N & 24E | Equipment Failure Air Relief Valve. 6/18/13 75 Gallons see previous report. 6.24.13 While replacing faulty Air Relief Valve (ARV); Approx 90 Gallons of sewage overflowed onto the ground while the repairs were completed. The majority of the sewage (Approx 4000 Gallons) was contained by waste hauler trucks during this activity and hauled away. | 6/18/13: See previous report. 6.24/13 Pressure into he line was minimized (in order to minimize overflow potentially) by bypassing 2 nearby lift stations and also turning off pumps at the nearest lift station additional containment was achieved during repair activity by having Godlove enterprises Inc. pump sewage out of the valve vault into a waste hauling truck. Twin Lakes RSD personnel replaced the faulty air-relief valve and also replaced a ball valve at the base of the air relief valve to compete repairs. Affected areas were treated with AG-Lime. Such equipment failures cannot be predicted or prevented. Twin Lakes RSD will continue regular preventative maintenance at lift stations to ensure flow and pressure in the LPSS remain within acceptable ranges. | SSO Reached Public Land
56318 | 38017 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-06-24 15:42 | 2013-06-24 17:15 | 2013-06-25 15:10 | 0 |  | 1142 N 1175 W Carroll Co. IN | Equipment Failure Check- Valve The Check-valve component in a curb stop assembly failed allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS and backflow into the discharge line from the grinder unit. This in turn caused a grommet failure. Allowing sewage to enter the grinder vault and eventually overflow to ground. | Excavated and replaced faulty check-valve. Placed lime on affected areas. The failed component was retained for evaluation. Such equipment failure cannot be diagnosed or prevented as the component was over five-feet beneath surface of the ground. | SSO Affected Private Property
56318 | 38440 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-07-05 09:11 | 2013-07-05 09:11 | 2013-07-05 18:50 | 0 |  | Lift Station #02 | Equipment Failure The PLC controlling the VFD pumps at lift-station #2 failed. This failure resulted in an error which shut down the pumps. this caused the level of sewage in the wet-well to rise above the alarm point and overflow into the lift station through a floor drain connected to the wet-well and to the ground outside the lift station. | VFD pumps were taken out of AUTO and PLaced in hand in order to pump down the sewage in the wet-well and stop the overflow. Sewage which had pooled inside the lift station was pumped back into the wet-well using a portable pump sewage on the ground was flushed with copious amounts of water and pumped back in to the wet-well using a portable pump. AG -Lime was applied to affected areas. | Sanitary Sewer
56318 | 38469 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-07-09 | 2013-07-09 12:00 | 2013-07-09 13:27 | 35 | gallons | 10472 North Earl Avenue | Equipment Failure Check-Valve Grommet The check-valve component in a curb-stop assembly failed; allowing sewage from the low pressure sewer system (LPSS) to ecit the LPSS and backflow in to the discharge line from the grinder unit. This in turn caused a grommet failure allowing sewage to enter an fill the grinder vault until it overflowed to ground. | The discharge line shut-off valve was closed to stop the discharge from the grinder. The curb-stop shut off was also closed to prevent additional backflow from the LPSS to the grinder. The grinder unit was replaced. The curb-stop assembly was excavated and the failed check-valve was replaced. AG-Lime was applied to affected areas. The failed component was replaced. Such equipment failure con not be prevented by Twin Lakes RSD personnel as the equipment is over five-feet beneath ground level. | SSO Affected Private Property
56318 | 40509 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-09-30 08:28 | 2013-09-30 08:42 | 2013-09-30 16:35 | 0 |  | Lift Station #02 | Equipment Failure The pressure tranducer/level meter in the wet well failed to transmit water level readings to the PLC which in turn prevented the PLC from actuating pumps at LS #2. This allowed sewage from the lower-pressure sewer system (LPSS) to exit the LPSS via the wet well and overflow to the ground. | Repaired Pump Station See Report | SSO Reached Public Land; SSO Affected Private Property
56318 | 41130 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-10-20 13:04 | 2013-10-20 13:55 | 2013-10-21 13:04 | 0 |  | 430 Sunnyside Dr 47960 | Equipment Failure The check-valve component in a curb-stop assembly failed allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS and backflow into the discharge line from the grinder unit. This in turn caused a grommet failure. Allowing sewage to enter and fill the grinder vault until it overflowed to ground. | See Report | SSO Affected Private Property
56318 | 45925 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-10-28 17:00 | 2013-10-28 17:50 | 2013-10-29 16:00 | 100 | gallons | 1962 Roundabout Rd 47960 | The check-valve component in a curb-stop assembly failed. Allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS and backflow into the discharge line from the grinder unit. This in turn caused a grommet failure allowing sewage to enter and fill the grinder vault until it overflowed to ground. | See Report | SSO Affected Private Property
56318 | 41391 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-10-28 17:27 | 2013-10-28 17:50 | 2013-10-29 16:00 | 0 |  | 1962 Roundabout Rd 47960 | Equipment Failure The check-valve component in a curb-stop assembly failed; allowing sewage from the low-pressure sewer system into the discharge line from the grinder unit. This in turn caused a grommet failure allowing sewage to enter and fill the grinder vault until it overflowed to ground. | See Report | SSO Affected Private Property
56318 | 39924 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-10-28 17:27 | 2013-10-28 17:50 | 2013-10-29 16:00 | 0 |  | 1962 Roundabout Rd 47960 | Equipment Failure the check-valve component in a curb-stop assembly failed; allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS and backflow into the discharge line from the grinder unit. This in turn caused a grommet failure allowing sewage to enter an fill the grinder vault until it overflowed to ground. | See Report | SSO Affected Private Property
56318 | 41384 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-10-28 17:27 | 2013-10-28 17:50 | 2013-10-29 16:00 | 0 |  | 1962 Roundabout Rd 47960 | Equipment Failure The check-valve component in a curb-stop assembly failed; allowing sewage from the low-pressure sewer system (LPSS) to exit the LPSS and backflow into the discharge line from the grinder unit. This in turn caused a grommet failure allowing sewage to enter and fill the grinder vault until it overflowed to ground. | See Report | SSO Affected Private Property
56318 | 42615 | IN0062367 | TWIN LAKES REGIONAL SEWER DISTRICT RATTLESNAKE CREEK | White | 2013-12-21 10:33 | 2013-12-21 10:53 | 2013-12-21 18:10 | 0 |  | 11934 Holiday Haven Monticello IN 47960 | Equipment Failure The ball-valve component in a flush-connection servicing the low-pressure sewer system (LPSS) worked open; allowing sewage from the LPSS to exit the LPSS fill the vault containing the flush connection until it overflowed to ground (200 Gallons) and then to Lake Freeman (50 gallons). | See Report | SSO Affected Private Property; SSO Reached Receiving Water | Lake Freeman
55320 | 36133 | IN0020567 | SOUTH WHITLEY WASTE WATER TREATMENT PLANT | Whitley | 2013-04-18 18:00 |  | 2013-04-19 13:00 | 1720000 | gallons | WWTP Lift Station | Precipitation event caused flow from lift station to exit the emergency bypass pipe. WWTP was taking full flow treatment at the time of discharge. 2100 gpm to WWTP. Sewage continued rising with pumps at capacity. |  | SSO Reached Receiving Water | Eel River
55320 | 36152 | IN0020567 | SOUTH WHITLEY WASTE WATER TREATMENT PLANT | Whitley | 2013-04-23 23:14 | 2013-04-23 23:34 | 2013-04-24 15:08 | 16000 | gallons | Lift station at WWTP Eel River | Untreated Release Rain 1.41 inches Heavy rain exceeded design. |  | SSO Reached Receiving Water | Eel River
55320 | 37565 | IN0020567 | SOUTH WHITLEY WASTE WATER TREATMENT PLANT | Whitley | 2013-06-01 00:20 |  | 2013-06-01 18:18 | 0 |  | South Whitley WWTP | Precipitation event exceeded the design flow in the Lift Station at the WWTP resulting in bypass of treatment plant via emergency overflow to receiving water |  | SSO Occurred at Treatment Plant; SSO Reached Receiving Water | Eel River
55320 | 38370 | IN0020567 | SOUTH WHITLEY WASTE WATER TREATMENT PLANT | Whitley | 2013-06-12 22:36 | 2013-06-13 01:08 | 2013-06-13 | 0 |  | Lift Station on WWTP 12 Emergency Overflow Eel River | Rain 2.62 inches Heavy rain exceeded design flow. Rain intensity of 2.68 per hour (.67 in 15 min) |  | SSO Affected Private Property | Eel River
55320 | 39055 | IN0020567 | SOUTH WHITLEY WASTE WATER TREATMENT PLANT | Whitley | 2013-06-26 10:36 | 2013-06-26 11:12 | 2013-06-27 08:59 | 0 |  | Liftstation at WWTP | Rain 1.3 inches Untreated Release Heavy Rainfall exceeded plant design |  | SSO Reached Receiving Water | Eel River
55320 | 39696 | IN0020567 | SOUTH WHITLEY WASTE WATER TREATMENT PLANT | Whitley | 2013-08-02 17:30 | 2013-08-02 23:15 | 2013-08-03 07:12 | 0 |  | Lift Station WWTP | Heavy rain fall exceeded plant disign |  | SSO Reached Receiving Water | Eel River
55247 | 41754 | IN0020753 | MIAMI VILLAGE MOBILE HOME PARK | Whitley | 2013-11-10 16:00 | 2013-11-11 14:30 | 2013-11-11 18:57 | 0 |  | MH on county road E Old Trail Rd located approx 360ft north of 001 discharge point into EEL River | Discharge line from WWTP to 001 discharge point was partial plugged due to mud and debris from pipe collapse in several places. | See Report | SSO Affected Private Property | Eel River
55270 | 36037 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-04-19 00:30 | 2013-04-20 23:00 | 2013-04-23 07:39 | 85200 | gallons | Overflow at EQ Basin #4 Martin Johnson Ditch | Untreated Release Rain 3.5 inches. Received 3.5 inches of rain in one evening on 4/18/13 causing flooding conditions. This is a follow up report with estimated end amount of overflow. | Held EQ basin at max capacity. Removed cap at EQ basin EQ basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer system. Continue to work on I&I reduction. | SSO Reached Receiving Water | Martin Ditch
55270 | 36458 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-04-19 00:30 |  | 2013-04-19 16:00 | 0 |  | Overflow at EQ Basin #4 Martin Johnson Ditch | Untreated Release Rain 3.5 inches. Received 3.5 inches of rain in one evening on 4/18/13 causing flooding conditions. | Held EQ basin at max capacity. Removed cap at EQ basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer. Continue to work on I&I reduction. Will report again when event has stopped and report amount released. | SSO Reached Receiving Water
55270 | 36039 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-04-19 00:30 | 2013-04-20 23:00 | 2013-04-23 07:42 | 85200 | gallons | Overflow at EQ Basin #4 Martin Johnson Ditch | Untreated Release Rain 3.5 Rain. Received 3.5 inches of rain in one evening on 4/18/13 causing flooding conditions. This is a follow up report with estimated end amount of overflow. | Held EQ basin at max capacity. Removed cap at EQ basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer system. | SSO Reached Receiving Water | Martin Ditch
55270 | 36688 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-04-24 00:30 | 2013-04-25 15:30 | 2013-04-28 11:36 | 46800 | gallons | EQ Basin #4 | Follow up report to incident 36299. Precipitation event(s) exceeded system capacity resulting in and untreated release from EQ basin to receiving water. | Held EQ basin at max capacity. Removed cap at EQ Basin #4 to prevent side wall erosion and relieve pressure from snaitary sewer system.Continue work on I & I reduction | SSO Reached Receiving Water | Martin Ditch
55270 | 36299 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-04-24 00:30 |  | 2013-04-24 15:42 | 0 |  | EQ Basin #4 | Precipitation event(s) caused an untreated release from the E.Q. Basin. | Held EQ Basin at max capacity. Removed cap at EQ Basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer system. Continue to work on I & I reduction. | SSO Reached Receiving Water | Martin Ditch
55270 | 37378 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-06-01 20:00 |  | 2013-06-02 12:30 | 0 |  | Overflow at EQ Basin #4 | Exceeded Max Capacity Rain 3.8 inches. Received 3.8 inches of rain on 6/1/2013 in a short period of time causing flooding conditions. | Held EQ basin a to max capacity. Removed cap at EQ basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer system. Continue to work on I/I reduction. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water
55270 | 37391 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-06-01 20:00 |  | 2013-06-02 12:30 | 0 |  | Overflow at EQ Basin #4 Occurred at Treatment Plant Reached Receiving Water (Martin Johnson Ditch) | Exceeded Max Capacity Rain 3.8 inches Received 3.8 inches of rain on 6/1/2013 in a shore period of time causing flooding conditions. | Held EQ Basin at max capacity. Removed cap at EQ basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer system. Continue to work on I&I reduction. | SSO Reached Receiving Water
55270 | 37370 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-06-01 20:00 | 2013-06-02 22:00 | 2013-06-04 00:34 | 31200 | gallons | Overflow at EQ Basin #4 | Exceeded Max Capacity Rain 3.8 inches. Occurred at Treatment Plant Reached Receiving Water | Held EQ basin at max capacity. Removed cap at EQ basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer system. Continue I/I reduction. | SSO Occurred at Treatment Plant; SSO Reached Receiving Water
55270 | 37393 | IN0021113 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-06-01 20:00 |  | 2013-06-02 12:30 | 0 |  | Overflow at EQ Basin #4 Occurred at Treatment Plant Reached Receiving Water (Martin Johnson Ditch) | Exceeded Max Capacity Rain 3.8 inches. Received 3.8 inches of rain on 6/1.2013 in a short period of time causing flooding conditions. | Held EQ Basin at max capacity. Removed cap EQ Basin #4 to prevent side wall erosion and relieve pressure from sanitary sewer system. Continue to work on I/I reduction. | SSO Occurred at Treatment Plant
55270 | 43671 | IN0021113 Outfall 001 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-12-20 09:30 | 2013-12-21 14:00 | 2013-12-24 17:06 | 1200 | gallons | Overflow at EQ Basin #4 | Exceeded Max Capacity Rain 2.0 inches Snow melt of 8 over 24 to 48 and over 2 rain causing flooding conditions. | See Report | SSO Reached Receiving Water | Martin Johnson Ditch
55270 | 43672 | IN0021113 Outfall 001 | CHURUBUSCO MUNICIPAL SEWAGE TREATMENT PLANT | Whitley | 2013-12-20 09:30 |  | 2013-12-22 21:15 | 1200 | gallons | Overflow at EQ Basin #4 | Exceeded Max Capacity Rain 2.0 inches Snow melt of 8 over 24 to 48 hrs and 2 of rain causing flooding conditions. | See Report | SSO Reached Receiving Water | Martin Johnson Ditch
55307 | 36787 | IN0037729 | BLUE RIDGE MOBILE HOME PARK | Whitley | 2013-05-01 14:00 |  | 2013-05-06 21:52 | 8000 | gallons/day | Constructe bypass around Polishing Pond to Outfall 001. | On Wednesday May 1 2013 the polishing pond of the wastewate treatment system serving the Blue Ridge Estates Manufactured housing community was taken out of service for cleaning or abandonment (pending Construction Permit). The pond has had issues with algae and accumulated solids contaminating final effluent samples and causing final effluent Total Suspended Solids and Ammonia-Nitrogen violations. The Constructed Bypass (a.k.a. Outfall 101) has a new Chlorine disinfection unit ultra sonic flow meter and stilling basin and a Dechlorinator Unit. The presence of an accurate effluent flow meter will determine if it is advisable to apply for a Construction Permit to close the polishing pond which is not aperating as designed and/or utilize an existing protion of the treatement facility as flow equalization and storage. | Secondary effluent samples collected the past few moths have confirmed that water leaving the treatment facility clarifier is well below permit levels. Water from the clarifier then goes through Chlorine disinfection tablet feeder; to tablet feeders that remove excessive Chlorine residu8al; and finally to the polishing pond. the polishing pond is the only treatment unit being bypassed; as such water leaving the treatment facility is fully treated and below permit limits. The bypass will cease once a source of actionis decided upon and after an IDEM Construction Permit is issued and after construction is completed. | SSO Occurred at Treatment Plant