## Minimum Requirements
RFP 18-035; Access Control System
MINIMUM REQUIREMENTS
ATTACHMENT H
The Minimum Requirements indicate the minimum requirements all Respondents must adhere to in order to be considered as a responsive Respondent. All Respondents must state their ability and willingness to meet these Minimum Requirements in their Transmittal Letter and in this attachment of the proposal. Failure to do so will be considered grounds for disqualification from further consideration. The Minimum Requirements for this RFP are as follows:
Instructions: In the yellow shaded boxes, please confirm the Respondent's ability to meet each Minimum Requirement.
Respondent Name:
Minimum Requirement | Respondent Meets Minimum Requirement? (Yes/No) | Comments
1. Respondent must be an authorized Lenel Value Added® reseller
2. Respondent must participate in the on-site visit at each fcilities for which they anticipate submitting a bid
3. Respondent will provide the wire to the Indiana State Police and their staff will run the wiring from head end to field hardware
4. Respondent will be responsible for the installation and connecting the wiring of all devices
5. Respondent must follow the Lenel recommended installation guidelines
6. All devices (locks and controllers) shall be 24 VDC. This will eliminate the need for another device/power supply for 12VDC. Readers can be 12 VDC, as they get power from the controller.
7. No LNL-1300 controllers should be used
8. Wiring in the head end enclosure should not block or impede the ability to access a controller
9. Wire must be suspended from the building structure and not attached to pipes or other wiring
10. Reader must be mounted in such a way that when a person presents their card, they will not have to stand in the swing of the door.
11. If a door release button is requested/needed, then the button should be wired to one of the auxiliary inputs on the controller for the reader/door the button is to unlock. A local I/O will be used to unlock the door. If there is an AiPhone, or other type device with a button, then that should be used to as the door release button.
12. A request to exit signal must not unlock the door.
13. Loops at the door should be avoided where possible
14. If drilling through a door to run wire, there must be a larger space drilled on the hinge side and lock side to accommodate the splice and extra wire.
15. Finish on door hardware must match existing equipment in the area.
16. Addressing on the 1320s and other controllers should start at address 0 (zero).
17. Cabinet tamper should be wired and working properly
18. The “AC Fail” (NC) must be wired to the Power Fail Input on the ISC or on a 1320 if an ISC is not present.
19. The “Battery Fail” (NO) must be wired to an auxiliary input. Preferably to the ISC on Aux 1 of the first reader. If there is no ISC, then to the Aux 1 on the first reader of a 1320.
20. Testing must be done on all doors to verify reader, door forced, and request to exits are working properly. Must coordinate with State representative to do a walkthrough of the doors to verify operation.
21. A list of the doors locations must be sent to State representative indicating the controller, 2220 or 1320, address and reader number so that the description in OnGuard can be updated.
22. After installation and testing, on the 2220, change dip switch 1 to disable the default username and password. Verify with State representative that a user has been created on the LNL-2220
23. Each facility must have a reader installed on the interior and exterior of one door so that upon a valid card read on the interior reader, the system will arm/unmask the motion detectors and other position switches so that they are monitored. On a valid card read on the exterior reader, the system will disarm/mask the motion and other position switches.
24. Exterior doors must have a door position switch installed
25. Motion detectors will be installed strategically throughout the building
26. Another door may not have a card reader but must have an electronic lock that will need to be wired into one of the spare outputs on the Lenel controller so that it can be controlled.