## Instructions
Best and Final Offer (BAFO)
100-23-75105, Mobile Fire Pump Trailer
INSTRUCTIONS | Respondent:
The Indiana Department of Homeland is seeking pricing for a custom built Mobile Pump Trailer to be utilized by the Fire Academy for training purposes. The awarded vendor will provide a trailer that conforms to ALL specifications in the Specification Document provided. Vendor will also provide 3 days (1 class each day) of instruction which is to be provided by a factory authorized representative.
Please populate the YELLOW-SHADED CELLS in the Item List tab
2. Price must be ALL INCLUSIVE, including trailer, shipping and training.
3. Review the Specifications tab. The specification are also listed in the Contract Negotiated Bid document section 1.4
4. Return WORKING Excel file with proposal on flash drive.

## Specification
Best and Final Offer (BAFO)
FACTORY INSTRUCTION
There shall be 3 days (1 class each day) of instruction provided by a factory authorized representative. This representative shall provide instruction to the end user on the operation, maintenance and care of the pump system delivered, as well as any equipment supplied with the pump system.
PUMP PAINT FINISH, SINGLE COLOR
The pump shall have a single-color paint finish. The paint color shall be determined at the preconstruction conference. The complete pump shall be thoroughly sanded, solvent cleaned and finished with high luster Axalta Coating Systems polyurethane paint before mounting to the drive engine and plumbing.
TRAILER SPECIFICATION:
Trailer: The trailer shall have a GVWR of 15,000 pounds and be fully DOT approved for road use. The trailer shall also be of heavy-duty construction with decking and fenders.
Length: Not to exceed 32’ in overall length.
Frame: The trailer frame rails shall be tube steel with steel formed cross members. The trailer frame shall be designed to allow for recess mounting of the pump engine fuel cell within the frame assembly itself.
Axles: There shall be one (1) 15,000-pound axle with suspension, for use over unimproved roads, provided.
Wheels and Tires: The tires, 425/65R-22.5PR shall be road rated tubeless radial type with matching spare.
Hitch: Gooseneck Hitch for 2-5/16” ball.
Jack: 2 - 10,000-pound front adjustable electric or hydraulic jack stand with foot shall be included.
Stabilizer Jacks: 2 rear corner manually adjustable stabilizer jacks shall be supplied.
Tie Downs: Four (4) tie down rings shall be provided.
Trailer Electrical: A six flat prong electrical connector shall be supplied with a matching plug shipped loose.
Road Lights: LED DOT lighting and reflectors shall be provided.
Trailer Brakes: Electric braking system with back up trailer battery and breakaway safety switch system shall be provided.
Weight Distribution: All mounted carried equipment must be mounted for proper weight distribution.
PUMP MODULE/TRAILER PAINT FINISH, SINGLE COLOR
The pump module/trailer shall be painted with a primer and powder coat finish. The complete pump module shall be thoroughly sanded, solvent cleaned before mounting to the drive engine and plumbing. The exact color code shall be determined at the pre-construction conference.
REQUIRED LABELS:
All labels, signs, nameplates, and instruction plates shall be permanent in nature with the information permanently engraved, stamped or etched thereon. All labels are to be mounted in a conspicuous place.
FLUID CAPACITY PLATE
A permanently affixed fluid data plate shall be installed on the pump system to indicate the type and quantities of the following fluid used in the pump system:
• Engine Oil
• Engine Coolant
• Pump Transmission Lubrication Fluid (if applicable)
• Trailer Tire Pressure - Cold (if applicable)
• All filters
• Pump Manufacturer
• Production Number
• Paint Number
• Year Built
• Date Shipped
• Pump Serial Number
• Test pressure and flow rate
General Construction
The fire package shall be designed, and the equipment mounted with due consideration to distribution of loads. Welding shall not be employed in the assembly of the package in a manner that shall prevent the removal of major component parts for service and/or repair. The package shall meet the performance requirements at elevations of 2000 feet (610m) above sea level and while stationary on any grade of up to and including 6% in any direction.
Workmanship: The workmanship is of the highest quality in its respective field. Special consideration has been given to the following points: Accessibility of the various units that require periodic maintenance operations; ease of operations and symmetrical proportions. Construction is rugged and ample safety factors are provided to carry loads as specified. The design of this apparatus embodies the latest approved automotive engineering practices. The entire package shall be assembled within the borders of the Continental United states to insure more readily available parts and service, as well as protection the purchaser should legal action ever be required.
Operations and Service Documentation: The contractor shall deliver with the fire package at least two sets of complete operation and service documentation covering the completed package as delivered and accepted. The documentation shall address at least the inspection, service, and operations of the fire package and all major components thereof (English)
Pump System Test: The pump system shall undergo test per applicable sections of NFPA standards, prior to delivery of the completed apparatus.
Delivery Period: March 1, 2024
Required Labels: All labels, signs, nameplates, and instruction plates shall be permanent in nature with the information permanently engraved, stamped, or etched thereon. All labels are to be mounted in a conspicuous place.
Performance: The package is design to preform to NFPA 1901 industrial fire pump rating of 750 GPM. From sufficient hydrant water source, the performance should exceed 750 GPM. The pump shall be free from objectionable pulsations and vibration.
Pump: General Product Description
Skid fire pump is rated 750 @ 150psi(10bar) per the current edition of NFPA 1901. This package includes steel frame, steel manifolds, controls, instruments, tier IV diesel engine and a 750gpm fire pump.
A 750 GPM single stage fire pump shall be installed. The pump shall be designed to operate directly mounted on an industrial engines bell housing. The engine and drive components shall provide sufficient horsepower and RPM to enable the pump to meet and exceed its rated performance. The entire pump shall be assembled and tested at the pump manufacturer's factory. The entire pump, both suction and discharge passages, shall be hydrostatically tested to a pressure of 500 PSI. Pump body shall be vertically split on a single plane, for easy removal of impeller assembly, including clearance rings.
All moving parts in contact with water shall be of high-quality bronze or stainless steel.
• • Vertically split, cast-iron bronze fitted pump casing
• • Impellers opposed design to eliminate end thrust
• • Broached impeller (not keyed) for longer life
• • Oversized, deep groove radial type bearings for longer life
• • 10 tooth splined shaft for durability
• • 4” NPT discharge
• • 5-6” NPT or weld flange suction
• • Uses standard SAE engine adapter
ENGINE SPECIFICATIONS
· Maximum Power: 134 HP
· Maximum Torque: 406 lb.-ft @ 1500 rpm
· Rated Speed: 2000-2400 rpm
· Minimum Power: 74 HP
· EMISSION STANDARDS o Emissions: U.S. EPA & CARB Tier 4 Final, EU Stage V
Engine Cooling System: The engine cooling system shall have the capacity to cool the engine according to the engine manufacturer’s requirements. A fan area safety guard shall be supplied. A shroud and recirculation shields system shall be used to ensure that once air has passed through the radiator, the same air is not drawn through again. The coolant system shall contain a mixture to keep the coolant from freezing to a temperature of -20 degrees Fahrenheit that is compatible with the engine manufacturer's requirement.
Engine Starting / Charging: The engine shall be equipped with a 12-volt starter, 12V Alternator
Muffler: A heavy-duty, oversized muffler with spark arrestor and rain cap shall be mounted horizontally.
Air Cleaner: A heavy-duty air cleaner with inlet bonnet shall be supplied.
Engine Mounting: The engine shall be mounted via integral mounts integrated on the fuel cell sufficient to support the load and vibrations of the engine.
Engine enclosure
Engine shall be enclosed to limit engine noise. Enclosure shall allow for engine maintenance. Sides and top covering should be removable with ease.
Plumbing: The pump plumbing system shall be built completely of carbon steel piping, carbon steel or brass fittings, and connections. Victaulic couplings or flanged connections shall be installed where required to permit flexing of the plumbing system and allow for quick removal of piping or valves for service. Where flexible hose is used the couplings shall be threaded stainless steel or Victaulic connections. Plumbing will be designed to NFPA 1901 Standards.
The fire pump and plumbing shall be hydrostatically tested in compliance to applicable sections of #1901 NFPA standards, with test results submitted on delivery.
Intake Manifolding: The manifold system shall be of schedule 10 Carbon Steel.
Intake: Two (2) 6” NPT male intake connections shall be provided, one each side of trailer
Intake Valves: Two (2) TFT Ball Intake Valves, one each side. 5.0"STORZ X 6.0"F Part #AX1ST-NX. Relief valve to be incorporated with the valve.
Discharge Manifolding: The manifold system shall be of schedule 40 carbon steel and have flanges and taps to accommodate the valving provided.
Discharge Outlet(s):
• One (1) 5-inch Rear outlet with TFT Ball Valve Part # AX1ST-NX 5 inch Storz and cap.
• Four (4) 2.5” NHT outlets with panel mounted control valves
• One 2.5” NHT outlet in hose tray above pump with panel mounted control valves (tray should hold 150’ of connected 2.5” hose)
• One 1.75” NHT outlet in hose tray above Pump with panel mounted control valves (tray should hold 150’ of connected 1.75” hose)
• Hose Trays should be no more that 6’ above ground level
Drains: The plumbing system shall be equipped with additional low point manually operated drain valves to allow total draining of the fire pump plumbing system.
Control Panel: An instrument panel with hooded LED light shall be supplied
Master Gauges: At the operator’s area there shall be two 4.5” liquid filled master gauges, which read both pressure and vacuum in psi and bar. One is for main pump discharge pressure and the other is for pump intake reading both pressure and vacuum.
Master Gauges: The discharge and master gauges shall be liquid filled with a solution to assure visual readings and reduce inner lens condensation. The body of the gauges shall be constructed of Zytel nylon with chrome-plated bezels. The face of the gauges shall be spun metal with black background and white markings. The pressure gauges shall maintain performance of all features and be free from defects in material and workmanship, which includes fluid fill leakage and discoloration for seven years.
Gauge Test Ports: A gauge testing ports for master intake and discharge pressure gauges shall be installed, with a nameplate label for each port.
Engine Speed Control
Manual operated system to control engine speed.
Priming System:
One (1) oil less 12VDC primer – Darley Part # AP00960
Electrical: The installation and materials used in the low voltage electrical system; including all panels, electrical components, switches and relays, wiring harnesses and other electrical components shall conform to the latest automotive standards, current automotive electrical system standards and the applicable requirements of the NFPA standards.
Battery Charger
There shall be a 12voltDC battery float charger installed.
The charger shall have the following operational specifications:
Battery Charger Receptacle
One (1) 120-volt 20 amp receptacle shall be installed (location to be determined at pre-construction).
Fuel Tank:
One (1) 125-gallon fuel tank shall be provided with visual float fuel gauge, baffle, fuel filler neck/cap, fuel pick up tube and drain plug. Tank shall be built into the pump skid allowing for a minimum 4 hr run time at full engine load.
Water Tank:
There shall be one (1) 300-gallon poly water tank on board with a direct supply to the water pump suction manifold. There will be a manually operated tank to pump isolation valve and a manually controlled tank fill valve from the pump discharge manifold.
Loose Equipment Storage:
There shall be a storage rack to carry a 3,000-gallon folding tank and 2- 10’ 6” hard suction hoses
There shall be a tool chest/locker, located under the goose neck hitch to carry items such as spanner wrenches and hose adapters. Box shall be 16”H x 48”L x 11”D
Hose Loads:
There shall be the following hose loads provided. Hose will be supplied from Bulldog Hose Company and will adhere to NFPA 1962.
· 400’ – 1.75” with NH couplings
· 400’ – 2.5” with NH couplings
· 500’ – 5” LDH lay flat supply hose with Storz couplings
· Storage for all supplied hose
Testing
Testing must meet the following minimum requirements:
Each pump will be tested at a rated capacity of 750 GPM at 150 PSI, 525 GPM at 200 PSI, 375 GPM at 250 PSI. All test points shall be conducted at a 6ft. lift height.
U.L. Witnessed, 750 GPM @ 150psi: OPTIONAL.
The pump shall be third party tested and witnessed by Underwriters Laboratories, Inc. UL testing has been recognized as a leading, third party, product safety certification organization for over 100 years. UL has served on the NFPA (National Fire Protection Association) technical committee for over thirty (30) years.
The testing organization must meet the following minimum requirements:
• Must be a nationally recognized testing laboratory recognized by OSHA
| • Must comply with the ASTM (American Society for Testing Materials) standard E543 | "Determining the qualifications for nondestructive testing agencies"
• Must have more than forty (40) years of Automotive Fire Apparatus safety testing experience and more than fifteen (15) years of factory aerial device testing and Certification experience
• Must not represent, be associated with, or in the manufacture or repair of automotive fire apparatus
• Must provide proof of ten (10) million dollars in excess liability insurance for bodily injury and property damage combined
WARRANTY, PUMP SYSTEM
There shall be a two (2) year mechanical parts and labor warranty provided with the pump system. The pump system shall be free of defects in material and workmanship for a warranty period of two (2) years after the date on which the pump system is first delivered to the original purchaser.
Concept Pictures
These figures are only an estimate and are not to be construed as an amount to be offered under this Negotiated Bid. However, when completing Minority and Women’s Business Enterprises Participation Plan Form (Attachment A), Indiana Veterans’ Participation Plan Form (Attachment A1), and the Indiana Economic Impact Form (Attachment C) please use the total bid amount from the Bid Cost (Attachment D).

## Bid Cost
Best and Final Offer (BAFO)
Negotiated Bid 23-75105 - Mobile Pump Trailer
BAFO
ITEM | QUANTITY | PRICE | TOTAL
Mobile Pump Trailer | 1 | 179900 | 179900
3 Days of Training | 1 | 0 | 0
Shipping | 1 | 0 | 0
| Total Bid Amount | 179900