Scope of Work

1. Underfloor Plenum

a. HEPA vacuum the raised floor surface to remove loose particulate prior to removing floor tiles

b. Lift a limited number of floor tiles to provide underfloor plenum access

c. Manually remove large debris and contaminants

d. HEPA vacuum the subfloor slab to remove dust and debris

e. HEPA vacuum and wipe clean floor stringers, pedestal heads and large mechanical components

f. Clean perforated tiles and replace to their original locations

g. Upon request, provide a comprehensive report highlighting conditions of the underfloor plenum

Notes:

1. Hardware devices are not shifted or moved to gain access to captive floor tiles.

2. During the cleaning service, all safely accessible floor tiles are removed to provide the most comprehensive cleaning possible.

3. Floor tile removal is managed to prevent equipment overheating, maintain floor system structural integrity and minimize safety hazards.

4. To ensure no service interruptions, special attention is directed to data cabling, electrical connections, sensors and detectors.

2. Floor Surfaces (Raised and Non-Raised Access Flooring)

a. HEPA vacuum all floor surfaces, including accessible areas beneath hardware devices, to remove loose particulate.

b. Safely damp mop floor surfaces.

c. As needed and based on maintenance frequency; scrub clean all accessible floor surfaces using low speed scrubbing machines to remove imbedded contaminants and scuff marks

d. Safely damp mop floor surfaces as many times as needed to remove residual contaminants and cleaning solution

e. Non-Raised flooring will be treated according to the requirements of the specific surface or material

i. Standard VCT: As needed and based on maintenance frequency, apply one coat of restorer or remove existing finish (strip) and reapply two coats of floor finish

ii. Static Dissipating Tile/ESD: Typically, floor finish is not applied. However, based on customer agreement and as needed, apply one coat of anti-static restorer or remove existing finish (strip) and reapply two coats of static-dissipating floor finish

iii. Sealed Concrete: HEPA vacuum and damp mop only

iv. Carpeting: HEPA vacuum only

3. Equipment and Environment - Level 1

HEPA Vacuum, Damp Wipe and Spot Scrub:

a. Exterior surfaces of equipment cabinets, racks and stand-alone equipment, e.g. mainframes, tape libraries

b. Exterior surfaces of support equipment, e.g. CRACs, PDUs

c. Exterior surfaces of furniture and desktop equipment, e.g. tables, storage cabinets, monitors

d. Major infrastructure components, e.g. interior windows, windowsills, wall mounted hardware

e. Overhead cable trays

f. Vacuum Approx 800 ft of carpeted space